## Victoria Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer at
http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Victoria Summary
Changes since last update
Kiata Wind Farm: Kiata Wind Farm Pty Ltd advises that Kiata Wind Farm (31.05 MW) is now a committed project with full commercial use expected December 2017.
Generation withdrawals
Withdrawn
None to report.
Announced withdrawals (i.e. Mothballed, Seasonal Shut down etc.)
Hazelwood: Hazelwood Power advises that Hazelwood Power Station will cease generation at the end of March 2017.
Committed projects
Coal, CCGT, OCGT, Gas other, Solar, Water, Biomass, Geo-thermal, Other : None to report.
Wind: Ararat, Mt Gellibrand, Kiata.
Proposed projects
Please refer to information presented in the worksheet titled 'New Developments'.
Plant limitations
AEMO has not been advised of any plant limitations for this region.
Status | Coal | CCGT | OCGT | Gas other | Solar* | Wind | Water | Biomass | Other | Total
Existing | 6230 | 21 | 1903.8 | 523.4 | 0 | 1249.4 | 2295.8 | 52.7 | 0 | 12276.1
Announced Withdrawal | 1600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600
Existing less Announced Withdrawal | 4630 | 21 | 1903.8 | 523.4 | 0 | 1249.4 | 2295.8 | 52.7 | 0 | 10676.1
Committed | 0 | 0 | 0 | 0 | 0 | 337.1 | 0 | 0 | 0 | 337.1
Proposed | 0 | 500 | 600 | 0 | 164 | 3418.7 | 34 | 0 | 0 | 4716.7
Withdrawn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note: Existing includes Announced Withdrawal
* Excludes rooftop PV installations.

## Change Log
Victoria Change Log
Lists all key updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Morwell Power Station: Energy Brix Australia Corporation Pty Ltd advises that the Morwell plant has revised its available capacity from 104 MW to 75 MW (-29 MW) in summer and winter, due to generation units with DUID MOR1 in operation and generation unit with DUID MOR2 operational when generation unit with DUID MOR1 is under maintenance. Generation unit with DUID MOR3 will be available on a 30 day recall.
Qenos Cogeneration Facility: AGL Energy advises that Qenos Cogeneration Facility is a committed project. The 21 MW combined-cycle gas turbine (CCGT) construction completion achieved in October 2012 and full commissioning at the end of March 2013.
Publication Date: | 2013-06-30
Macarthur Wind Farm: AGL Energy advises that the 420 MW Macarthur wind farm project was completed in January 2013.
Mortons Lane Wind Farm: Mortons Lane WindFarm Pty Ltd advises that the 19.5 MW Mortons Lane wind farm project was completed in December 2012.
Qenos Cogeneration Facility: AGL Energy advises that 21 MW Qenos Cogeneration Facility project was completed in March 2013.
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm is a committed project. The 131.2 MW wind farm expected commissioning is January 2015.
Mildura Power Station: Solar Systems advises that Mildura Power Station demonstration facility is a committed project. The 1.5 MW solar plant is under construction and expected completion is July 2013.
Hallam Road Power Station: LMS Energy advises that the upgrades to Unit 7 was completed in June 2012 and Unit 8 in November 2012 increasing the capacity by 2.2 MW.
Publication Date: | 2013-08-13
Mildura Power Station: Solar Systems advises that Mildura Power Station Stage 2 of the project is to be 100 MW of capacity.
Publication Date: | 2013-11-15
Mildura Power Station: Solar Systems advises that Mildura Power Station demonstration facility (1.5 MW) project was completed in July 2013.
Portland Stage 4 Cape Nelson North and Cape Sir William Grant: Pacific Hydro Australia advises that Portland Stage 4 Cape Nelson North and Cape Sir William Grant (47.15 MW) construction at the site is to commence in September 2013, with full commissioning planned for September 2015.
Publication Date: | 2014-05-30
Loy Yang A: AGL Energy advises Loy Yang A Power Station has revised its available capacity to 2100 MW (-90 MW) in summer due to operational experience in ambient conditions.
Macarthur: AGL Energy advises Macarthur Power Station has revised its available capacity to 315 MW (-105 MW) in summer to reflect the actual behaviour of the wind generation assets during high temperature days.
Morwell/Energy Brix: Energy Brix Australia Corporation Pty Ltd advises Morwell/Energy Brix Power Station has revised its available capacity to 65 MW (-10 MW) in summer due to the Morwell mine fire destroying conveyors, thus restricting coal supply.
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm is a committed project. The 131.2 MW wind farm expected commissioning is July 2014.
Bald Hill Wind Farm (Phase 1): Mitsui and Co. Australia Ltd advises that Bald Hill wind farm is a committed project. The 106.6 MW wind farm expected commissioning is May 2015.
Portland Stage 4 Cape Nelson North and Cape Sir William Grant: Pacific Hydro Portland Wind Farm Pty Ltd advises that Portland Stage 4 Cape Nelson North and Cape Sir William Grant wind farm is a committed project. The 47.15 MW wind farm expected commissioning is May 2015.
Publication Date: | 2014-08-07
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm has been in full production since July 2014. The commissioning date has been revised to February 2015.
Anglesea Power Station: Alcoa of Australia Limited advises that Anglesea Power Station is changed its registration classification from Non-Scheduled to a Scheduled generator.
Publication Date: | 2014-12-10
Bald Hills Wind Farm (Phase 1): Mitsui and Co. Australia Ltd advises that Bald Hills wind farm (106.6 MW) is a committed project. The wind farm is under construction with expected commissioning in May 2015.
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm (131.2 MW) project is completed and in full commercial operation since mid 2014.
Morwell/Energy Brix: Energy Brix Australia Corporation Pty Ltd advises Morwell/Energy Brix Power Station has been withdrawn from service since August 2014.
Publication Date: | 2015-05-15
Portland Stage 4 Cape Nelson North and Cape Sir William Grant: Pacific Hydro Portland Wind Farm Pty Ltd advises that Portland Stage 4 (47.15 MW) project is completed and in full commercial operation since end of Feb 2015.
Ararat Wind Farm: Ararat Wind Farm Pty Ltd advises that Ararat wind farm (240 MW) is to start construction in July 2015 with full commercial operation expected in May 2016.
Coonooer Bridge Wind Farm: Windlab Systems Pty Ltd advises that Coonooer Bridge wind farm (19.8 MW) is to start construction in April 2015 with full commercial operation expected in March 2016.
Anglesea Power Station: Alcoa of Australia Limited advises Anglesea Power Station will retire from service from 31 August 2015 and to be decommissioned.
Publication Date: | 2015-08-13
Yallourn W Power Station: EnergyAustralia Holdings Pty Ltd advises Yallourn W Power Station has revised its available capacity to 1516 MW (+12 MW) in summer due to turbine upgrades.
Loy Yang A: AGL Energy advises Loy Yang A Power Station has revised its available capacity to 2070 MW (-30 MW) in summer due to change in performance re-evaluation. Also, revised its available capacity to 2210 MW (-60 MW) in winter due to the difficulty of producing maximum daily capacity for extended periods.
Loy Yang B: AGL Energy advises Loy Yang B Power Station has revised its available capacity to 980 MW (+15 MW) in summer due to increase in condenser vacuum limit. Also, revised its available capacity to 1070 MW (+20 MW) in winter due to increase in condenser vacuum limit.
Ararat Wind Farm: Ararat Wind Farm Pty Ltd advises that Ararat wind farm (240 MW) is to start construction in July 2015 with full commercial operation expected in May 2017.
Morwell/Energy Brix: Energy Brix Australia Corporation Pty Ltd advises Morwell/Energy Brix Power Station has temporarily closed its operations from August 2014.
Publication Date: | 2015-10-23
Coonooer Bridge Wind Farm: Windlab Systems Pty Ltd advises that Coonooer Bridge wind farm (19.8 MW) is now a committed project. Full commercial operation is expected in March 2016.
Publication Date: | 2016-03-03
Ararat Wind Farm: Ararat Wind Farm Pty Ltd advises that Ararat wind farm (240 MW) is to be in full commercial operation expected in May 2017.
Coonooer Bridge Wind Farm: Windlab Systems Pty Ltd advises that Coonooer Bridge wind farm (19.8 MW) is now a committed project. Full commercial operation is expected in March 2016.
Publication Date: | 2016-04-15
Ararat Wind Farm: Ararat Wind Farm Pty Ltd advises that Ararat wind farm (240 MW) is to be in full commercial operation expected in May 2017.
Coonooer Bridge Wind Farm: Windlab Systems Pty Ltd advises that Coonooer Bridge wind farm (19.8 MW) is now a committed project. Full commercial operation is expected in March 2016.
Publication Date: | 2016-08-11
Mt Gellibrand Wind Farm: Acciona Energy advises that Mt Gellibrand Stage 1 (66 MW) is a committed project.
New Development: Mallee Solar Park, Kiata Wind Farm.
Publication Date: | 2016-11-18
Hazelwood: Hazelwood Power advises that Hazelwood Power Station will cease generation at the end of March 2017.
Publication Date: | 2017-02-27
Kiata Wind Farm: Kiata Wind Farm Pty Ltd advises that Kiata Wind Farm (31.05 MW) is now a committed project with full commercial use expected December 2017.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Number and Nameplate Capacity (MW) | Installed Capacity (MW) | Technology Type | Fuel Type | Dispatch Type | Service Status
Bairnsdale | Alinta DEBO | 2 x 47 | 94 | OCGT | Natural Gas Pipeline | S | In Service
Bald Hills p1 | Mitsui and Co. Australia Ltd | 52 x 2.05 | 106.6 | Wind - Onshore | Wind | SS | In Service
Bogong / Mackay | AGL | 2 x 80 6 x 25 | 310 | Hydro - Gravity | Water | S | In Service
Dartmouth | AGL | 1 x 185 | 185 | Hydro - Gravity | Water | S | In Service
Eildon | AGL | 2 x 60 2 x 7.5 | 135 | Hydro - Gravity | Water | S | In Service
Hazelwood | Hazelwood Power | 8 x 200 | 1600 | Steam Sub Critical | Brown Coal | S | Announced Withdrawal
Hume VIC | Green State Power Pty Ltd | 1 x 29 | 29 | Hydro - Gravity | Water | S | In Service
Jeeralang A | Industry Funds Management Nominees Ltd | 4 x 53 | 212 | OCGT | Natural Gas Pipeline | S | In Service
Jeeralang B | Industry Funds Management Nominees Ltd | 3 x 76 | 228 | OCGT | Natural Gas Pipeline | S | In Service
Laverton North | Snowy Hydro Ltd | 2 x 156 | 312 | OCGT | Natural Gas Pipeline | S | In Service
Loy Yang A | AGL Energy | 3 x 560 1 x 500 | 2180 | Steam Sub Critical | Brown Coal | S | In Service
Loy Yang B | IPM Australia Limited | 2 x 500 | 1000 | Steam Sub Critical | Brown Coal | S | In Service
Macarthur | Macarthur Wind Farm Pty Ltd and Meridian Wind Macarthur Pty Ltd | 140 x 3 | 420 | Wind - Onshore | Wind | SS | In Service
Mortlake | Origin Energy Power Limited | 2 x 283 | 566 | OCGT | Natural Gas Pipeline | S | In Service
Mt Mercer | Mt Mercer Windfarm Pty Ltd | 64 x 2.05 | 131.2 | Wind - Onshore | Wind | SS | In Service
Murray 1 | Snowy Hydro Ltd | 10 x 95 | 950 | Hydro - Gravity | Water | S | In Service
Murray 2 | Snowy Hydro Ltd | 4 x 138 | 552 | Hydro - Gravity | Water | S | In Service
Newport | Industry Funds Manaegment Nominees Ltd | 1 x 510 | 510 | Steam Sub Critical | Natural Gas Pipeline | S | In Service
Oaklands Hill | Oaklands Hill Wind farm pty ltd | 32 x 2.1 | 67.2 | Wind - Onshore | Wind | SS | In Service
Somerton | AGL Energy | 4 x 40 | 160 | OCGT | Natural Gas Pipeline | S | In Service
Valley Power | Snowy Hydro Ltd | 6 x 50 | 300 | OCGT | Natural Gas Pipeline | S | In Service
West Kiewa | AGL | 4 x 15 | 60 | Hydro - Gravity | Water | S | In Service
Yallourn W | EnergyAustralia Holdings Pty Ltd | 2 x 350 2 x 375 | 1450 | Steam Sub Critical | Brown Coal | S | In Service
Total |  |  | 11558

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation
Power Station | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | Dispatch Type
Ararat | 170 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | SS
Bairnsdale | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | S
Bald Hills p1 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 1600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hume VIC | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Jeeralang A | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | S
Jeeralang B | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | S
Laverton North | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Loy Yang A | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | S
Loy Yang B | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | S
Macarthur | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | SS
Mortlake | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | S
Mt Gellibrand | 0 | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Murray 1 | 950 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | S
Murray 2 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | S
Newport | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | S
Oaklands Hill | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | SS
Somerton | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | S
Valley Power | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | S
West Kiewa | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | S
Total | 11229.71 | 9559.71 | 9625.71 | 9625.71 | 9625.71 | 9625.71 | 9625.71 | 9625.71 | 9625.71 | 9625.71
The table above lists the latest Summer capacities for Victorian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 7.5% of the installed capacity during summer, and 6.8% during winter, based on AEMO's analysis of historical wind output over summer 2011-12 to 2015-16, and winter 2011 - 2015.
The two tables below have been included to better represent the supply availability in Victoria, by taking into account the firm contribution by semi-scheduled generation. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the summer period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation
Power Station | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | Dispatch Type
Bairnsdale | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | S
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 1600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hume VIC | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Jeeralang A | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | S
Jeeralang B | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | S
Laverton North | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Loy Yang A | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | 2070 | S
Loy Yang B | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | S
Mortlake | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | S
Murray 1 | 950 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | S
Murray 2 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | S
Newport | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | S
Somerton | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | 133.51 | S
Valley Power | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | S
West Kiewa | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | 1420 | S
Firm Wind Capacity | 59.565 | 61.44 | 66.39 | 66.39 | 66.39 | 66.39 | 66.39 | 66.39 | 66.39 | 66.39 | SS
Total | 10495.075 | 8801.95 | 8806.9 | 8806.9 | 8806.9 | 8806.9 | 8806.9 | 8806.9 | 8806.9 | 8806.9
Summer aggregate available semi-scheduled generation
Power Station | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | Dispatch Type
Ararat | 170 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | SS
Bald Hills p1 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Macarthur | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | SS
Mt Gellibrand | 0 | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Oaklands Hill | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | SS
Total (Wind) | 794.2 | 819.2 | 885.2 | 885.2 | 885.2 | 885.2 | 885.2 | 885.2 | 885.2 | 885.2

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation
Power Station | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Dispatch Type
Ararat | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | SS
Bairnsdale | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Bald Hills p1 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hume VIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Jeeralang A | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | S
Jeeralang B | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | S
Laverton North | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | S
Loy Yang A | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | S
Loy Yang B | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | S
Macarthur | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | SS
Mortlake | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | S
Mt Gellibrand | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Murray 1 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | S
Murray 2 | 560 | 560 | 560 | 420 | 420 | 420 | 560 | 560 | 560 | 560 | S
Newport | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | S
Oaklands Hill | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | SS
Somerton | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | S
Valley Power | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | S
West Kiewa | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | S
Total | 10408.3 | 10474.3 | 10474.3 | 10334.3 | 10334.3 | 10334.3 | 10474.3 | 10474.3 | 10474.3 | 10474.3
The table above lists the latest Winter capacities for Victorian generation. Winter conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 7.5% of the installed capacity during summer, and 6.8% during winter, based on AEMO's analysis of historical wind output over summer 2011-12 to 2015-16, and winter 2011 - 2015.
The two tables below have been included to better represent the supply availability in Victoria, by taking into account the firm contribution by semi-scheduled generation. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the winter period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation
Power Station | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Dispatch Type
Bairnsdale | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hume VIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Jeeralang A | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | S
Jeeralang B | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | S
Laverton North | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | S
Loy Yang A | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | 2210 | S
Loy Yang B | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | S
Mortlake | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | S
Murray 1 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | S
Murray 2 | 560 | 560 | 560 | 420 | 420 | 420 | 560 | 560 | 560 | 560 | S
Newport | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | S
Somerton | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | S
Valley Power | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | S
West Kiewa | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | 1528 | S
Firm Wind Capacity | 65.3344 | 69.8224 | 69.8224 | 69.8224 | 69.8224 | 69.8224 | 69.8224 | 69.8224 | 69.8224 | 69.8224 | SS
Total | 9512.8344 | 9517.3224 | 9517.3224 | 9377.3224 | 9377.3224 | 9377.3224 | 9517.3224 | 9517.3224 | 9517.3224 | 9517.3224
Winter aggregate available semi-scheduled generation
Power Station | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Dispatch Type
Ararat | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | SS
Bald Hills p1 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Macarthur | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | SS
Mt Gellibrand | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Oaklands Hill | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | SS
Total (Wind) | 960.8 | 1026.8 | 1026.8 | 1026.8 | 1026.8 | 1026.8 | 1026.8 | 1026.8 | 1026.8 | 1026.8

## Existing NS Generation
Existing non-scheduled generation
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type | Service Status
200 Victoria St | Cogent Energy Pty Ltd | 0.386 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
321 Exhibition Street Trigen | Cogent Energy | 1.2 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
990 Latrobe St | Cogent Energy Pty Ltd | 0.386 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
Ballarat | LMS ENERGY Pty Ltd | 0.789 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Ballarat Base Hospital | Ballarat Base Hospital | 3.06 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Banimboola | AGL | 12.2 | Hydro - Gravity | Water | In service
Belgrave-Hallam Rd Micro Hydro | South East Water | 0.25 | Hydro - Gravity | Water | In service
Bendigo | LMS ENERGY Pty Ltd | 0.5 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Berwick | EDL LFG Vic Pty Ltd | 4.57 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Broadmeadows | EDL LFG Vic Pty Ltd | 6.18 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Brooklyn | EDL LFG Vic Pty Ltd | 2.83 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Challicum Hills | Pacific Hydro Challicum Hills Pty Ltd | 52.5 | Wind - Onshore | Wind | In service
Chepstowe Wind Farm | Chepstowe Wind Farm Pty Ltd | 6.15 | Wind - Onshore | Wind | In service
Clayton | EDL LFG Vic Pty Ltd | 12 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Clover | AGL | 29 | Hydro - Gravity | Water | In service
Codrington | Energy Pacific Vic Pty Ltd | 18.2 | Wind - Onshore | Wind | In service
Coonooer Bridge Wind Farm | Windlab Systems Pty Ltd | 19.8 | Wind - Onshore | Wind | In service
Corio | EDL LFG Vic Pty Ltd | 1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Crown Melbourne | Crown Resorts | 5.58 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Dandenong PEP | Cogent Energy Pty Ltd | 2 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
Diamond Energy Shepparton | Diamond Energy Pty Ltd | 1.1 | Spark Ignition Reciprocating Engine | Sewerage / Waste Water | In service
Diamond Energy Tatura | Diamond Energy Pty Ltd | 1.1 | Spark Ignition Reciprocating Engine | Sewerage / Waste Water | In service
Eildon Small Hydro | Pacific Hydro Investments Pty Ltd | 4.5 | Hydro - Gravity | Water | In service
Glenmaggie Hydro | Pacific Hydro Investments Pty Ltd | 3.8 | Hydro - Gravity | Water | In service
Hallam Road | LMS Energy Pty Ltd | 8.984 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Leonards Hill | Hepburn Community Wind Park Co-operative Limited | 4.1 | Wind - Onshore | Wind | In service
Longford | Longford Gas Plant | 31.8 | OCGT | Natural Gas Pipeline | In service
Mornington Waste Disposal Facility | LMS Energy Pty Ltd | 0.77 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Mortons Lane Wind Farm | Mortons Lane Windfarm Pty Ltd | 19.5 | Wind - Onshore | Wind | In service
Portland Wind Farm | Pacific Hydro Portland Wind Farm Pty Ltd | 149.15 | Wind - Onshore | Wind | In service
Qenos Cogeneration Facility | AGL | 21 | CCGT | Natural Gas Pipeline | In service
Rubicon Mountain Streams | AGL | 13.5 | Hydro - Gravity | Water | In service
Shepparton | LMS ENERGY Pty Ltd | 0.78 | Spark Ignition Reciprocating Engine | Non-biomass recycled municipal and industrial materials | In service
South East Water - Hallam Plant | South East Water | 0.25 | Hydro - Gravity | Water | In service
Springvale | EDL LFG Vic Pty Ltd | 4.2 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Toora | Ratch Australia | 21 | Wind - Onshore | Wind | In service
Waubra | Pyrenees Wind Energy Developments | 192 | Wind - Onshore | Wind | In service
William Hovel | Pacific Hydro Investments Pty Ltd | 1.8 | Hydro - Gravity | Water | In service
Wollert | LMS Energy Pty Ltd | 6.738 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Wonthaggi | Regional Wind Farms | 12 | Wind - Onshore | Wind | In service
Wyndham Renewable Energy Facility | LMS Energy Pty Ltd | 1.903 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Yambuk | Energy Pacific Vic Pty Ltd | 30 | Wind - Onshore | Wind | In service
Yarrawonga | AGL | 9.5 | Hydro - Gravity | Water | In service
Total |  | 718.056

## New Developments
Projects under development
Project | Owner | Unit ID | Technology Type | Fuel Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Full Commercial Use Date
Ararat | Ararat Wind Farm Pty Ltd | 1-75 | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 240 | SS | May 2017
Bannerton Solar Park | Syncline Energy Pty Ltd | 1 | PV panels | Solar | [5 empty] | Pub An | 51.2 | SS | TBA
Ben More | Ratch Australia | 23 - 37 | Wind - Onshore | Wind | [5 empty] | Pub An | 70 - 110 | SS | TBA
Berrimal | ACCIONA Energy | 1-24 | Wind - Onshore | Wind | [5 empty] | Pub An | 24-66 | SS | TBA
Berrybank Wind Farm | Berrybank Development Pty Ltd | Units 1-79 | Wind - Onshore | Wind | [5 empty] | Pub An | 260 | SS | Oct 2019
Bulgana Wind Farm | Enerfin Energy Company of Australia Pty Ltd | 1-63 | [7 empty] | Pub An | TBA | SS | TBA
Cherry Tree Wind Farm | Infigen Energy | Units 1-16 | Wind - Onshore | Wind | [5 empty] | Pub An | 48 | SS | TBA
Crowlands | Energy Pacific Vic Pty Ltd | 1-63 | Wind - Onshore | Wind | [5 empty] | Pub An | 82 | SS | TBA
Darlington Wind Farm | Union Fenosa Wind Australia Pty Ltd | Units 1-70 | Wind - Onshore | Wind | [5 empty] | Pub An | 350 | SS | TBA
Dundonnell | Tilt Renewables | 1-96 | Wind - Onshore | Wind | [5 empty] | Pub An | 288 | SS | Dec 2019
Gannawarra Solar Farm | Gannawarra Solar Farm Pty Ltd | 1 | PV panels | Solar | [5 empty] | Pub An | 52.8 | SS | TBA
Hawkesdale Wind Farm | Ryan Corner Development Pty Ltd | Units 1-26 | Wind - Onshore | Wind | [5 empty] | Pub An | 91 | SS | TBA
Kerang Solar Farm | Kerang Solar Farm Pty Ltd | 1 | PV panels | Solar | [5 empty] | Pub An | 60 | NS | TBA
Kiata Wind Farm | Kiata Wind Farm Pty Ltd | 1-9 | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 31.05 | TBA | Dec 2017
Lal Lal Wind Energy Facility - Elaine end | Westwind Energy Pty Ltd | 39-60 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 60-79 | SS | Dec 2018
Lal Lal Wind Energy Facility - Yendon end | Westwind Energy Pty Ltd | 1-38 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 104-137 | SS | Dec 2018
Mallee Solar Park | EnergyAustralia | 1 |  | Solar | [5 empty] | Pub An | TBA | NS | TBA
Moorabool | Moorabool Wind Farm Pty Ltd | 1-50 51-107 | Wind - Onshore Wind - Onshore | Wind | [5 empty] | Pub An | 214-342 | SS | Jul 2019
Mortlake South | ACCIONA Energy | 1-42 | Wind - Onshore | Wind | [5 empty] | Pub An | 126 | SS | TBA
Mt Gellibrand | ACCIONA Energy | 23-44 | Wind - Onshore | Wind | [5 empty] | Pub An | 66 | SS | Dec 2018
| ACCIONA Energy | 1-22 | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 66 | SS | Jun 2018
Penshurst | RES Australia Pty Ltd | 1-134 | Wind - Onshore | Wind | [5 empty] | Pub An | 198 | SS | TBA
Port Phillip Heads Tidal Energy Project | Tenax Energy | 1 | Tidal | Water | [5 empty] | Pub An | 34 | NS | TBA
Ryan Corner Wind Farm | Ryan Corner Development Pty Ltd | Units 1-56 | Wind - Onshore | Wind | [5 empty] | Pub An | 196 | SS | TBA
Salt Creek | Tilt Renewables | 1-15 | Wind - Onshore | Wind |  |  |  |  | ü | Pub An | 50 | SS | Jun 2018
Shaw River Power Station | Santos TGR Pty Ltd | Shaw River 1 | CCGT | Natural Gas Pipeline | [5 empty] | Pub An | 500 | S | TBA
Stockyard Hill | Origin Energy | 1-149 | Wind - Onshore | Wind | [5 empty] | Pub An | 536 | SS | TBA
Tarrone GT | AGL Energy Limited | 1-2 | OCGT | Natural Gas Pipeline | [5 empty] | Pub An | 500-600 | S | TBA
Tarrone Wind Farm | Union Fenosa Wind Australia Pty Ltd | Units 1-17 | Wind - Onshore | Wind | [5 empty] | Pub An | 54 | SS | TBA
Willatook | Wind Prospect WA Pty Ltd | 1-145 | Wind - Onshore | Wind | [5 empty] | Pub An | 261 | SS | TBA
Woolsthorpe | Woolsthorpe Wind Farm Pty Ltd | 20 | Wind - Onshore | Wind | [5 empty] | Pub An | 50 approx | SS | Mar 2018
Yaloak South | Energy Pacific Vic Pty Ltd | 1-14 | Wind - Onshore | Wind | [5 empty] | Pub An | 28.7 | NS | TBA
Note: if nameplate capacity is provided as a range the maximum will be used when summarising the data.

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as semi-scheduled or non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as scheduled or non-scheduled. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW, unless AEMO approves its classification as scheduled or semi-scheduled.
Generating systems greater than 30 MW must be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating of less than 5 MW may be exempted by AEMO if its generation is purchased entirely by the local retail or a customer at the generator's connection point or the generator is classified as a market generating unit by a market small generation aggregator. A generating unit with a nameplate rating between 5 MW and 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.