## Details
COMMISSIONING TEST PLAN | [7 empty] | USER INSTRUCTIONS
FACILITY DETAILS
[8 empty] | 1 | This spreadsheet must be completed and submitted to Market Operations to be regarded as a valid request for a Commissioning Test Plan for a Facility.
Market Participant: | ALINTA
[8 empty] | 2 | Data entry is restricted to the areas shaded yellow and green (yellow being mandatory), which have built-in automatic checks to validate entered data.
Facility: | ALINTA_PNJ_U2
[8 empty] | 3 | The following fields are mandatory: Market Participant, Facility, Email Address, Start and End Trading Days, Purpose of Test and Test Description. The Commissioning Test Plan will not be accepted by System Management unless these fields are completed.
Contact Details: |  | Operational |  |  | Commercial
| Email | clifford.merwood@alcoa.com.au |  |  | robbie.flood@alintaenergy.com.au
| Mobile | 0404800156 |  |  | 424983938 |  |  | 4 | For Commissioning Tests exceeding one Trading Day, please make copies of the 'DDMMYYYY' worksheet. The worksheet will automatically rename when entering the Trading Day of test within the Details worksheet.
| Phone | 95574397 |  |  | 293722651
| Fax | 95302589 |  |  | 894863217
[8 empty] | 5 | Details within the 'DDMMYYYY' worksheet (Commissioning Test Schedule) are also mandatory and required in order for the Commissioning Test Plan to be accepted by System Management.
Fuel Types: | Fuel "1" |  |  | Fuel "2" |  | Fuel "3"
| Natural Gas | [6 empty] | 6 | Separate Commissioning Test Plan templates are required to be completed for each Facility registered in the Wholesale Electricity Market.
TEST DETAILS | [7 empty] | 7 | Please email all completed Commissioning Test Plan templates to Market Operations; market.operations@westernpower.com.au
Associated Outage No: | 210801 | [7 empty] | Commissioning Test Plan template v1.0
| START |  |  |  | END
Commissioning Test Period: | Trading Day |  | Trading Interval |  | Trading Day |  | Trading Interval
| 2014-04-17 |  | 8:00 |  | 2014-04-17 |  | 7:30
Purpose of Test: | The plan only covers the initial commissioning of the bypass system after the construction phase and specificly deals with the commissioning steps required to confirm the bypass system is operating correctly for GT loads down to 55MW. For loads lower than this level a load test and operational trial will be used in accordance with the SH3/4 Bypass implementation plan at a later date.
Test Description | Start in a normal manner (with the bypass and isolation valves in service) and be loaded to 85MW GT Load. During this start up the following will occur. · Final leak check of installed piping at Load Hold 1 Point (GT load – 28MW) · Testing of the new SH PSV at the Load Hold Point 2 (GT load - 70MW). Once 85MW has been reached duct burners shall be started up and a steam make of 250tph would be established. Approximately 10 minutes before the first load change venting of steam will be established to supply 100 tph to the refinery and the remainder of steam load to vent. This is to avoid an upset to the refinery if the transition does not occur as expected. The GT Load will then be reduced to 55MW in 10MW steps with a 30 minute pause at each load. Once a 55MW the load will be returned to 85MW again at 10MW steps with a 30 minute pause at each load. If the valve transition, is shown to be successful, (measured by steam supply staying within steam quality parameters for flow (210 to 250tph) and temperature (465 to 485 DegC) then the vent will be closed and full steam supply will be returned to the refinery from the cogen unit under test. Once shown to hold steam inside the required contractual parameters, two more transitions from 85MW to 55MW and back will be completed to allow fine tuning of the transition points, (these tunning points are to be determined and agreed by both Alcoa and Alinta). These two transition cycles will be done in one step at normal ramp rates with a 30 minute pause at the 55MW level in each cycle. Further transition changes may be organised by Alcoa on this day to allow further operator training.
System Under Test: | ALINTA_PNJ_U2
Contingency Plan: | Should there be additional requirements, an updated commissioning plan will be provided to System Management requesting these changes.

## 17042014
| COMMISSIONING TEST SCHEDULE | [7 empty] | COMMISSIONING TEST SCHEDULE PROFILES
(Make copy of sheet for additional Trading Days)
TIME |  | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
Date of test | Interval start time | Active Power (MW) | Reactive Power (MVAr) | Natural Gas | Low, Medium or High | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
2014-04-17 | 8:00 | 0 | 0 | Natural Gas | Low |  |  | FSNL - Trip for High Temperature
2014-04-17 | 8:30 | 0 | 0 | Natural Gas | Low
2014-04-17 | 9:00 | 0 | 20 | Natural Gas | Low
2014-04-17 | 9:30 | 28 | 20 | Natural Gas | Low |  |  | Load Hold 1 - Leak inspection
2014-04-17 | 10:00 | 70 | 20 | Natural Gas | Low |  |  | Load Hold 2 - SH PSV testing
2014-04-17 | 10:30 | 70 | 20 | Natural Gas | Low |  |  | Duct burners on and set steam make to 250 tph
2014-04-17 | 11:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 11:30 | 75 | 20 | Natural Gas | Low |  |  | Open Start up vent - 100 tph to refinery 150 tph to vent
2014-04-17 | 12:00 | 65 | 20 | Natural Gas | Low
2014-04-17 | 12:30 | 55 | 20 | Natural Gas | Low
2014-04-17 | 13:00 | 65 | 20 | Natural Gas | Low
2014-04-17 | 13:30 | 75 | 20 | Natural Gas | Low
2014-04-17 | 14:00 | 85 | 20 | Natural Gas | Low |  |  | Close vent and return steam flow to 250 tph
2014-04-17 | 14:30 | 55 | 20 | Natural Gas | Low
2014-04-17 | 15:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 15:30 | 55 | 20 | Natural Gas | Low
2014-04-17 | 16:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 16:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 17:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 17:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 18:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 18:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 19:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 19:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 20:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 20:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 21:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 21:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 22:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 22:30 | 85 | 20 | Natural Gas | Low
2014-04-17 | 23:00 | 85 | 20 | Natural Gas | Low
2014-04-17 | 23:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 24:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 24:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 25:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 25:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 26:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 26:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 27:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 27:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 28:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 28:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 29:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 29:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 30:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 30:30 | 85 | 20 | Natural Gas | Low
2014-04-18 | 31:00 | 85 | 20 | Natural Gas | Low
2014-04-18 | 31:30 | 85 | 20 | Natural Gas | Low
| Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
| 2014-04-17 | 2014-04-17 |  | Natural Gas | Low | C1 | S1
[5 empty] | Medium | C2A | S2
[5 empty] | High | C2B | S3
[6 empty] | C3A | S4
[6 empty] | C3B | S5
[6 empty] | C4 | S6
[6 empty] | C5 | S7
[6 empty] | C6 | S8
[6 empty] | C7 | S9
[6 empty] | C8 | S10
[6 empty] | C9 | S11
S12
S13