## Details
COMMISSIONING GENERATION TEST DETAILS
GENERATOR DETAILS
Market Participant: | Verve Energy, Kwinana Power Station
Facility Designation: | Unit 6 (K6)
Contact Details: |  | Operational |  |  | Commercial
| Email | peter.payze@verveenergy.com.au |  |  | clive.hebbard@verveenergy.com.au
| Mobile |  |  |  | 0429 043 124
| Phone | 94112608 |  |  | 94112508
Fax
Fuel Types: | Fuel "1" |  |  | Fuel "2" |  | Fuel "3"
| natural gas |  |  | coal |  | fuel oil
TEST DETAILS
Test Period: | Start Date |  | Start Time |  | End Date |  | End Time
| 2013-08-28 |  | 8:00 |  | 2013-09-18 |  | 22:30
Purpose of Test(s): | K6 commissioning following B Class Overhaul
System Under Test: | Kwinana Power Station Unit G6
Test Description | Unit tuning, vibration monitoring, and load tests required following B Class Overhaul.
Contingency Plan(s): | Should the unit require additional tuning or the load profile require modification a request will be made to system management. Detailed and regular communication between Kwinana and System Management to ensure system stability.

## 7 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-07 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0 | 0 | natural gas | low |  |  | Run to speed
8:30 | 0 | 0 | natural gas | low |  |  | Run to speed and synchronise
9:00 | 30 | 5 | natural gas | medium |  |  | Pedestal checks
9:30 | 50 | 5 | natural gas | medium |  |  | Pedestal checks
10:00 | 50 | 5 | natural gas | medium |  |  | Pedestal checks
10:30 | 50 | 5 | natural gas | medium |  |  | Pedestal checks
11:00 | 50 | 5 | natural gas | medium |  |  | Pedestal checks
11:30 | 50 | 5 | natural gas | medium |  |  | Pedestal checks
12:00 | 30 | 5 | natural gas | medium |  |  | Pedestal checks
12:30 | 20 | 5 | natural gas | medium |  |  | Pedestal checks
13:00 | 0 | 0 | natural gas | low |  |  | Overspeed checks
13:30 | 0 | 0 | natural gas | low |  |  | Overspeed checks
14:00 | 0 | 0 |  |  |  |  | Run to T/G cool down
14:30 | 0 | [5 empty] | Cool down
15:00 | 0 | [5 empty] | Cool down
15:30 | 0 | [5 empty] | Cool down
16:00 | 0 | [5 empty] | Cool down
16:30 | 0 | [5 empty] | Cool down
17:00 | 0 | [5 empty] | Cool down
17:30 | 0 | [5 empty] | Cool down
18:00 | 0 | [5 empty] | Cool down
18:30 | 0 | [5 empty] | Cool down
19:00 | 0 | [5 empty] | Cool down
19:30 | 0 | [5 empty] | Cool down
20:00 | 0 | [5 empty] | Cool down
20:30 | 0 | [5 empty] | Cool down
21:00 | 0 | [5 empty] | Cool down
21:30 | 0 | [5 empty] | Cool down
22:00 | 0 | [5 empty] | Cool down
22:30 | 0 | [5 empty] | Cool down
23:00 | 0 | [5 empty] | Cool down
23:30 | 0 | [5 empty] | Cool down
24:00 | 0 | [5 empty] | Cool down
24:30 | 0 | [5 empty] | Cool down
25:00 | 0 | [5 empty] | Cool down
25:30 | 0 | [5 empty] | Cool down
26:00 | 0 | [5 empty] | Pre-warm turbine
26:30 | 0 | [5 empty] | Pre-warm turbine
27:00 | 0 | [5 empty] | Pre-warm turbine
27:30 | 0 | [5 empty] | Pre-warm turbine
28:00 | 0 | [5 empty] | Pre-warm turbine
28:30 | 0 | [5 empty] | Pre-warm turbine
29:00 | 0 | [5 empty] | Pre-warm turbine
29:30 | 0 | [5 empty] | Pre-warm turbine
30:00 | 0 | [5 empty] | Cool down
30:30 | 0 | [5 empty] | Cool down
31:00 | 0 | [5 empty] | Cool down
31:30 | 0 | [5 empty] | Cool down
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 8 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-08 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0 | [5 empty] | Cool down for bolt adjustment
8:30 | 0 | [5 empty] | Cool down for bolt adjustment
9:00 | 0 | [5 empty] | Cool down for bolt adjustment
9:30 | 0 | [5 empty] | Cool down for bolt adjustment
10:00 | 0 | [5 empty] | Cool down for bolt adjustment
10:30 | 0 | [5 empty] | Cool down for bolt adjustment
11:00 | 0 | [5 empty] | Cool down for bolt adjustment
11:30 | 0 | [5 empty] | Cool down for bolt adjustment
12:00 | 0 | [5 empty] | Cool down for bolt adjustment
12:30 | 0 | [5 empty] | Cool down for bolt adjustment
13:00 | 0 | [5 empty] | Cool down for bolt adjustment
13:30 | 0 | [5 empty] | Cool down for bolt adjustment
14:00 | 0 | [5 empty] | Cool down for bolt adjustment
14:30 | 0 | [5 empty] | Cool down for bolt adjustment
15:00 | 0 | [5 empty] | Cool down for bolt adjustment
15:30 | 0 | [5 empty] | Cool down for bolt adjustment
16:00 | 0 | [5 empty] | Cool down for bolt adjustment
16:30 | 0 | [5 empty] | Cool down for bolt adjustment
17:00 | 0 | [5 empty] | Cool down for bolt adjustment
17:30 | 0 | [5 empty] | Cool down for bolt adjustment
18:00 | 0 | [5 empty] | Cool down for bolt adjustment
18:30 | 0 | [5 empty] | Cool down for bolt adjustment
19:00 | 0 | [5 empty] | Cool down for bolt adjustment
19:30 | 0 | [5 empty] | Cool down for bolt adjustment
20:00 | 0 | [5 empty] | Cool down for bolt adjustment
20:30 | 0 | [5 empty] | Cool down for bolt adjustment
21:00 | 0 | [5 empty] | Cool down for bolt adjustment
21:30 | 0 | [5 empty] | Cool down for bolt adjustment
22:00 | 0 | [5 empty] | Cool down for bolt adjustment
22:30 | 0 | [5 empty] | Cool down for bolt adjustment
23:00 | 0 | [5 empty] | Cool down for bolt adjustment
23:30 | 0 | [5 empty] | Cool down for bolt adjustment
24:00 | 0 | [5 empty] | Cool down for bolt adjustment
24:30 | 0 | [5 empty] | Cool down for bolt adjustment
25:00 | 0 | [5 empty] | Cool down for bolt adjustment
25:30 | 0 | [5 empty] | Cool down for bolt adjustment
26:00 | 0 | [5 empty] | Cool down for bolt adjustment
26:30 | 0 | [5 empty] | Cool down for bolt adjustment
27:00 | 0 | [5 empty] | Cool down for bolt adjustment
27:30 | 0 | [5 empty] | Cool down for bolt adjustment
28:00 | 0 | [5 empty] | Cool down for bolt adjustment
28:30 | 0 | [5 empty] | Cool down for bolt adjustment
29:00 | 0 | [5 empty] | Cool down for bolt adjustment
29:30 | 0 | [5 empty] | Cool down for bolt adjustment
30:00 | 0 | [5 empty] | Cool down for bolt adjustment
30:30 | 0 | [5 empty] | Cool down for bolt adjustment
31:00 | 0 | [5 empty] | Cool down for bolt adjustment
31:30 | 0 | [5 empty] | Cool down for bolt adjustment
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 9 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-09 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0 | [5 empty] | Governor adjustments
8:30 | 0 | [5 empty] | Governor adjustments
9:00 | 0 | [5 empty] | Governor adjustments
9:30 | 0 | [5 empty] | Governor adjustments
10:00 | 0 | [5 empty] | Governor adjustments
10:30 | 0 | [5 empty] | Governor adjustments
11:00 | 0 | [5 empty] | Governor adjustments
11:30 | 0 | [5 empty] | Governor adjustments
12:00 | 0 | [5 empty] | Governor adjustments
12:30 | 0 | 0 | natural gas | low |  |  | Pressure raising
13:00 | 0 | 0 | natural gas | low |  |  | Pressure raising
13:30 | 0 | 0 | natural gas | low |  |  | Pressure raising
14:00 | 0 | 0 | natural gas | low |  |  | Run to speed
14:30 | 0 | 0 | natural gas | low |  |  | Aux Governor setting
15:00 | 30 | 5 | natural gas | medium |  |  | Load machine to 30MW
15:30 | 50 | 5 | natural gas | medium |  |  | Governor tests
16:00 | 50 | 5 | natural gas | medium |  |  | Governor tests
16:30 | 0 | [5 empty] | Shut down
17:00 | 0 | [5 empty] | Hot bank boiler
17:30 | 0 | [5 empty] | Hot bank boiler
18:00 | 0 | [5 empty] | Hot bank boiler
18:30 | 0 | [5 empty] | Hot bank boiler
19:00 | 0 | [5 empty] | Hot bank boiler
19:30 | 0 | [5 empty] | Hot bank boiler
20:00 | 0 | [5 empty] | Hot bank boiler
20:30 | 0 | [5 empty] | Hot bank boiler
21:00 | 0 | [5 empty] | Hot bank boiler
21:30 | 0 | [5 empty] | Hot bank boiler
22:00 | 0 | [5 empty] | Hot bank boiler
22:30 | 0 | [5 empty] | Hot bank boiler
23:00 | 0 | [5 empty] | Hot bank boiler
23:30 | 0 | [5 empty] | Hot bank boiler
24:00 | 0 | [5 empty] | Hot bank boiler
24:30 | 0 | [5 empty] | Hot bank boiler
25:00 | 0 | [5 empty] | Hot bank boiler
25:30 | 0 | [5 empty] | Hot bank boiler
26:00 | 0 | [5 empty] | Hot bank boiler
26:30 | 0 | [5 empty] | Hot bank boiler
27:00 | 0 | [5 empty] | Hot bank boiler
27:30 | 0 | [5 empty] | Hot bank boiler
28:00 | 0 | [5 empty] | Hot bank boiler
28:30 | 0 | [5 empty] | Hot bank boiler
29:00 | 0 | [5 empty] | Hot bank boiler
29:30 | 0 | [5 empty] | Hot bank boiler
30:00 | 0 | [5 empty] | Hot bank boiler
30:30 | 0 | [5 empty] | Hot bank boiler
31:00 | 0 | [5 empty] | Hot bank boiler
31:30 | 0 | [5 empty] | Hot bank boiler
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 10 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-10 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0 |  | natural gas | medium |  |  | Run to speed
8:30 | 30 | 5 | natural gas | medium |  |  | Synchronise
9:00 | 50 | 5 | natural gas | low |  |  | Vibration analysis
9:30 | 50 | 5 | natural gas | low |  |  | Vibration analysis
10:00 | 80 | 5 | natural gas | low |  |  | Vibration analysis
10:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
11:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
11:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
12:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
12:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
13:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
13:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
14:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning test
14:30 | 90 | 10 | natural gas & coal | low |  |  | Mill commissioning test
15:00 | 90 | 10 | natural gas & coal | low |  |  | Mill commissioning test
15:30 | 90 | 10 | natural gas & coal | low |  |  | Mill commissioning test
16:00 | 100 | 10 | natural gas & coal | low |  |  | Mill commissioning test
16:30 | 100 | 10 | natural gas & coal | low |  |  | Mill commissioning test
17:00 | 100 | 10 | natural gas & coal | low |  |  | Mill commissioning test
17:30 | 80 | 5 | natural gas & coal | low |  |  | Reduce load
18:00 | 80 | 5 | natural gas & coal | low |  |  | Hold and monitor
18:30 | 80 | 5 | natural gas & coal | low |  |  | Hold and monitor
19:00 | 50 | 5 | natural gas | low |  |  | Reduce load
19:30 | 50 | 5 | natural gas | low |  |  | Hold and monitor
20:00 | 0 | 0 | natural gas | low |  |  | Monitor run down
20:30 | 0 | 0 |  |  |  |  | Hot Bank Boiler
21:00 | 0 | 0 |  |  |  |  | Hot Bank Boiler
21:30 | 0 | 0 |  |  |  |  | Hot Bank Boiler
22:00 | 0 | 0 |  |  |  |  | Hot Bank Boiler
22:30 | 0 | [5 empty] | Hot Bank Boiler
23:00 | 0 | [5 empty] | Hot Bank Boiler
23:30 | 0 | [5 empty] | Hot Bank Boiler
24:00 | 0 | [5 empty] | Hot Bank Boiler
24:30 | 0 | [5 empty] | Hot Bank Boiler
25:00 | 0 | [5 empty] | Hot Bank Boiler
25:30 | 0 | [5 empty] | Hot Bank Boiler
26:00 | 0 | [5 empty] | Hot Bank Boiler
26:30 | 0 | [5 empty] | Hot Bank Boiler
27:00 | 0 | [5 empty] | Hot Bank Boiler
27:30 | 0 | [5 empty] | Hot Bank Boiler
28:00 | 0 | [5 empty] | Hot Bank Boiler
28:30 | 0 | [5 empty] | Hot Bank Boiler
29:00 | 0 | [5 empty] | Hot Bank Boiler
29:30 | 0 | [5 empty] | Hot Bank Boiler
30:00 | 0 | [5 empty] | Hot Bank Boiler
30:30 | 0 | [5 empty] | Hot Bank Boiler
31:00 | 0 | [5 empty] | Hot Bank Boiler
31:30 | 0 | [5 empty] | Hot Bank Boiler
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 11 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-11 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0 | 0 | natural gas |  |  |  | Run to speed
8:30 | 30 | 5 | natural gas | medium |  |  | synchronise
9:00 | 50 | 5 | natural gas | low |  |  | increase load
9:30 | 80 | 5 | natural gas | low |  |  | increase load
10:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
10:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
11:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
11:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
12:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
12:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
13:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
13:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
14:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
14:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
15:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
15:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
16:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
16:30 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
17:00 | 80 | 5 | natural gas & coal | low |  |  | Mill commissioning tests
17:30 | 50 | 5 | natural gas | low |  |  | reduce load
18:00 | 30 | 5 | natural gas | low |  |  | reduce load
18:30 | 0 | 0 | natural gas | low |  |  | monitor run down
19:00 | 0 | 0 |  |  |  |  | hot bank boiler
19:30 | 0 | 0 |  |  |  |  | hot bank boiler
20:00 | 0 | 0 |  |  |  |  | hot bank boiler
20:30 | 0 | 0 |  |  |  |  | hot bank boiler
21:00 | 0 | 0 |  |  |  |  | hot bank boiler
21:30 | 0 | 0 |  |  |  |  | hot bank boiler
22:00 | 0 | 0 |  |  |  |  | hot bank boiler
22:30 | 0 | [5 empty] | hot bank boiler
23:00 | 0 | [5 empty] | hot bank boiler
23:30 | 0 | [5 empty] | hot bank boiler
24:00 | 0 | [5 empty] | hot bank boiler
24:30 | 0 | [5 empty] | hot bank boiler
25:00 | 0 | [5 empty] | hot bank boiler
25:30 | 0 | [5 empty] | hot bank boiler
26:00 | 0 | [5 empty] | hot bank boiler
26:30 | 0 | [5 empty] | hot bank boiler
27:00 | 0 | [5 empty] | hot bank boiler
27:30 | 0 | [5 empty] | hot bank boiler
28:00 | 0 | [5 empty] | hot bank boiler
28:30 | 0 | [5 empty] | hot bank boiler
29:00 | 0 | [5 empty] | hot bank boiler
29:30 | 0 | [5 empty] | hot bank boiler
30:00 | 0 | [5 empty] | hot bank boiler
30:30 | 0 | [5 empty] | hot bank boiler
31:00 | 0 | [5 empty] | hot bank boiler
31:30 | 0 | [5 empty] | hot bank boiler
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 12 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-12 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 30 | 5 | natural gas | medium |  |  | synchronise
8:30 | 60 | 5 | natural gas | low |  |  | raise load
9:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
9:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
10:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
10:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
11:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
11:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
12:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
12:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
13:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
13:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
14:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
14:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
15:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
15:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
16:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
16:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
17:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
17:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
18:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
18:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
19:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
19:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance test
20:00 | 60 | 5 | natural gas | low |  |  | Reduce load
20:30 | 30 | 5 | natural gas | low |  |  | Reduce load
21:00 | 0 | 0 |  |  |  |  | Monitor rundown
21:30 | 0 | [5 empty] | Hot bank boiler
22:00 | 0 | [5 empty] | Hot bank boiler
22:30 | 0 | [5 empty] | Hot bank boiler
23:00 | 0 | [5 empty] | Hot bank boiler
23:30 | 0 | [5 empty] | Hot bank boiler
24:00 | 0 | [5 empty] | Hot bank boiler
24:30 | 0 | [5 empty] | Hot bank boiler
25:00 | 0 | [5 empty] | Hot bank boiler
25:30 | 0 | [5 empty] | Hot bank boiler
26:00 | 0 | [5 empty] | Hot bank boiler
26:30 | 0 | [5 empty] | Hot bank boiler
27:00 | 0 | [5 empty] | Hot bank boiler
27:30 | 0 | [5 empty] | Hot bank boiler
28:00 | 0 | [5 empty] | Hot bank boiler
28:30 | 0 | [5 empty] | Hot bank boiler
29:00 | 0 | [5 empty] | Hot bank boiler
29:30 | 0 | [5 empty] | Hot bank boiler
30:00 | 0 | [5 empty] | Hot bank boiler
30:30 | 0 | [5 empty] | Hot bank boiler
31:00 | 0 | [5 empty] | Hot bank boiler
31:30 | 0 | [5 empty] | Hot bank boiler
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 13 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-13 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0
8:30 | 30 | 5 | natural gas | low |  |  | Monitor run up
9:00 | 60 | 5 | natural gas | low |  |  | Monitor run up
9:30 | 60 | 5 | natural gas | low |  |  | Monitor run up
10:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
10:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
11:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
11:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
12:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
12:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
13:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
13:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
14:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
14:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
15:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
15:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
16:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
16:30 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
17:00 | 90 | 10 | natural gas & coal | low |  |  | Mill performance tests
17:30 | 120 | 10 | natural gas & coal | low |  |  | Mill performance tests
18:00 | 120 | 10 | natural gas & coal | low |  |  | Mill performance tests
18:30 | 120 | 10 | natural gas & coal | low |  |  | Mill performance tests
19:00 | 120 | 10 | natural gas & coal | low |  |  | Mill performance tests
19:30 | 120 | 10 | natural gas & coal | low |  |  | Mill performance tests
20:00 | 120 | 10 | natural gas | low |  |  | unit available for SM
20:30 | 100 | 10 | natural gas | low |  |  | unit available for SM
21:00 | 80 | 5 | natural gas | low |  |  | unit available for SM
21:30 | 60 | 5 | natural gas | low |  |  | unit available for SM
22:00 | 40 | 5 | natural gas | low |  |  | unit available for SM
22:30 | 0
23:00 | 0
23:30 | 0
24:00 | 0
24:30 | 0
25:00 | 0
25:30 | 0
26:00 | 0
26:30 | 0
27:00 | 0
27:30 | 0
28:00 | 0
28:30 | 0
29:00 | 0
29:30 | 0
30:00 | 0
30:30 | 0
31:00 | 0
31:30 | 0
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 14 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-14 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0
8:30 | 30 | 5 | natural gas | low |  |  | Monitor run up
9:00 | 60 | 5 | natural gas | low |  |  | Monitor run up
9:30 | 60 | 5 | natural gas | low |  |  | Monitor run up
10:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
10:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
11:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
11:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
12:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
12:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
13:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
13:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
14:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
14:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
15:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
15:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
16:00 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
16:30 | 90 | 10 | natural gas & coal | low |  |  | Commissing Stage C FO systems
17:00 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
20:00 | 120 | 10 | natural gas | low |  |  | unit available for SM
20:30 | 100 | 10 | natural gas | low |  |  | unit available for SM
21:00 | 80 | 5 | natural gas | low |  |  | unit available for SM
21:30 | 60 | 5 | natural gas | low |  |  | unit available for SM
22:00 | 40 | 5 | natural gas | low |  |  | unit available for SM
22:30 | 0
23:00 | 0
23:30 | 0
24:00 | 0
24:30 | 0
25:00 | 0
25:30 | 0
26:00 | 0
26:30 | 0
27:00 | 0
27:30 | 0
28:00 | 0
28:30 | 0
29:00 | 0
29:30 | 0
30:00 | 0
30:30 | 0
31:00 | 0
31:30 | 0
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 15 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-15 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0
8:30 | 30 | 5 | natural gas | low |  |  | Monitor run up
9:00 | 60 | 5 | natural gas | low |  |  | Monitor run up
9:30 | 60 | 5 | natural gas | low |  |  | Monitor run up
10:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
10:30 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
11:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
11:30 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
12:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
12:30 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
13:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
13:30 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
14:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
14:30 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
15:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
15:30 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
16:00 | 90 | 10 | natural gas & fuel oil | low |  |  | Fuel Oil firing tests
16:30 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:00 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
20:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
20:30 | 100 | 10 | natural gas & coal | low |  |  | unit available for SM
21:00 | 80 | 5 | natural gas & coal | low |  |  | unit available for SM
21:30 | 60 | 5 | natural gas | low |  |  | unit available for SM
22:00 | 40 | 5 | natural gas | low |  |  | unit available for SM
22:30 | 0
23:00 | 0
23:30 | 0
24:00 | 0
24:30 | 0
25:00 | 0
25:30 | 0
26:00 | 0
26:30 | 0
27:00 | 0
27:30 | 0
28:00 | 0
28:30 | 0
29:00 | 0
29:30 | 0
30:00 | 0
30:30 | 0
31:00 | 0
31:30 | 0
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 16 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-16 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0
8:30 | 30 | 5 | natural gas | low |  |  | Monitor run up
9:00 | 60 | 5 | natural gas | low |  |  | Monitor run up
9:30 | 60 | 5 | natural gas | low |  |  | Monitor run up
10:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
10:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
11:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
11:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
12:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
12:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
13:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
13:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
14:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
14:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
15:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
15:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
16:00 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
16:30 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:00 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
20:00 | 120 | 10 | natural gas | low |  |  | unit available for SM
20:30 | 100 | 10 | natural gas | low |  |  | unit available for SM
21:00 | 80 | 5 | natural gas | low |  |  | unit available for SM
21:30 | 60 | 5 | natural gas | low |  |  | unit available for SM
22:00 | 40 | 5 | natural gas | low |  |  | unit available for SM
22:30 | 0
23:00 | 0
23:30 | 0
24:00 | 0
24:30 | 0
25:00 | 0
25:30 | 0
26:00 | 0
26:30 | 0
27:00 | 0
27:30 | 0
28:00 | 0
28:30 | 0
29:00 | 0
29:30 | 0
30:00 | 0
30:30 | 0
31:00 | 0
31:30 | 0
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13

## 17 Sep
COMMISSIONING TEST DAILY SCHEDULE | [7 empty] | COMMISSIONING TEST DAILY PROFILES
(Make copy of sheet as required.)
DATE | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
2013-09-17 | Active Power (MW) | Reactive Power (MVAr) | 'natural gas' 'coal' 'fuel oil' or combination. | low medium or high | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
8:00 | 0
8:30 | 30 | 5 | natural gas | low |  |  | Monitor run up
9:00 | 60 | 5 | natural gas | low |  |  | Monitor run up
9:30 | 60 | 5 | natural gas | low |  |  | Monitor run up
10:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
10:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
11:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
11:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
12:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
12:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
13:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
13:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
14:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
14:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
15:00 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
15:30 | 90 | 10 | natural gas & coal & fuel oil | low |  |  | Mixed fuel furing tests
16:00 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
16:30 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:00 | 90 | 10 | natural gas & coal | low |  |  | unit available for SM
17:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
18:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:00 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
19:30 | 120 | 10 | natural gas & coal | low |  |  | unit available for SM
20:00 | 120 | 10 | natural gas | low |  |  | unit available for SM
20:30 | 100 | 10 | natural gas | low |  |  | unit available for SM
21:00 | 80 | 5 | natural gas | low |  |  | unit available for SM
21:30 | 60 | 5 | natural gas | low |  |  | unit available for SM
22:00 | 40 | 5 | natural gas | low |  |  | unit available for SM
22:30 | 0
23:00 | 0
23:30 | 0
24:00 | 0
24:30 | 0
25:00 | 0
25:30 | 0
26:00 | 0
26:30 | 0
27:00 | 0
27:30 | 0
28:00 | 0
28:30 | 0
29:00 | 0
29:30 | 0
30:00 | 0
30:30 | 0
31:00 | 0
31:30 | 0
Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
2013-08-28 | 2013-09-18 |  | natural gas | low | C1 | S1
|  |  | coal | medium | C2A | S2
|  |  | fuel oil | high | C2B | S3
|  |  | natural gas & coal |  | C3A | S4
|  |  | natural gas & fuel oil |  | C3B | S5
|  |  | coal & fuel oil |  | C4 | S6
|  |  | natural gas & coal & fuel oil |  | C5 | S7
[5 empty] | C6 | S8
[5 empty] | C7 | S9
[5 empty] | C8 | S10
[5 empty] | C9 | S11
S12
S13