## New South Wales Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer at http://www.aemo.com.au/Electricity/Planning/Related-Information/Generation-Information
New South Wales Summary
Changes since last update
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to close on 31 July 2017.
New Development: Gidginbung Solar Farm, White Rock Solar Farm, Manildra Solar Farm, Capital Solar Farm, Parkes Solar Farm, Griffith Solar Farm, Dubbo Solar Hub, Griffith Solar Farm are added.
Generation Withdrawals
Withdrawn
None to report.
Announced Withdrawals (i.e. Mothballed, Seasonal Shut down etc.)
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to close on 31 July 2017.
Liddell Power Station: AGL Energy Limited advises that Liddell C Power Station (2000 MW) is to shut down in 2022.
Committed projects
Coal, CCGT, OCGT, Gas other, Wind, Water, Biomass, Geo-thermal, Other : None to report.
Solar: Moree Solar Farm advises that Moree Solar Farm (56 MW) full commercial operation is planned for the end of March 2016.
Proposed Projects
Please refer to information presented in the worksheet titled 'New Developments'.
Plant Limitations
AEMO has not been advised of any plant limitations for this region.
New South Wales existing and potential new developments by generation type (MW)

## Change Log
New South Wales Change Log
Lists all updates to new development projects and existing generation information since the 2012 ESOO published 9 August 2012.
Publication Date: | 2012-12-20
Eraring Power Station: Eraring Energy advises that the upgrade of unit 4 was completed in November 2012.
Publication Date: | 2013-02-22
Wallerawang Power Station: Energy Australia advises that the Wallerawang plant has revised its available capacity from 1,000 MW to 500 MW (-500 MW) for summer 2013–14 and winter 2013, due to the unit with DUID (dispatchable unit ID) WW7 being unavailable and only being brought back into service under extreme weather conditions.
Colongra Power Station: Delta Electricity advises that the Colongra plant available capacity has been revised from 668 MW to 724 MW (+56 MW) in summer, based on operating with distillate fuel.
Publication Date: | 2013-06-30
Wallerawang Power Station: Energy Australia advises that the Wallerawang plant available capacity has been revised from 500 MW to 1,000 MW (+500 MW) in summer 2013–14, where both units are available dependant on demand.
Liddell Power Station: Energy Australia advises that the Liddell plant available capacity has been revised from 2,060 MW to 2,020 MW (-40 MW) in summer and winter due to a reassessment of plant capacity.
Tallawarra Power Station: Energy Australia advises that the Tallawarra plant's available capacity has been revised from 435 MW to 440 MW (+5 MW) in winter.
Gullen Range Wind Farm: Gullen Range Wind Farm Pty Ltd advises that this is a committed project. Construction at the site has commenced and commissioning is planned for July 2014.
Capital East Solar Farm P1: Infigen's Capital East Solar Farm demonstration facility is a committed project. Construction at site has commenced.
Publication Date: | 2013-08-13
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that this is a committed project. Construction of the first phase of 113 MW at the site has commenced and commissioning is planned for December 2014.
Taralga Wind Farm: CBD Energy/Banco Santander advises that this 106.7 MW Wind Farm is a committed project. Construction at the site has commenced and commissioning is planned for October 2014.
Publication Date: | 2013-11-15
Capital East Solar Farm P1: Infigen's Capital East Solar Farm (0.13 MW) demonstration facility project is was completed in June 2013.
Broken Hill: AGL Energy Limited advises that both the Broken Hill (53 MW) large-scale solar photovoltaic (PV) project is set to proceed after achieving financial close. Construction of the Broken Hill project is expected to commence in July 2014, and is scheduled to be completed around November 2015
Nyngan: AGL Energy Limited advises that both the Nyngan (102 MW) large-scale solar photovoltaic (PV) projects is set to proceed after achieving financial close. Construction of the Nyngan project is expected to commence in February 2014, with completion scheduled by mid 2015.
Royalla Solar Farm: Royalla Asset Pty Ltd ATF Royalla Asset Trust advises that Royalla Solar Farm (20 MW) in ACT is now classified as a committed project, and construction at the site has commenced, with full commissioning planned for August 2014.
Onesun Capital Solar Farm: Elementus Energy Pty Ltd advises that Onesun Capital Solar Farm (7 MW) in ACT expects construction to commence in June 2014, with full commissioning planned for April 2015.
Mugga Lane Solar Facility: Zhenfa Canberra Solar Farm One Pty Ltd advises that Mugga Lane Solar Facility (13 MW) in ACT expects construction to commence in June 2014, with full commissioning planned for Q4 2014.
Publication Date: | 2014-02-28
Nyngan Solar Plant: AGL Engergy Limited advises the Nyngan Solar Plant (102 MW solar) is now classified as a committed project. Construction has commenced, and full commissioning is planned for July 2015.
Jupiter Wind Farm Project: EPYC Pty Ltd has announced the Jupiter Wind Farm Project (up to 100 wind turbines). If approved, construction and commissioning of the wind farm near Tarago would be completed by the end of 2016. The capacity of the project is yet to be advised.
Wallerawang C: EnergyAustralia advises that Wallerawang C unit 7 (500 MW black coal) has been removed from service in January 2014. Unit 8 (500 MW) will remain available until the end of March 2014, and will then be placed on a three-month recall should market conditions change.
Publication Date: | 2014-05-30
Bayswater Power Station: Macquarie Generation advises that the Bayswater Power Station available capacity has been revised from 2,720 MW to 2,700 MW (-20 MW) in summer and winter due to a reassessment of plant capacity.
Guthega Power Station: Snowy Hydro Ltd advises that Guthega's available capacity has been revised from 68 MW to 34 MW (-34 MW) for summer 2022–23, due to major refurbishment of unit 1; and 68 MW to 34 MW (-34 MW) for summer 2023–24, due to major refurbishment of unit 2.
Broken Hill Solar Plant: AGL PV Solar Development Pty Limited advises that Broken Hill Solar Plant (53 MW) is a committed project. Construction of the 53 MW at the site is to commence in July 2014 and commissioning is planned for August 2015.
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that Boco Rock Wind Farm (113 MW) is a committed project. Construction of the first phase at the site has commenced and commissioning is planned for March 2015.
Publication Date: | 2014-08-07
Moree Solar Farm: Moree Solar Farm advises that Moree Soalr Farm (56 MW) is a committed project. Construction is to commence in July 2014 and commissioning is planned for February 2016.
OneSun Capital: Elementus Energy Pty Ltd advises that OneSun Capital (10 MW) construction is to commence in October 2014 and commissioning is planned for April 2015.
Publication Date: | 2014-12-10
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that Boco Rock Wind Farm (113 MW) is a committed project. Construction of the first phase at the site has commenced and commissioning is planned for January 2015.
Taralga Wind Farm: CBD Energy/Banco Santander advises that Taralga Wind Farm (106.7 MW) is a committed project. Construction at the site has commenced and commissioning is planned for May 2015.
Royalla Solar Farm: Royalla Asset Pty Ltd ATF Royalla Asset Trust advises that Royalla Solar Farm (20 MW) is a committed project. Construction has commenced, and full commissioning is planned for February 2015.
Moree Solar Farm: Moree Solar Farm advises that Moree Soalr Farm (56 MW) is a committed project. Construction commenced in November 2014 and commissioning is planned for February 2016.
Wallerawang C Power Station: EnergyAustralia advises that Wallerawang C Power Station (1000 MW black coal) has been removed from service in January 2014 (Unit 8 500 MW) and March 2014 (Unit 7 500 MW), and will permanently closed and decommissioned.
Redbank Power Station: Redbank Energy Ltd advises that Redbank Power Station (143.8 MW black coal) has been removed from service from August 2014 and shut down. There are no future plans at this stage for Redbank to return to service.
Gullen Range Wind Farm: Gullen Range Wind Farm Pty Ltd advises that Gullen Range Wind Farm (165.5 MW) project has been completed and in full commercial operation since November 2014.
Wilga Park Power Station B: Santos advises the Wilga Park Power Station B (6 MW) project has been completed and in full commercial operation since Sepetember 2014.
Publication Date: | 2015-04-15
Taralga Wind Farm: CBD Energy/Banco Santander advises that Taralga Wind Farm (106.7 MW) is under construction and full commercial operation is planned for May 2015.
Moree Solar Farm: Moree Solar Farm advises that Moree Solar Farm (56 MW) is under construction since November 2014 and full commercial operation is planned for the end of March 2016.
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that Boco Rock Wind Farm (113 MW) has been completed and in full commercial operation since March 2015.
Royalla Solar Farm: Royalla Asset Pty Ltd ATF Royalla Asset Trust advises that Royalla Solar Farm (20 MW) has been completed and in full commercial operation since February 2015.
Wilga Park Power Station B: Santos advises the Wilga Park Power Station B (6 MW) project has been completed and in full commercial operation since January 2015.
Gullen Range Solar Project: Goldwind Australia Pty Ltd advises has announced plans to add a solar plant at the Gullen Range wind farm site.
Publication Date: | 2015-08-13
Taralga Wind Farm: CBD Energy/Banco Santander advises that Taralga Wind Farm (106.7 MW) has been completed and in full commercial operation since May 2015.
Nyngan Solar Plant: AGL Engergy Limited advises the Nyngan Solar Plant (102 MW) has been completed and in full commercial operation since July 2015.
Wallerawang C Power Station: EnergyAustralia advises that Wallerawang C Power Station (1000 MW black coal) has permanently closed in November 2014.
Liddell Power Station: AGL Energy Limited advises that Liddell C Power Station (2000 MW) is to shut down in 2022.
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to retire in 2017.
Redbank Power Station: Redbank Energy Ltd advises that Redbank Power Station (143.8 MW black coal) has been removed from service from August 2014 and shut down. There are no future plans at this stage for Redbank to return to service.
Publication Date: | 2015-10-23
Broken Hill Solar Plant: AGL PV Solar Development Pty Limited advises that Broken Hill Solar Plant (53 MW) has been in full commercial operation since October 2015.
Publication Date: | 2016-03-03
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to close on 31 July 2017
Moree Solar Farm: Moree Solar Farm advises that Moree Solar Farm (56 MW) full commercial operation is planned for the end of March 2016.
New Development: Gidginbung Solar Farm, White Rock Solar Farm, Manildra Solar Farm, Capital Solar Farm, Parkes Solar Farm, Griffith Solar Farm, Dubbo Solar Hub, Griffith Solar Farm
Publication Date: | 2016-04-15
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to close on 31 July 2017
Moree Solar Farm: Moree Solar Farm advises that Moree Solar Farm (56 MW) full commercial operation is planned for the end of March 2016.
New Development: Gidginbung Solar Farm, White Rock Solar Farm, Manildra Solar Farm, Capital Solar Farm, Parkes Solar Farm, Griffith Solar Farm, Dubbo Solar Hub, Griffith Solar Farm

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Technology Type | Fuel Type | Dispatch Type | Service Status
Capacity (MW)
Bayswater | AGL Energy Limited | 4 x 660 | 2640 | Steam Sub Critical | Black Coal | S | In service
Blowering | Snowy Hydro Ltd | 1 x 80 | 80 | Hydro - Gravity | Water | S | In service
Boco Rock Wind Farm | Boco Rock Wind Farm Pty Ltd | 67 x 1.8 | 113 | Wind - Onshore | Wind | SS | In service
Broken Hill Solar Plant | AGL PV Solar Development Pty Limited | 40 X 1.325 | 53 | PV panels | Solar | SS | In service
Colongra | Snowy Hydro Ltd | 4 x 181 | 724 | OCGT | Natural Gas Pipeline | S | In service
Eraring | Origin Energy Eraring Pty Ltd | 4 x 720 | 2880 | Steam Sub Critical | Black Coal | S | In service
Gullen Range | Gullen Range Wind Farm Pty Ltd | 56 x 2.5 17 x 1.5 | 165.5 | Wind - Onshore | Wind | SS | In service
Gunning | Gunning Wind Energy Developments | 31 x 1.5 | 46.5 | Wind - Onshore | Wind | SS | In service
Guthega | Snowy Hydro Ltd | 2 x 30 | 60 | Hydro - Gravity | Water | S | In service
Hume NSW | Green State Power Pty Ltd | 1 x 29 | 29 | Hydro - Gravity | Water | S | In service
Hunter Valley GT | AGL Energy Limited | 2 x 25 | 50 | OCGT | Fuel Oil | S | In service
Liddell | AGL Energy Limited | 4 x 500 | 2000 | Steam Sub Critical | Black Coal | S | Announced Withdrawal
Mt Piper | EnergyAustralia | 2 x 700 | 1400 | Steam Sub Critical | Black Coal | S | In service
Nyngan | AGL Energy Limited | 81 x 1.26 | 102 | PV panels | Solar | SS | In service
Redbank | Redbank Energy Ltd | 1 x 143.8 | 0 | Steam Sub Critical | Black Coal | S | Withdrawn
Shoalhaven | Origin Energy Eraring Pty Ltd | 2 x 80 2 x 40 | 240 | Pump Storage | Water | S | In service
Smithfield Energy Facility | Smithfield Power Partnership | 1 x 62 3 x 36.3 | 170.9 | CCGT | Natural Gas Pipeline | S | Announced Withdrawal
Tallawarra | EnergyAustralia | 1 x 420 | 420 | CCGT | Natural Gas Pipeline | S | In service
Taralga | CBD Energy/Banco Santander | 21 x 2 21 x 1.8 9 x 3 | 106.7 | Wind - Onshore | Wind | SS | In service
Tumut 3 | Snowy Hydro Ltd | 6 x 250 | 1500 | Hydro - Gravity | Water | S | In service
Upper Tumut | Snowy Hydro Ltd | 4 x 82 4 x 72 | 616 | Hydro - Gravity | Water | S | In service
Uranquinty | Origin Energy Uranquinty Power Pty Ltd | 4 x 166 | 664 | OCGT | Natural Gas Pipeline | S | In service
Vales Point B | Sunset Power International Pty Ltd | 2 x 660 | 1320 | Steam Sub Critical | Black Coal | S | In service
Woodlawn Wind Farm | Woodlawn Wind Pty Ltd | 23 x 2.1 | 48.3 | Wind - Onshore | Wind | SS | In service
Committed Project
Moree Solar Farm | Moree Solar Farm | 1 x 56 | 56 | PV panels | Solar | SS | Committed
Total |  |  | 15484.9

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – New South Wales (MW)
Power Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | -25 | S
Bayswater | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | S
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Boco Rock Wind Farm | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Colongra | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | S
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Gullen Range | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Guthega | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Hunter Valley GT | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | S
Liddell | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 0 | 0 | 0 | S
Mt Piper | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | S
Nyngan (Solar) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Redbank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Smithfield Energy Facility | 162 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tallawarra | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | S
Taralga | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | S
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Committed Project
Moree Solar Farm | 0 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | SS
Total | 15673 | 15687 | 15525 | 15525 | 15525 | 15525 | 15525 | 13505 | 13505 | 13505
The table above lists the latest summer capacities for New South Wales generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2014–15 these figures are 1.2% of the installed capacity during summer, and 3.4% during winter, based on the contribution factors published by AEMO in the 2015 NEM Historical Market Information Report.
Due to the intermittent nature of sunlight, solar generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from solar generators during peak periods. For 2014–15 this figures is 25% of the installed capacity during summer and winter, based on the new generation contribution factors published by AEMO in the 2013 Planning Assumptions.
The two tables below have been included to better represent supply availability in New South Wales, by taking into account the firm contribution by wind. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled wind generation for the summer period. The total refers to the maximum amount that the wind farms can generate at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation – New South Wales (MW)
Power Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | -25 | S
Bayswater | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | S
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Colongra | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | S
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Guthega | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Hunter Valley GT | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | S
Liddell | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 0 | 0 | 0 | S
Mt Piper | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | 1360 | S
Redbank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Smithfield Energy Facility | 162 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tallawarra | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | S
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
Firm Wind Capacity | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | SS
Firm Solar Capacity | 38.75 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | SS
Total | 15141.79 | 15145.29 | 14983.29 | 14983.29 | 14983.29 | 14983.29 | 14983.29 | 12963.29 | 12963.29 | 12963.29
Summer aggregate available semi-scheduled generation
Power Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | -25 | S
Boco Rock Wind Farm | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Gullen Range | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Nyngan (Solar) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Taralga | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | SS
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Total (Wind) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
Committed Project
Moree Solar Farm | 0 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | SS
Total (Solar) | 155 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation – New South Wales (MW)
Project Station | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Dispatch Type
Bayswater | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | S
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Boco Rock Wind Farm | 0 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Colongra | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | S
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Gullen Range | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Guthega | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hunter Valley GT | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Liddell | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 0 | 0 | 0 | 0 | S
Mt Piper | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Nyngan (Solar) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Redbank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Smithfield Energy Facility | 178 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tallawarra | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | S
Taralga | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | S
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 533.6 | 533.6 | 533.6 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Committed Projects
Moree Solar Farm | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | SS
Total | 15633.6 | 15686.6 | 15508.6 | 15591 | 15591 | 15591 | 13571 | 13571 | 13571 | 13571
The table above lists the latest winter capacities for New South Wales generation.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2014–15 these figures are 1.2% of the installed capacity during summer, and 3.4% during winter, based on the contribution factors published by AEMO in the 2015 NEM Historical Market Information Report.
Due to the intermittent nature of sunlight, solar generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from solar generators during peak periods. For 2014–15 this figures is 25% of the installed capacity during summer and winter, based on the new generation contribution factors published by AEMO in the 2013 Planning Assumptions.
The two tables below have been included to better represent supply availability in New South Wales, by taking into account the firm contribution by wind. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled wind generation for the winter period. The total refers to the maximum amount that the wind farms can generate at the winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation – New South Wales (MW)
Project Station | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Dispatch Type
Bayswater | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | 2700 | S
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Colongra | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | S
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Guthega | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hunter Valley GT | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Liddell | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 0 | 0 | 0 | 0 | S
Mt Piper | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Redbank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Smithfield Energy Facility | 178 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tallawarra | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | S
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 533.6 | 533.6 | 533.6 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
Firm Wind Capacity | 12.478 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | SS
Firm Solar Capacity | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | 42.25 | SS
Total | 15152.328 | 15154.13 | 14976.13 | 15058.53 | 15058.53 | 15058.53 | 13038.53 | 13038.53 | 13038.53 | 13038.53
Winter aggregate available semi-scheduled generation
Project Station | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Dispatch Type
Boco Rock Wind Farm | 0 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Gullen Range | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Nyngan (Solar) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Taralga | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | 106.7 | SS
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Total (Wind) | 367 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
Committed Project
Moree Solar Farm | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | SS
Total (Solar) | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169

## Existing NS Generation
Existing non-scheduled generation – New South Wales
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type | Service Status
101 Miller St | Cogent Energy | 2.4 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
133 Castleragh St | Cogent Energy | 0.8 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
20 Bond Street | Cogent Energy | 0.6 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
40 Mount St | Cogent Energy | 0.8 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Appin | EDL CSM NSW Pty Ltd | 55.62 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
Awaba | LMS Energy Pty Ltd | 1.123 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Bankstown Sports Club | Bankstown Sports Club | 2.14 | Compression Reciprocating Engine | Diesel | In service
Belconnen | EDL LFG ACT Pty Ltd | 1.03 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Belrose | EDL LFG NSW Pty Ltd | 1.03 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Blackmores | Cogent Energy | 0.8 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Blayney | Green State Power Pty Ltd | 9.9 | Wind - Onshore | Wind | In service
Broadwater | Cape Byron Power | 38 | Steam Sub Critical | Bagasse | In service
Broken Hill GT | Essential Energy | 50 | OCGT | Diesel | In service
Brown Mountain | Green State Power Pty Ltd | 5.2 | Hydro - Gravity/Run of River | Water | In service
Burrendong | AGL | 19 | Hydro - Gravity | Water | In service
Burrinjuck | Green State Power Pty Ltd | 27.2 | Hydro - Gravity | Water | In service
Capital East Solar Farm P1 | Infigen Energy | 0.13 | PV panels | Solar | In service
Capital Wind Farm | Renewable Power Ventures Pty Ltd | 140.7 | Wind - Onshore | Wind | In service
Charlestown Square Cogeneration | GPT RE Limited | 2.808 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Condong | Cape Byron Power | 30 | Steam Sub Critical | Bagasse | In service
Copeton | AGL | 20 | Hydro - Gravity | Water | In service
Crookwell | Green State Power Pty Ltd | 4.8 | Wind - Onshore | Wind | In service
Cullerin Range Wind Farm | Cullerin Range Wind Farm Pty Ltd | 30 | Wind - Onshore | Wind | In service
EarthPower Biomass Plant | EarthPower Technologies Sydney Pty Ltd | 3.9 | Spark Ignition Reciprocating Engine | Biomass recycled municipal and industrial material | In service
Eastern Creek | EDL LFG NSW Pty Ltd | 5.06 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Eastern Creek 2 Gas Utilisation Facility | LMS Energy Pty Ltd | 7.861 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Eraring GT | Origin Energy Eraring Pty Ltd | 42 | OCGT | Diesel | In service
Erskine Park | Cogent Energy | 0.4 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Glenbawn | AGL | 5 | Hydro - Gravity | Water | In service
Glennies Creek | Envirogen Oaky Pty Ltd | 11 | Compression Reciprocating Engine | Waste Coal Mine Gas | In service
Grange Avenue | EDL LFG NSW Pty Ltd | 1.26 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Hunter Economic Zone | Infratil Energy Australia Pty Ltd | 29 | Compression Reciprocating Engine | Diesel | In service
Jacks Gully | EDL LFG NSW Pty Ltd | 2.3 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Jindabyne | Snowy Hydro Ltd | 1.1 | Hydro - Gravity | Water | In service
Jounama | Snowy Hydro Ltd | 14.4 | Hydro - Gravity | Water | In service
Keepit | Green State Power Pty Ltd | 7.2 | Hydro - Gravity | Water | In service
Kooragang | Ausgrid | 0.6 | Wind - Onshore | Wind | In service
Lucas Heights I | EDL LFG NSW Pty Ltd | 5.39 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Lucas Heights II Stage 2 | EDL LFG NSW Pty Ltd | 17.25 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Mugga Lane | EDL LFG ACT Pty Ltd | 3.45 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Nine Network Willoughby | Nine Network | 3.2 | Compression Reciprocating Engine | Diesel | In service
Nymboida | Essential Energy | 33.6 | Hydro - Gravity | Water | In service
Oaky | Essential Energy | 4.8 | Hydro - Gravity | Water | In service
Pindari | AGL | 5.7 | Hydro - Gravity | Water | In service
Royalla Solar Farm | Royalla Asset Pty Ltd ATF Royalla Asset Trust | 20 | PV panels | Solar | In service
St George Leagues Club | St George Leagues Club | 1.48 | Compression Reciprocating Engine | Diesel | In service
Stotts Creek | LMS ENERGY Pty Ltd | 0.3 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Summer Hill | LMS Energy Pty Ltd | 2.246 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Tahmoor | Envirogen Pty Lld | 7.26 | CCGT | Coal Seam Methane | In service
Teralba | Envirogen Pty Ltd | 3.11 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
The Drop | Pacific Hydro Investments Pty Ltd | 2.5 | Hydro - Gravity | Water | In service
Tower | EDL CSM NSW Pty Ltd | 41.2 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
UNSW | Cogent Energy | 0.8 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Warragamba HEPS | Sydney Catchment Authority | 50 | Hydro - Gravity | Water | In service
West Illawarra Leagues Club | Wests Illawarra Leagues Club | 0.99 | Compression Reciprocating Engine | Diesel | In service
West Nowra Landfill Gas Power Generation Facility | AGL | 1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Western Suburbs League Club Campbelltown | Western Suburbs League Club Campbelltown | 1.32 | Compression Reciprocating Engine | Diesel | In service
Wilga Park Power Station A | Santos | 10 | Spark Ignition Reciprocating Engine | Natural Gas - Unprocessed | In service
Wilga Park Power Station B | Santos | 6 | Spark Ignition Reciprocating Engine | Natural Gas - Unprocessed | In service
Woodlawn Bioreactor Energy Generation | Veolia Environmental Services Aust P/L | 5.325 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Wyangala A | Hydro Power Pty Ltd | 20 | Hydro - Gravity | Water | In service
Wyangala B | AGL | 4 | Hydro - Gravity | Water | In service
Wyong | LMS ENERGY Pty Ltd | 2.246 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Total |  | 828.329

## New Developments
Projects under development – New South Wales
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Full Commercial Use Date
Bango Wind Farm | Bango Wind Farm Pty Ltd | up to 90 | Wind | Wind - Onshore | [5 empty] | Pub An | 140 | SS | TBA
Bayswater B | AGL Energy | All Units | Black Coal | Steam Super Critical | [5 empty] | Pub An | 2000 | S | TBA
Ben Lomond | AGL Energy | 1-67 | Wind | Wind - Onshore | [5 empty] | Pub An | 200 | SS | TBA
Bodangora Wind Farm | Infigen Energy | Units 1-33 | Wind | Wind - Onshore | [5 empty] | Pub An | 100 | SS | TBA
Box Hill | AGL Energy | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 25 | NS | TBA
Capital 2 Wind Farm | Infigen Energy | Units 1-33 | Wind | Wind - Onshore | [5 empty] | Pub An | 100 | SS | TBA
Chipping Norton Waste to Energy | Benedict Industries PL | 1 | Biomass recycled municipal and industrial material | Steam Sub Critical | [5 empty] | Pub An | 8 | NS | 2017-05-01
Collector | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 175 | SS | 2017-09-01
Conroys Gap | Conroys Gap Wind Farm Pty Ltd | 1-15 | Wind | Wind - Onshore | [5 empty] | Pub An | 30 | SS | TBA
Crookwell 2 Wind Farm | Crookwell Development Pty Ltd | 46 | Wind | Wind - Onshore | ü |  | ü |  |  | Pub An | 92 | SS | TBA
Crookwell 3 Wind Farm | Crookwell Development Pty Ltd | Units 1-28 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 56 | SS | TBA
Crudine Ridge Wind Farm | Crudine Ridge Wind Farm Pty Ltd | 1-77 | Wind | Wind - Onshore | [5 empty] | Pub An | 135 | SS | TBA
Dalton | AGL | 1-2 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 500 | S | TBA
Flyers Creek Wind Farm | Infigen Energy | Units 1-42 | Wind | Wind - Onshore | [5 empty] | Pub An | 126 | SS | TBA
Glen Innes Wind Farm | Glen Innes WindPower Pty Ltd | Units 1-25 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 100 | SS | TBA
Gloucester Gas Project | AGL Energy | All Units | Coal Seam Methane | CCGT | [5 empty] | Pub An | 15 | SS | TBA
Jupiter Wind Farm | EPYC Pty Ltd | 1-100 | Wind | Wind - Onshore | [5 empty] | Pub An | tba | SS | TBA
Kyoto Energy Park | Pamada Pty Ltd | Units 1-24 | Wind | Wind - Onshore | [5 empty] | Pub An | 60 | SS | TBA
Liverpool Range Wind Farm | EPURON Pty Ltd | Units 1-288 | Wind | Wind - Onshore | [5 empty] | Pub An | 864 | SS | TBA
Manildra Photovoltaic Solar Farm | Infigen Energy | Inverters 1-66 | Solar | PV panels | [5 empty] | Pub An | 50 | SS | TBA
Mugga Lane Solar Park | Zhenfa Canberra Solar Farm One Pty Ltd | Mugga Lane Solar Park | Solar | PV panels | ü | ü | ü | ü | ü | Adv | 13 | NS | TBA
OneSun Capital | Elementus Energy Pty Ltd | TBA | Solar | PV panels | ü |  |  |  |  | Pub An | 10 | NS | TBA
Moree Solar Farm | Moree Solar Farm | 56 | Solar | PV panels | ü | ü | ü | ü | ü | Com | 56 | SS | TBA
Paling Yards Wind Farm | Union Fenosa Wind Australia Pty Ltd | Units 1-55 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 178 | SS | TBA
Rugby Wind Farm | Wind Lab Developments | 1-52 | Wind | Wind - Onshore | [5 empty] | Pub An | 166.4 | SS | TBA
Rye Park Wind Farm | Trustpower | 1- 126 | Wind | Wind - Onshore | [5 empty] | Pub An | 350 | SS | 2018-11-01
Sapphire Wind Farm | Sapphire Wind Farm Pty Ltd | 125-159 | Wind | Wind - Onshore | [5 empty] | Pub An | 319 | SS | TBA
Silverton Wind Farm | Silverton Wind Farm Developments Pty Ltd | 1-105 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 250 | SS | TBA
Tomago GT | AGL Energy | station | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | TBA | S | TBA
Uungula Wind Farm | Uungula Wind Farm Pty Ltd | 1-249 | Wind | Wind - Onshore | [5 empty] | Pub An | 622.5 | SS | TBA
Wellington | ERM Power Limited | 1-2 | Coal Seam Methane | OCGT | [5 empty] | Pub An | 550 | S | TBA
White Rock Wind Farm | White Rock Wind Farm Pty Ltd | 1-119 | Wind | Wind - Onshore | [5 empty] | Pub An | 297.5 | SS | TBA
Yass Valley Wind Farm | Yass Valley Wind Farm Pty Ltd | 1-124 | Wind | Wind - Onshore | [5 empty] | Pub An | 310 | SS | TBA
Gidginbung Solar Farm | EPHO Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 12.2 | TBA | TBA | x
White Rock Solar Farm | Goldwind Australia Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 20 | TBA | TBA | x
Manildra Solar Farm | Infigen Energy | TBA | Solar | Solar | [5 empty] | Pub An | 42.4 | TBA | TBA | x
Capital Solar Farm | Infigen Energy | TBA | Solar | Solar | [5 empty] | Pub An | 39 | TBA | TBA
Parkes Solar Farm | Neoen Australia Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 46 | TBA | TBA | x
Griffith Solar Farm | Neoen Australia Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 26.4 | TBA | TBA | x
Dubbo Solar Hub | Neoen Australia Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 22.4 | TBA | TBA | x
Griffith Solar Farm | SF Suntech Australia Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 33.9 | TBA | TBA | x

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as semi-scheduled or non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as scheduled or non-scheduled. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW, unless AEMO approves its classification as semi-scheduled or semi-scheduled.
Generating systems greater than 30 MW must be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating of less than 5 MW may be be exempted by AEMO if its generation is purchased entirely by the local retail or a customer at the generator's connection point or the generator is classified as a market generating unit by a market small generation aggregator. A generating unit with a nameplate rating is between 5 MW and 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.