## South Australia Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer on the 'Disclaimer' tab of this workbook.
South Australia Summary
Committed project developments
Snowtown S2: TrustPower advises that the status of the Snowtown 2 project is now Committed. Snowtown Stage 2 project will consist of two separately
metered wind farms, Snowtown 2 North (144 MW) and Snowtown 2 South (126 MW), sharing a single transmission line owned by TrustPower.
Plant retirements
AEMO has not been advised of any plant retirements in South Australia within the 10-year planning outlook.
Changes since the 2012 ESOO (existing generation)
Playford B Power Station: Alinta energy advises that Playford B power station will be available with a recall time of around 90 days. Alinta Energy have also revised the output from last year's in summer and winter from 200 MW to 180 MW (-20 MW) due to Turbine 2 being out of service. However should AEMO require it, Turbine 2 can be brought back into service, taking the longer-term availability of Playford B Power Station up to 200 MW.
Hallett 4 North Brown Hill: AGL advises that Hallett 4 North Brown Hill's available capacity has been revised from 81.9 MW to 99.2 MW (+17.3 MW) in summer, due to de-rating applied to all Suzlon S88/S97 machines.
Hallett Stage 1 Brown Hill: AGL advises that Hallett Stage 1 Brown Hill's available capacity has been revised from 58.5 MW to 70.9 MW (+12.4 MW) in summer, due to de-rating applied to all Suzlon S88/S97 machines.
Plant limitations
Torrens Island B Power Station: AGL advises that Torrens Island B's available capacity in summer may be affected by tides and temperature of the Port River, from which water is used to cool the plant.
Dry storage
Northern Power Station: Alinta Energy advises that Northern will only be available if recalled (with a recall time of up to three weeks) from 1 April 2013 to 30 September 2013 and from 1 April 2014 to 30 September 2014. After 1 October 2014, the power station will return to normal service. Alinta Energy also advises that summer operation will continue as normal.

## Change Log
South Australia Change Log
Lists all updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Snowtown S2: TrustPower advises that the Snowtown 2 project is now in a Committed status. Snowtown Stage 2 project will consist of two separately
metered wind farms, Snowtown 2 North (144 MW) and Snowtown 2 South (126 MW), sharing a single transmission line owned by TrustPower.
Publication Date: | 2013-06-30
Playford B Power Station: Alinta energy advises that Playford B power station will be available with a recall time of around 90 days.
Alinta Energy have also revised the output from last year's in summer and winter from 200 MW to 180 MW (-20 MW) due to Turbine 2 being out of service.
However should AEMO require it, Turbine 2 can be brought back into service, taking the longer-term availability of Playford B Power Station up to 200 MW.
Hallett 4 North Brown Hill: AGL advises that Hallett 4 North Brown Hill's available capacity has been revised from 81.9 MW to 99.2 MW (+17.3 MW) in summer,
due to de-rating applied to all Suzlon S88/S97 machines.
Hallett Stage 1 Brown Hill: AGL advises that Hallett Stage 1 Brown Hill's available capacity has been revised from 58.5 MW to 70.9 MW (+12.4 MW) in summer,
due to de-rating applied to all Suzlon S88/S97 machines.

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless classified as semi-scheduled, or AEMO is permitted to classify it as non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW and equal to or greater than 5 MW.
Generating systems greater than 30 MW may be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating less than 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Clements Gap | Pacific Hydro Clements Gap Pty Ltd | 27 x 2.1 | 56.7 | Wind - Onshore | Wind | SS
Dry Creek GT | Synergen Power Pty Ltd | 3 x 52 | 156 | OCGT | Natural Gas Pipeline | S
Hallett 4 North Brown Hill | Brown Hill North Pty Ltd | 63 x 2.1 | 132.3 | Wind - Onshore | Wind | SS
Hallett 5 The Bluff WF | Eurus Energy | 25 x 2.1 | 52.5 | Wind - Onshore | Wind | SS
Hallett GT | EnergyAustralia | 2 x 24.8 1 x 27.5 2 x 17.3 3 x 17 4 x 16.4 | 228.3 | OCGT | Natural Gas Pipeline | S
Hallett Stage 1 Brown Hill | Palisade Investment Partner Limited | 45 x 2.1 | 94.5 | Wind - Onshore | Wind | SS
Hallett Stage 2 Hallett Hill | Infrastructure Capital Group Limited | 34 x 2.1 | 71.4 | Wind - Onshore | Wind | SS
Ladbroke Grove | Origin Energy Power Limited | 2 x 40 | 80 | OCGT | Natural Gas Pipeline | S
Lake Bonney 2 Wind Farm | Lake Bonney Wind Power Pty Ltd | 53 x 3 | 159 | Wind - Onshore | Wind | SS
Lake Bonney 3 Wind Farm | Lake Bonney Wind Power Pty Ltd | 13 x 3 | 39 | Wind - Onshore | Wind | SS
Mintaro GT | Synergen Power Pty Ltd | 1 x 90 | 90 | OCGT | Natural Gas Pipeline | S
Northern | Flinders Operating Services Pty Ltd | 2 x 265 | 530 | Steam Sub Critical | Brown Coal | S
Osborne | Osborne Cogeneration Pty Ltd | 1 x 118 1 x 62 | 180 | CCGT | Natural Gas Pipeline | S
Pelican Point | Pelican Point Power Limited | 1 x 478 | 478 | CCGT | Natural Gas Pipeline | S
Playford B | Flinders Operating Services Pty Ltd | 4 x 60 | 240 | Steam Sub Critical | Brown Coal | S
Port Lincoln GT | Synergen Power Pty Ltd | 2 x 25 1 x 23.5 | 73.5 | OCGT | Diesel | S
Quarantine | Origin Energy Power Limited | 4 x 24 1 x 128 | 224 | OCGT | Natural Gas Pipeline | S
Snowtown | Snowtown Wind Farm Pty Ltd | 47 x 2.1 | 98.7 | Wind - Onshore | Wind | SS
Snuggery | Synergen Power Pty Ltd | 3 x 21 | 63 | OCGT | Diesel | S
Torrens Island A | AGL Energy | 4 x 120 | 480 | Steam Sub Critical | Natural Gas Pipeline | S
Torrens Island B | AGL Energy | 4 x 200 | 800 | Steam Sub Critical | Natural Gas Pipeline | S
Waterloo | Waterloo Windfarm Pty Ltd | 37 x 3 | 111 | Wind - Onshore | Wind | SS
Committed
Snowtown S2 North | Snowtown Wind Farm Pty Ltd | 48 x 3 | 144 | Wind - Onshore | Wind | SS
Snowtown S2 South | Snowtown Wind Farm Pty Ltd | 42 x 3 | 126 | Wind - Onshore | Wind | SS
Total |  |  | 4707.9

## Existing Wind Generation
Existing & committed wind generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Clements Gap | Pacific Hydro Clements Gap Pty Ltd | 27 x 2.1 | 56.7 | Wind - Onshore | Wind | SS
Hallett 4 North Brown Hill | Brown Hill North Pty Ltd | 63 x 2.1 | 132.3 | Wind - Onshore | Wind | SS
Hallett 5 The Bluff WF | Eurus Energy | 25 x 2.1 | 52.5 | Wind - Onshore | Wind | SS
Hallett Stage 1 Brown Hill | Palisade Investment Partner Limited | 45 x 2.1 | 94.5 | Wind - Onshore | Wind | SS
Hallett Stage 2 Hallett Hill | Infrastructure Capital Group Limited | 34 x 2.1 | 71.4 | Wind - Onshore | Wind | SS
Lake Bonney 2 Wind Farm | Lake Bonney Wind Power Pty Ltd | 53 x 3 | 159 | Wind - Onshore | Wind | SS
Lake Bonney 3 Wind Farm | Lake Bonney Wind Power Pty Ltd | 13 x 3 | 39 | Wind - Onshore | Wind | SS
Snowtown | Snowtown Wind Farm Pty Ltd | 47 x 2.1 | 98.7 | Wind - Onshore | Wind | SS
Waterloo | Waterloo Windfarm Pty Ltd | 37 x 3 | 111 | Wind - Onshore | Wind | SS
Canunda | Canunda Power Pty Ltd | 23 x 2 | 46 | Wind - Onshore | Wind | NS
Cathedral Rocks | JV Cathedral Rock Investments Pty Ltd and Acciona | 33 x 2 | 66 | Wind - Onshore | Wind | NS
Lake Bonney 1 Wind Farm | Lake Bonney Wind Power Pty Ltd | 46 x 1.75 | 80.5 | Wind - Onshore | Wind | NS
Mt Millar | Mount Millar Windfarm Pty Ltd | 35 x 2 | 70 | Wind - Onshore | Wind | NS
Starfish Hill | Ratch Australia | 23 x 1.5 | 34.5 | Wind - Onshore | Wind | NS
Wattle Point | Infrastructure Capital Group | 55 x 1.65 | 90.75 | Wind - Onshore | Wind | NS
Committed
Snowtown S2 North | Snowtown Wind Farm Pty Ltd | 48 x 3 | 144 | Wind - Onshore | Wind | SS
Snowtown S2 South | Snowtown Wind Farm Pty Ltd | 42 x 3 | 126 | Wind - Onshore | Wind | SS
Total |  |  | 1472.85

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – South Australia (MW)
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Dry Creek GT | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | S
Hallett 4 North Brown Hill | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | SS
Hallett 5 The Bluff WF | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | SS
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Hallett Stage 1 Brown Hill | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | SS
Hallett Stage 2 Hallett Hill | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | SS
Ladbroke Grove | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | S
Lake Bonney 2 Wind Farm | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | SS
Lake Bonney 3 Wind Farm | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | SS
Mintaro GT | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | S
Northern | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | S
Osborne | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | S
Pelican Point | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | S
Playford Ba | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | S
Port Lincoln GT | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | S
Quarantine | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | S
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snuggery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | S
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed
Snowtown S2 North | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Total | 4070.4 | 4340.4 | 4340.4 | 4340.4 | 4340.4 | 4340.4 | 4340.4 | 4340.4 | 4340.4 | 4340.4
a Alinta Energy advises that Playford B power plant will only be available with a recall time of around 90 days
The table above lists the latest summer capacities for South Australian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2012–13 these figures have been updated to 8.6% of the installed capacity during summer, and 7.9% during winter compared to the 2011–12 contribution factors.
The two tables below have been included to better represent supply availability in South Australia, by taking into account the firm contribution by wind. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Summer total available semi-scheduled capacity by power station table lists the total available capacity for semi-scheduled wind generation for the summer period. The total available refers to the maximum amount that the wind farms can generate at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation – South Australia (MW)
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Dry Creek GT | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | S
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Ladbroke Grove | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | S
Mintaro GT | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | S
Northern | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | S
Osborne | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | S
Pelican Point | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | S
Playford Ba | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | S
Port Lincoln GT | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | S
Quarantine | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | S
Snuggery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | S
Firm Wind Capacity | 70.0986 | 93.3186 | 93.3186 | 93.3186 | 93.3186 | 93.3186 | 93.3186 | 93.3186 | 93.3186 | 93.3186 | SS
Total | 3429.0986 | 3452.3186 | 3452.3186 | 3452.3186 | 3452.3186 | 3452.3186 | 3452.3186 | 3452.3186 | 3452.3186 | 3452.3186
a. Alinta Energy advises that Playford B power plant will only be available with a recall time of around 90 days
Summer aggregate available semi-scheduled generation
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Hallett 4 North Brown Hill | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | SS
Hallett 5 The Bluff WF | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | SS
Hallett Stage 1 Brown Hill | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | SS
Hallett Stage 2 Hallett Hill | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | SS
Lake Bonney 2 Wind Farm | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | SS
Lake Bonney 3 Wind Farm | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | SS
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed
Snowtown S2 North | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Total | 711.4 | 981.4 | 981.4 | 981.4 | 981.4 | 981.4 | 981.4 | 981.4 | 981.4 | 981.4

## Winter Scheduled Capacities
Winter aggregate scheduled and semi-scheduled generation – South Australia (MW)
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Dry Creek GT | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | S
Hallett 4 North Brown Hill | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | SS
Hallett 5 The Bluff WF | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | SS
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Hallett Stage 1 Brown Hill | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | SS
Hallett Stage 2 Hallett Hill | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | SS
Ladbroke Grove | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Mintaro GT | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | S
Northerna | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | S
Osborne | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | S
Pelican Point | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | S
Playford Bb | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | S
Port Lincoln GT | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | S
Quarantine | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | S
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snuggery | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | S
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed
Snowtown S2 North | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Total | 4488 | 4632 | 4632 | 4632 | 4632 | 4632 | 4632 | 4632 | 4632 | 4632
a. Alinta Energy advises that Northern power plant will only be available from 1 April 2013 to 30 September 2013 and 1 April 2014 to 30 September 2014 with a recall time of up to 3 weeks. After 1 October 2014 Northern power plant will be in service.
b. Alinta Energy advises that Playford B power plant will only be available with a recall time of around 90 days
The table above lists the latest winter capacities for South Australian generation.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2012-13 these figures have been updated to 8.6% of the installed capacity during summer, and 7.9% during winter compared to the 2011–12 contribution factors.
The two tables below have been included to better represent supply availability in South Australia, by taking into account the firm contribution by wind. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Winter total available semi-scheduled capacity by power station table lists the total available capacity for semi-scheduled wind generation for the summer period. The total available refers to the maximum amount that the wind farms can generate at the summer reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation – South Australia (MW)
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Dry Creek GT | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | S
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Ladbroke Grove | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Mintaro GT | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | S
Northerna | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | S
Osborne | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | S
Pelican Point | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | 474 | S
Playford Bb | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | S
Port Lincoln GT | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | S
Quarantine | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | S
Snuggery | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Torrens Island A | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | S
Torrens Island B | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | S
Firm Wind Capacity | 74.3469 | 85.7229 | 85.7229 | 85.7229 | 85.7229 | 85.7229 | 85.7229 | 85.7229 | 85.7229 | 85.7229 | SS
Total | 3621.3469 | 3632.7229 | 3632.7229 | 3632.7229 | 3632.7229 | 3632.7229 | 3632.7229 | 3632.7229 | 3632.7229 | 3632.7229
a. Alinta Energy advises that Northern power plant will only be available from 1 April 2013 to 30 September 2013 and 1 April 2014 to 30 September 2014 with a recall time of up to 3 weeks. After 1 October 2014 Northern power plant will be in service.
b. Alinta Energy advises that Playford B power plant will only be available with a recall time of around 90 days
Winter aggregate available semi-scheduled generation
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Hallett 4 North Brown Hill | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | 132.2 | SS
Hallett 5 The Bluff WF | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | SS
Hallett Stage 1 Brown Hill | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | SS
Hallett Stage 2 Hallett Hill | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | SS
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed
Snowtown S2 North | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Total | 941 | 1085 | 1085 | 1085 | 1085 | 1085 | 1085 | 1085 | 1085 | 1085

## New Developments
Projects under development – South Australia
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Commissioning Start Date
Arckaringa | Arckaringa Joint Venture | 1-2 | Black Coal | IGCC | [5 empty] | Pub An | 570 | S | 2019-12-31
Barn Hill | Barn HIll Wind Farm Pty Ltd | 1-62 | Wind | Wind - Onshore | [5 empty] | Pub An | 124-186 | SS | TBA
Carmodys Hill | Energy Pacific Vic Pty Ltd | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
Ceres Project | REpower | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 624 | SS | TBA
Cherokee Power Station | Tungkillo Powerco Pty Ltd | A | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 250 | S | 2016-10-01
Exmoor | Acciona Energy | 1-48 | Wind | Wind - Onshore | [5 empty] | Pub An | 144 | SS | TBA
Hallett Mt Bryan WF | AGL Energy Limited | 1-33 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 99 | SS | TBA
Hornsdale Wind Farm | Investec | A | Wind | Wind - Onshore | [5 empty] | Pub An | 270 | SS | 2015-11-01
Innamincka | Geodynamics Limited / Origin Energy Geothermal Pty | 1 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 10 | S | 2016-07-01
|  | 10 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2020-07-01
|  | 11 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2020-07-01
|  | 2 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2019-07-01
|  | 3 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2019-07-01
|  | 4 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2019-07-01
|  | 5 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2019-07-01
|  | 6 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2019-07-01
|  | 7 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2019-07-01
|  | 8 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2020-07-01
|  | 9 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 50 | S | 2020-07-01
Kangaroo Island Biomass Powerplant | Rural Aus Investment Limited | 1 | Dry Wood | Steam Sub Critical | [5 empty] | Pub An | 10 | S | TBA
Keyneton | Energy Pacific Vic Pty Ltd | 1-57 | Wind | Wind - Onshore | [5 empty] | Pub An | 105 | SS | TBA
Kongorong | Ratch Australia | 1-57 | Wind | Wind - Onshore | [5 empty] | Pub An | 100-240 | SS | 2018-06-01
Kulpara | Ratch Australia | 52 | Wind | Wind - Onshore | [5 empty] | Pub An | 60-150 | SS | 2020-03-01
Lincoln Gap Wind Farm | Lincoln Gap Wind Farm Pty Ltd | 1-59 | Wind | Wind - Onshore |  |  | ü |  |  | Pub An | 118 | SS | TBA
Mount Hill | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 80-180 | SS | TBA
Parachilna | Torrens Energy Limited | 1 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | - | SS | TBA
Paralana project | Petratherm Limited | Paralana 1 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 3.75 | NS | 2015-07-01
Paralana Stage 2 | Petratherm | 1 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 30 | S | TBA
Pelican Point S2 | Pelican Point Power Limited | 1-2 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 320 | S | TBA
Point Paterson | Acquasol Infrastructure Pty Ltd | CCGT Units | Natural Gas Pipeline | CCGT | [5 empty] | Pub An | 150 | S | 2017-02-28
Point Paterson | Acquasol Infrastructure Pty Ltd | Solar Units | Solar | Solar Thermal | [5 empty] | Pub An | 50 | S | 2016-05-26
Port Augusta Geothermal | Torrens Energy Limited | 1 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | - | SS | TBA
Robertstown | EnergyAustralia Renewables Pty Ltd | 1-25 | Wind | Wind - Onshore | [5 empty] | Pub An | 75 | SS | TBA
Snowtown S2 North | Snowtown Wind Farm Pty Ltd | 1-48 | Wind | Wind - Onshore | ü | ü | ü | ü | ü | Com | 144 | SS | 2014-11-30
Snowtown S2 South | Snowtown Wind Farm Pty Ltd | 1-42 | Wind | Wind - Onshore | ü | ü | ü | ü | ü | Com | 126 | SS | 2014-05-01
Stony Gap | EnergyAustralia Renewables Pty Ltd | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
Waterloo | Waterloo Windfarm Pty Ltd | 38-43 | Wind | Wind - Onshore | [5 empty] | Pub An | 18 | SS | TBA
Whyalla SolarOasis | SolarOasis Pty Ltd | All Units | Solar | Solar Thermal | ü |  |  |  |  | Pub An | 40 | SS | TBA
Willogoleche | Willogoleche Power Pty Ltd | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 72-108 | SS | TBA
Woakwine Wind Farm | Infigen Energy | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 400 | SS | TBA

## Existing NS Generation
Existing non-scheduled generation – South Australia
Power Station | Owner | Fuel Type | Technology Type | Nameplate Capacity (MW)
Amcor Gawler Glass Bottle Plant | Amcor Packaging Australia Pty Ltd | Diesel | Compression Reciprocating Engine | 4.02
Angaston | Infratil Energy Australia Pty Ltd | Diesel | Compression Reciprocating Engine | 50
Blue Lake Milling Power Plant | Vibe Energy Pty Ltd | Diesel | Compression Reciprocating Engine | 0.505
Canunda | Canunda Power Pty Ltd | Wind | Wind - Onshore | 46
Cathedral Rocks | JV Cathedral Rock Investments Pty Ltd and Acciona | Wind | Wind - Onshore | 66
Highbury | EDL LFG SA Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 1.03
Lake Bonney 1 Wind Farm | Lake Bonney Wind Power Pty Ltd | Wind | Wind - Onshore | 80.5
Lonsdale | Infratil Energy Australia Pty Ltd | Diesel | Compression Reciprocating Engine | 20.7
Mt Millar | Mount Millar Windfarm Pty Ltd | Wind | Wind - Onshore | 70
Pedler Creek | EDL LFG SA Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 3.09
Pt Stanvac A | Infratil Energy Australia Pty Ltd | Diesel | Compression Reciprocating Engine | 28.8
Pt Stanvac B | Infratil Energy Australia Pty Ltd | Diesel | Compression Reciprocating Engine | 28.8
Starfish Hill | Ratch Australia | Wind | Wind - Onshore | 34.5
Tatiara Meats | Vibe Energy Pty Ltd | Diesel | Compression Reciprocating Engine | 0.5
Tea Tree Gully | EDL LFG SA Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 1.03
Terminal Storage Mini Hydro | Lofty Ranges Power Pty Ltd | Water | Hydro - Gravity | 2.5
Wattle Point | Infrastructure Capital Group | Wind | Wind - Onshore | 90.75
Wingfield 1 | EDL LFG SA Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 4.1
Wingfield 2 | EDL LFG SA Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 4.1
Total |  |  |  | 536.925

## Disclaimer
Important Notice
Purpose
The purpose of this publication is to provide technical, market data and information regarding opportunities in the National Electricity Market.
AEMO publishes the Electricity Statement of Opportunities in accordance with clause 3.13.3(q) of the National Electricity Rules (Rules). This publication has been prepared by AEMO using information available at 31 July 2013, unless otherwise specified. Information made available after 31 July 2013 may have been included in this publication where practical.
Disclaimer
AEMO has made every effort to ensure the quality of the information in this publication but cannot guarantee that information, forecasts and assumptions are accurate, complete or appropriate for your circumstances. This publication does not include all of the information that an investor, participant or potential participant in the National Electricity Market might require, and does not amount to a recommendation of any investment.
Anyone proposing to use the information in this publication (including information and reports from third parties) should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this publication:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this publication; and
· are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this publication.
Acknowledgement
AEMO acknowledges the support, co-operation and contribution of all participants in providing data and information used in this publication.
Copyright
© 2013 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.