## Information
2021 System strength and inertia workbook
Version history
Version number | Release date | Description
v1.0 | 2021-05-07 | Initial release. Provides data for the 2021 Notice of Tasmania system strength and inertia shortfalls.
About
This spreadsheet is released by the Australian Energy Market Operator (AEMO). The initial release contains the charts and data from the 2021 Notice of Tasmania system strength and inertia shortfalls, and from the 2019 Notice of Tasmania system strength and inertia shortfalls. It is expected that this spreadsheet will be updated from time to time as system strength and inertia information is released by AEMO. This spreadsheet and the reports it relates to can be accessed via https://aemo.com.au/en/energy-systems/electricity/national-electricity-market-nem/nem-forecasting-and-planning/planning-for-operability.
Disclaimer
This dataset or the information in it may be subsequently updated or amended. This work does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed legal advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document: • make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this workbook; and • are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this workbook.
Worksheet index
Worksheet | Description
2021 TAS System strength | This is the 2020 fault level projection duration curve data for each fault level node in the Tasmania region of the National Electricity Market. These charts are used in the 2020 System Strength and Inertia Report and the 2021 Notice of Tasmania system strength and inertia shortfalls.
2021 TAS Inertia | This is the 2020 inertia projection duration curve data for the Tasmania region of the National Electricity Market. These charts are used in the 2020 System Strength and Inertia Report and the 2021 Notice of Tasmania system strength and inertia shortfalls.
2019 TAS System strength | This is the 2019 fault level projection duration curve data for each fault level node in the Tasmania region of the National Electricity Market. These charts are used in the 2019 Notice of inertia and fault level shortfalls in Tasmania.
2019 TAS Inertia | This is the 2019 inertia projection duration curve data for the Tasmania region of the National Electricity Market. These charts are used in the 2019 Notice of inertia and fault level shortfalls in Tasmania.
References
System Strength Requirements Methodology
2020 System Strength and Inertia Report
2019 Notice of Inertia and Fault Level Shortfalls in Tasmania
2021 Notice of Tasmania system strength and inertia shortfalls

## 2021 TAS System strength
2021 Tasmania system strength
This is the 2020 fault level projection duration curve data for each fault level node in the Tasmania region of the National Electricity Market. These charts are used in the 2020 System Strength and Inertia Report and the 2021 Notice of Tasmania system strength and inertia shortfalls.
| Burnie Fault Level Node | [9 empty] | George Town Fault Level Node | [10 empty] | Waddamana Fault Level Node | [9 empty] | Risdon Fault Level Node
|  | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | 2029-30 Fault Levels (MVA) | Post-Contingent Requirement (MVA) |  |  | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | 2029-30 Fault Levels (MVA) | Pre-Contingent Requirement |  |  | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | 2029-30 Fault Levels (MVA) | Pre-Contingent Requirement |  |  | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | 2029-30 Fault Levels (MVA) | Pre-Contingent Requirement
| 0% | 683 | 684 | 685 | 685 | 679 | 682 | 683 | 560 |  | 0% | 2978 | 2995 | 3007 | 3105 | 3074 | 2951 | 2978 | 1450 |  | 0% | 3186 | 3212 | 3220 | 3205 | 3209 | 3192 | 3173 | 1400 |  | 0% | 2091 | 2093 | 2099 | 2095 | 2096 | 2091 | 2088 | 1330
| 1% | 674 | 674 | 678 | 679 | 673 | 673 | 675 | 560 |  | 1% | 2796 | 2782 | 2758 | 2831 | 2830 | 2699 | 2723 | 1450 |  | 1% | 3095 | 3121 | 3134 | 3140 | 3137 | 3111 | 3114 | 1400 |  | 1% | 2066 | 2072 | 2078 | 2077 | 2079 | 2067 | 2070 | 1330
| 2% | 671 | 671 | 676 | 676 | 671 | 670 | 671 | 560 |  | 2% | 2716 | 2710 | 2727 | 2739 | 2720 | 2647 | 2674 | 1450 |  | 2% | 3064 | 3085 | 3109 | 3104 | 3115 | 3057 | 3073 | 1400 |  | 2% | 2054 | 2062 | 2066 | 2068 | 2068 | 2054 | 2061 | 1330
| 3% | 669 | 668 | 673 | 674 | 669 | 667 | 669 | 560 |  | 3% | 2667 | 2656 | 2679 | 2702 | 2685 | 2581 | 2621 | 1450 |  | 3% | 3021 | 3052 | 3069 | 3075 | 3071 | 3009 | 3040 | 1400 |  | 3% | 2042 | 2049 | 2056 | 2058 | 2056 | 2041 | 2050 | 1330
| 4% | 666 | 665 | 671 | 672 | 667 | 663 | 666 | 560 |  | 4% | 2612 | 2608 | 2648 | 2654 | 2648 | 2525 | 2577 | 1450 |  | 4% | 2981 | 3013 | 3028 | 3038 | 3020 | 2970 | 3014 | 1400 |  | 4% | 2028 | 2037 | 2042 | 2049 | 2039 | 2028 | 2040 | 1330
| 5% | 664 | 662 | 669 | 670 | 665 | 661 | 664 | 560 |  | 5% | 2568 | 2564 | 2602 | 2624 | 2592 | 2477 | 2546 | 1450 |  | 5% | 2944 | 2981 | 2981 | 3010 | 2969 | 2930 | 2981 | 1400 |  | 5% | 2021 | 2028 | 2024 | 2040 | 2023 | 2020 | 2029 | 1330
| 6% | 663 | 661 | 667 | 668 | 663 | 659 | 662 | 560 |  | 6% | 2529 | 2532 | 2554 | 2581 | 2560 | 2447 | 2503 | 1450 |  | 6% | 2906 | 2962 | 2955 | 2977 | 2935 | 2913 | 2958 | 1400 |  | 6% | 2012 | 2019 | 2010 | 2032 | 2014 | 2015 | 2018 | 1330
| 7% | 659 | 657 | 663 | 666 | 660 | 656 | 659 | 560 |  | 7% | 2466 | 2455 | 2497 | 2530 | 2492 | 2412 | 2446 | 1450 |  | 7% | 2871 | 2915 | 2907 | 2940 | 2897 | 2883 | 2916 | 1400 |  | 7% | 1997 | 2009 | 1986 | 2020 | 2004 | 2004 | 2001 | 1330
| 8% | 658 | 654 | 662 | 664 | 658 | 655 | 658 | 560 |  | 8% | 2436 | 2432 | 2471 | 2498 | 2466 | 2391 | 2431 | 1450 |  | 8% | 2858 | 2908 | 2891 | 2917 | 2888 | 2866 | 2903 | 1400 |  | 8% | 1992 | 2004 | 1974 | 2014 | 1999 | 1999 | 1994 | 1330
| 9% | 656 | 653 | 660 | 662 | 657 | 653 | 656 | 560 |  | 9% | 2409 | 2411 | 2444 | 2471 | 2447 | 2376 | 2417 | 1450 |  | 9% | 2842 | 2891 | 2873 | 2901 | 2872 | 2857 | 2885 | 1400 |  | 9% | 1986 | 1996 | 1966 | 2009 | 1994 | 1995 | 1988 | 1330
| 10% | 654 | 652 | 659 | 661 | 656 | 652 | 655 | 560 |  | 10% | 2386 | 2393 | 2427 | 2448 | 2428 | 2361 | 2405 | 1450 |  | 10% | 2827 | 2880 | 2855 | 2891 | 2860 | 2844 | 2867 | 1400 |  | 10% | 1977 | 1987 | 1958 | 2006 | 1990 | 1991 | 1981 | 1330
| 11% | 652 | 651 | 658 | 659 | 655 | 650 | 654 | 560 |  | 11% | 2367 | 2371 | 2405 | 2433 | 2407 | 2347 | 2392 | 1450 |  | 11% | 2815 | 2867 | 2843 | 2882 | 2847 | 2838 | 2851 | 1400 |  | 11% | 1971 | 1979 | 1953 | 2000 | 1983 | 1984 | 1973 | 1330
| 12% | 652 | 651 | 658 | 659 | 655 | 650 | 654 | 560 |  | 12% | 2367 | 2371 | 2405 | 2433 | 2407 | 2347 | 2392 | 1450 |  | 12% | 2815 | 2867 | 2843 | 2882 | 2847 | 2838 | 2851 | 1400 |  | 12% | 1971 | 1979 | 1953 | 2000 | 1983 | 1984 | 1973 | 1330
| 13% | 650 | 650 | 656 | 658 | 654 | 649 | 652 | 560 |  | 13% | 2353 | 2357 | 2393 | 2414 | 2381 | 2337 | 2377 | 1450 |  | 13% | 2802 | 2855 | 2829 | 2872 | 2838 | 2825 | 2837 | 1400 |  | 13% | 1962 | 1971 | 1944 | 1993 | 1979 | 1979 | 1966 | 1330
| 14% | 647 | 648 | 655 | 655 | 652 | 647 | 650 | 560 |  | 14% | 2340 | 2339 | 2381 | 2390 | 2362 | 2327 | 2362 | 1450 |  | 14% | 2789 | 2841 | 2814 | 2860 | 2826 | 2814 | 2823 | 1400 |  | 14% | 1955 | 1960 | 1935 | 1986 | 1972 | 1974 | 1960 | 1330
| 15% | 643 | 647 | 652 | 654 | 650 | 646 | 649 | 560 |  | 15% | 2325 | 2322 | 2366 | 2370 | 2351 | 2318 | 2348 | 1450 |  | 15% | 2773 | 2824 | 2799 | 2846 | 2818 | 2803 | 2811 | 1400 |  | 15% | 1944 | 1952 | 1925 | 1974 | 1962 | 1966 | 1952 | 1330
| 16% | 642 | 644 | 650 | 649 | 648 | 645 | 648 | 560 |  | 16% | 2307 | 2305 | 2353 | 2361 | 2343 | 2309 | 2334 | 1450 |  | 16% | 2762 | 2811 | 2781 | 2833 | 2810 | 2794 | 2798 | 1400 |  | 16% | 1934 | 1943 | 1914 | 1965 | 1955 | 1958 | 1944 | 1330
| 17% | 642 | 641 | 649 | 647 | 646 | 645 | 646 | 560 |  | 17% | 2284 | 2287 | 2342 | 2351 | 2333 | 2299 | 2324 | 1450 |  | 17% | 2748 | 2796 | 2766 | 2819 | 2796 | 2779 | 2786 | 1400 |  | 17% | 1926 | 1936 | 1903 | 1954 | 1946 | 1950 | 1936 | 1330
| 18% | 640 | 639 | 648 | 646 | 645 | 644 | 645 | 560 |  | 18% | 2270 | 2279 | 2327 | 2341 | 2319 | 2288 | 2311 | 1450 |  | 18% | 2728 | 2779 | 2746 | 2804 | 2779 | 2768 | 2775 | 1400 |  | 18% | 1917 | 1928 | 1890 | 1942 | 1940 | 1942 | 1927 | 1330
| 19% | 636 | 636 | 646 | 645 | 644 | 641 | 643 | 560 |  | 19% | 2229 | 2254 | 2300 | 2310 | 2281 | 2266 | 2284 | 1450 |  | 19% | 2686 | 2739 | 2691 | 2762 | 2754 | 2738 | 2740 | 1400 |  | 19% | 1898 | 1910 | 1867 | 1927 | 1923 | 1928 | 1912 | 1330
| 20% | 633 | 635 | 645 | 644 | 642 | 640 | 642 | 560 |  | 20% | 2208 | 2238 | 2285 | 2287 | 2266 | 2252 | 2272 | 1450 |  | 20% | 2664 | 2712 | 2654 | 2740 | 2735 | 2721 | 2721 | 1400 |  | 20% | 1886 | 1903 | 1857 | 1912 | 1916 | 1920 | 1903 | 1330
| 21% | 631 | 634 | 643 | 642 | 641 | 640 | 640 | 560 |  | 21% | 2179 | 2231 | 2275 | 2278 | 2249 | 2243 | 2257 | 1450 |  | 21% | 2641 | 2688 | 2622 | 2718 | 2720 | 2704 | 2704 | 1400 |  | 21% | 1874 | 1892 | 1841 | 1902 | 1908 | 1912 | 1894 | 1330
| 22% | 628 | 632 | 642 | 639 | 639 | 639 | 638 | 560 |  | 22% | 2152 | 2213 | 2261 | 2258 | 2234 | 2234 | 2244 | 1450 |  | 22% | 2608 | 2658 | 2595 | 2690 | 2701 | 2689 | 2683 | 1400 |  | 22% | 1862 | 1880 | 1820 | 1889 | 1897 | 1902 | 1884 | 1330
| 23% | 626 | 630 | 639 | 638 | 636 | 637 | 636 | 560 |  | 23% | 2145 | 2195 | 2240 | 2239 | 2223 | 2224 | 2233 | 1450 |  | 23% | 2578 | 2630 | 2549 | 2658 | 2674 | 2666 | 2663 | 1400 |  | 23% | 1847 | 1866 | 1796 | 1874 | 1884 | 1893 | 1871 | 1330
| 24% | 626 | 630 | 639 | 638 | 636 | 637 | 636 | 560 |  | 24% | 2145 | 2195 | 2240 | 2239 | 2223 | 2224 | 2233 | 1450 |  | 24% | 2578 | 2630 | 2549 | 2658 | 2674 | 2666 | 2663 | 1400 |  | 24% | 1847 | 1866 | 1796 | 1874 | 1884 | 1893 | 1871 | 1330
| 25% | 621 | 627 | 637 | 636 | 634 | 635 | 635 | 560 |  | 25% | 2122 | 2169 | 2216 | 2219 | 2201 | 2208 | 2223 | 1450 |  | 25% | 2548 | 2589 | 2509 | 2625 | 2645 | 2643 | 2639 | 1400 |  | 25% | 1831 | 1847 | 1771 | 1858 | 1868 | 1883 | 1860 | 1330
| 26% | 615 | 623 | 633 | 635 | 629 | 633 | 632 | 560 |  | 26% | 2090 | 2148 | 2187 | 2197 | 2192 | 2191 | 2210 | 1450 |  | 26% | 2505 | 2550 | 2475 | 2590 | 2612 | 2618 | 2607 | 1400 |  | 26% | 1806 | 1822 | 1747 | 1836 | 1852 | 1869 | 1846 | 1330
| 27% | 610 | 619 | 630 | 633 | 628 | 630 | 630 | 560 |  | 27% | 2064 | 2118 | 2149 | 2171 | 2176 | 2174 | 2194 | 1450 |  | 27% | 2452 | 2508 | 2423 | 2548 | 2573 | 2596 | 2584 | 1400 |  | 27% | 1781 | 1794 | 1729 | 1808 | 1832 | 1857 | 1831 | 1330
| 28% | 606 | 613 | 625 | 632 | 626 | 627 | 626 | 560 |  | 28% | 2044 | 2081 | 2108 | 2156 | 2152 | 2154 | 2178 | 1450 |  | 28% | 2399 | 2459 | 2370 | 2510 | 2531 | 2567 | 2554 | 1400 |  | 28% | 1758 | 1770 | 1708 | 1784 | 1813 | 1840 | 1814 | 1330
| 29% | 600 | 608 | 622 | 629 | 624 | 622 | 622 | 560 |  | 29% | 2013 | 2043 | 2066 | 2132 | 2117 | 2143 | 2161 | 1450 |  | 29% | 2349 | 2411 | 2338 | 2470 | 2485 | 2528 | 2528 | 1400 |  | 29% | 1735 | 1749 | 1688 | 1761 | 1787 | 1823 | 1799 | 1330
| 30% | 595 | 604 | 617 | 627 | 620 | 619 | 619 | 560 |  | 30% | 1970 | 1995 | 2009 | 2102 | 2094 | 2110 | 2145 | 1450 |  | 30% | 2298 | 2348 | 2306 | 2434 | 2434 | 2490 | 2492 | 1400 |  | 30% | 1711 | 1724 | 1676 | 1744 | 1762 | 1800 | 1783 | 1330
| 31% | 593 | 600 | 612 | 623 | 617 | 615 | 616 | 560 |  | 31% | 1926 | 1953 | 1968 | 2064 | 2059 | 2083 | 2117 | 1450 |  | 31% | 2248 | 2288 | 2267 | 2389 | 2386 | 2446 | 2454 | 1400 |  | 31% | 1689 | 1700 | 1660 | 1726 | 1735 | 1781 | 1767 | 1330
| 32% | 593 | 593 | 608 | 618 | 612 | 606 | 608 | 560 |  | 32% | 1856 | 1857 | 1867 | 2001 | 1982 | 2042 | 2066 | 1450 |  | 32% | 2150 | 2195 | 2177 | 2306 | 2320 | 2362 | 2387 | 1400 |  | 32% | 1638 | 1649 | 1621 | 1691 | 1691 | 1739 | 1728 | 1330
| 33% | 593 | 591 | 606 | 614 | 609 | 604 | 604 | 560 |  | 33% | 1813 | 1818 | 1833 | 1959 | 1949 | 2021 | 2036 | 1450 |  | 33% | 2121 | 2150 | 2125 | 2271 | 2287 | 2328 | 2351 | 1400 |  | 33% | 1619 | 1631 | 1614 | 1671 | 1677 | 1715 | 1709 | 1330
| 34% | 593 | 586 | 604 | 611 | 604 | 604 | 604 | 560 |  | 34% | 1782 | 1772 | 1820 | 1915 | 1912 | 1984 | 2006 | 1450 |  | 34% | 2078 | 2116 | 2115 | 2230 | 2247 | 2286 | 2310 | 1400 |  | 34% | 1601 | 1613 | 1597 | 1658 | 1663 | 1692 | 1693 | 1330
| 35% | 593 | 586 | 604 | 611 | 604 | 604 | 604 | 560 |  | 35% | 1782 | 1772 | 1820 | 1915 | 1912 | 1984 | 2006 | 1450 |  | 35% | 2078 | 2116 | 2115 | 2230 | 2247 | 2286 | 2310 | 1400 |  | 35% | 1601 | 1613 | 1597 | 1658 | 1663 | 1692 | 1693 | 1330
| 36% | 593 | 586 | 604 | 605 | 604 | 604 | 604 | 560 |  | 36% | 1751 | 1735 | 1792 | 1867 | 1875 | 1965 | 1983 | 1450 |  | 36% | 2052 | 2068 | 2082 | 2190 | 2200 | 2246 | 2265 | 1400 |  | 36% | 1584 | 1592 | 1583 | 1644 | 1647 | 1673 | 1676 | 1330
| 37% | 593 | 586 | 604 | 604 | 604 | 604 | 604 | 560 |  | 37% | 1714 | 1708 | 1761 | 1848 | 1865 | 1927 | 1956 | 1450 |  | 37% | 2010 | 2046 | 2048 | 2169 | 2179 | 2195 | 2228 | 1400 |  | 37% | 1570 | 1579 | 1574 | 1629 | 1629 | 1654 | 1658 | 1330
| 38% | 592 | 586 | 604 | 604 | 604 | 604 | 604 | 560 |  | 38% | 1672 | 1675 | 1749 | 1811 | 1842 | 1874 | 1917 | 1450 |  | 38% | 1985 | 2019 | 2026 | 2131 | 2147 | 2195 | 2191 | 1400 |  | 38% | 1555 | 1568 | 1574 | 1616 | 1623 | 1634 | 1642 | 1330
| 39% | 592 | 586 | 604 | 604 | 604 | 603 | 604 | 560 |  | 39% | 1659 | 1632 | 1749 | 1761 | 1790 | 1858 | 1869 | 1450 |  | 39% | 1957 | 1981 | 2026 | 2098 | 2119 | 2169 | 2168 | 1400 |  | 39% | 1542 | 1549 | 1574 | 1600 | 1608 | 1633 | 1628 | 1330
| 40% | 591 | 586 | 603 | 604 | 604 | 603 | 603 | 560 |  | 40% | 1659 | 1623 | 1749 | 1749 | 1759 | 1824 | 1842 | 1450 |  | 40% | 1927 | 1945 | 2026 | 2058 | 2093 | 2146 | 2125 | 1400 |  | 40% | 1526 | 1543 | 1574 | 1585 | 1599 | 1622 | 1612 | 1330
| 41% | 591 | 586 | 603 | 604 | 604 | 602 | 603 | 560 |  | 41% | 1659 | 1623 | 1749 | 1749 | 1749 | 1786 | 1793 | 1450 |  | 41% | 1911 | 1945 | 2026 | 2026 | 2042 | 2112 | 2098 | 1400 |  | 41% | 1522 | 1543 | 1574 | 1574 | 1574 | 1610 | 1600 | 1330
| 42% | 590 | 585 | 602 | 604 | 603 | 601 | 602 | 560 |  | 42% | 1659 | 1623 | 1749 | 1749 | 1749 | 1749 | 1749 | 1450 |  | 42% | 1911 | 1945 | 2026 | 2026 | 2026 | 2088 | 2053 | 1400 |  | 42% | 1522 | 1543 | 1568 | 1574 | 1574 | 1599 | 1577 | 1330
| 43% | 589 | 585 | 601 | 603 | 603 | 600 | 602 | 560 |  | 43% | 1659 | 1623 | 1745 | 1749 | 1749 | 1749 | 1749 | 1450 |  | 43% | 1911 | 1945 | 2020 | 2026 | 2026 | 2048 | 2026 | 1400 |  | 43% | 1522 | 1543 | 1561 | 1574 | 1574 | 1581 | 1574 | 1330
| 44% | 584 | 583 | 598 | 602 | 602 | 596 | 597 | 560 |  | 44% | 1659 | 1619 | 1727 | 1746 | 1749 | 1749 | 1749 | 1450 |  | 44% | 1911 | 1945 | 2000 | 2026 | 2026 | 2026 | 2026 | 1400 |  | 44% | 1522 | 1537 | 1544 | 1574 | 1574 | 1574 | 1574 | 1330
| 45% | 581 | 582 | 596 | 601 | 601 | 594 | 596 | 560 |  | 45% | 1655 | 1613 | 1719 | 1740 | 1749 | 1749 | 1749 | 1450 |  | 45% | 1911 | 1932 | 1979 | 2026 | 2026 | 2026 | 2026 | 1400 |  | 45% | 1522 | 1530 | 1537 | 1574 | 1574 | 1574 | 1574 | 1330
| 46% | 578 | 580 | 594 | 600 | 598 | 593 | 594 | 560 |  | 46% | 1649 | 1607 | 1703 | 1739 | 1745 | 1745 | 1749 | 1450 |  | 46% | 1911 | 1921 | 1963 | 2019 | 2026 | 2026 | 2026 | 1400 |  | 46% | 1522 | 1524 | 1530 | 1564 | 1574 | 1574 | 1574 | 1330
| 47% | 578 | 580 | 594 | 600 | 598 | 593 | 594 | 560 |  | 47% | 1649 | 1607 | 1703 | 1739 | 1745 | 1745 | 1749 | 1450 |  | 47% | 1911 | 1921 | 1963 | 2019 | 2026 | 2026 | 2026 | 1400 |  | 47% | 1522 | 1524 | 1530 | 1564 | 1574 | 1574 | 1574 | 1330
| 48% | 577 | 577 | 593 | 596 | 595 | 592 | 592 | 560 |  | 48% | 1638 | 1600 | 1687 | 1727 | 1739 | 1739 | 1746 | 1450 |  | 48% | 1904 | 1904 | 1951 | 2007 | 2019 | 2026 | 2026 | 1400 |  | 48% | 1514 | 1521 | 1523 | 1557 | 1566 | 1574 | 1574 | 1330
| 49% | 576 | 575 | 590 | 594 | 592 | 590 | 590 | 560 |  | 49% | 1634 | 1591 | 1669 | 1722 | 1728 | 1727 | 1739 | 1450 |  | 49% | 1892 | 1893 | 1936 | 1999 | 2007 | 2019 | 2019 | 1400 |  | 49% | 1508 | 1511 | 1510 | 1555 | 1559 | 1566 | 1566 | 1330
| 50% | 574 | 572 | 587 | 591 | 589 | 588 | 588 | 560 |  | 50% | 1627 | 1575 | 1645 | 1703 | 1724 | 1722 | 1728 | 1450 |  | 50% | 1884 | 1881 | 1912 | 1975 | 1998 | 2001 | 2007 | 1400 |  | 50% | 1502 | 1505 | 1500 | 1545 | 1555 | 1559 | 1555 | 1330
| 51% | 572 | 569 | 585 | 589 | 586 | 586 | 586 | 560 |  | 51% | 1613 | 1556 | 1626 | 1683 | 1716 | 1716 | 1722 | 1450 |  | 51% | 1866 | 1869 | 1904 | 1960 | 1975 | 1986 | 1991 | 1400 |  | 51% | 1493 | 1496 | 1485 | 1539 | 1545 | 1554 | 1550 | 1330
| 52% | 570 | 565 | 582 | 586 | 585 | 585 | 585 | 560 |  | 52% | 1597 | 1534 | 1609 | 1668 | 1701 | 1694 | 1711 | 1450 |  | 52% | 1858 | 1851 | 1887 | 1945 | 1963 | 1967 | 1972 | 1400 |  | 52% | 1486 | 1485 | 1478 | 1530 | 1539 | 1543 | 1541 | 1330
| 53% | 568 | 562 | 579 | 582 | 582 | 582 | 582 | 560 |  | 53% | 1575 | 1507 | 1592 | 1646 | 1678 | 1673 | 1686 | 1450 |  | 53% | 1847 | 1833 | 1867 | 1936 | 1951 | 1961 | 1951 | 1400 |  | 53% | 1482 | 1478 | 1464 | 1524 | 1535 | 1538 | 1537 | 1330
| 54% | 565 | 558 | 577 | 579 | 578 | 580 | 580 | 560 |  | 54% | 1555 | 1489 | 1574 | 1623 | 1652 | 1652 | 1652 | 1450 |  | 54% | 1832 | 1811 | 1844 | 1910 | 1944 | 1947 | 1937 | 1400 |  | 54% | 1476 | 1470 | 1450 | 1514 | 1522 | 1530 | 1523 | 1330
| 55% | 564 | 556 | 574 | 577 | 575 | 577 | 578 | 560 |  | 55% | 1535 | 1476 | 1563 | 1608 | 1623 | 1626 | 1623 | 1450 |  | 55% | 1824 | 1800 | 1820 | 1900 | 1935 | 1938 | 1910 | 1400 |  | 55% | 1467 | 1459 | 1444 | 1499 | 1510 | 1520 | 1510 | 1330
| 56% | 563 | 554 | 572 | 576 | 572 | 576 | 576 | 560 |  | 56% | 1519 | 1462 | 1549 | 1592 | 1609 | 1609 | 1603 | 1450 |  | 56% | 1814 | 1782 | 1801 | 1872 | 1906 | 1920 | 1889 | 1400 |  | 56% | 1457 | 1447 | 1432 | 1485 | 1507 | 1510 | 1496 | 1330
| 57% | 561 | 552 | 569 | 574 | 569 | 573 | 572 | 560 |  | 57% | 1507 | 1449 | 1534 | 1567 | 1595 | 1583 | 1566 | 1450 |  | 57% | 1792 | 1765 | 1785 | 1846 | 1882 | 1903 | 1845 | 1400 |  | 57% | 1455 | 1438 | 1422 | 1474 | 1492 | 1506 | 1480 | 1330
| 58% | 559 | 549 | 565 | 571 | 566 | 570 | 568 | 560 |  | 58% | 1491 | 1432 | 1516 | 1553 | 1573 | 1563 | 1548 | 1450 |  | 58% | 1779 | 1745 | 1771 | 1821 | 1853 | 1877 | 1803 | 1400 |  | 58% | 1442 | 1427 | 1410 | 1460 | 1480 | 1489 | 1462 | 1330
| 59% | 556 | 548 | 562 | 568 | 562 | 567 | 564 | 560 |  | 59% | 1475 | 1422 | 1498 | 1535 | 1555 | 1541 | 1519 | 1450 |  | 59% | 1764 | 1727 | 1762 | 1799 | 1821 | 1838 | 1780 | 1400 |  | 59% | 1431 | 1416 | 1398 | 1446 | 1465 | 1480 | 1446 | 1330
| 60% | 554 | 545 | 559 | 565 | 559 | 564 | 559 | 560 |  | 60% | 1463 | 1413 | 1482 | 1519 | 1538 | 1519 | 1485 | 1450 |  | 60% | 1744 | 1708 | 1747 | 1780 | 1794 | 1815 | 1765 | 1400 |  | 60% | 1421 | 1407 | 1390 | 1433 | 1453 | 1466 | 1430 | 1330
| 61% | 551 | 541 | 555 | 561 | 556 | 561 | 555 | 560 |  | 61% | 1444 | 1401 | 1471 | 1503 | 1514 | 1495 | 1461 | 1450 |  | 61% | 1725 | 1693 | 1732 | 1768 | 1778 | 1791 | 1737 | 1400 |  | 61% | 1414 | 1400 | 1379 | 1422 | 1440 | 1454 | 1412 | 1330
| 62% | 547 | 537 | 553 | 557 | 553 | 558 | 551 | 560 |  | 62% | 1429 | 1388 | 1455 | 1489 | 1489 | 1479 | 1424 | 1450 |  | 62% | 1711 | 1679 | 1717 | 1749 | 1763 | 1776 | 1715 | 1400 |  | 62% | 1403 | 1391 | 1376 | 1409 | 1426 | 1438 | 1397 | 1330
| 63% | 544 | 534 | 549 | 553 | 551 | 555 | 546 | 560 |  | 63% | 1414 | 1373 | 1438 | 1474 | 1469 | 1463 | 1406 | 1450 |  | 63% | 1686 | 1667 | 1703 | 1725 | 1743 | 1757 | 1693 | 1400 |  | 63% | 1395 | 1380 | 1366 | 1397 | 1412 | 1423 | 1381 | 1330
| 64% | 540 | 530 | 547 | 551 | 549 | 552 | 543 | 560 |  | 64% | 1392 | 1358 | 1422 | 1460 | 1452 | 1445 | 1387 | 1450 |  | 64% | 1669 | 1651 | 1688 | 1709 | 1719 | 1732 | 1663 | 1400 |  | 64% | 1385 | 1370 | 1356 | 1383 | 1401 | 1413 | 1378 | 1330
| 65% | 537 | 527 | 544 | 548 | 546 | 549 | 540 | 560 |  | 65% | 1378 | 1351 | 1407 | 1442 | 1436 | 1425 | 1370 | 1450 |  | 65% | 1655 | 1633 | 1670 | 1692 | 1701 | 1715 | 1642 | 1400 |  | 65% | 1376 | 1361 | 1347 | 1379 | 1389 | 1401 | 1363 | 1330
| 66% | 532 | 520 | 538 | 544 | 541 | 544 | 531 | 560 |  | 66% | 1354 | 1327 | 1389 | 1414 | 1406 | 1399 | 1332 | 1450 |  | 66% | 1618 | 1599 | 1639 | 1659 | 1662 | 1673 | 1586 | 1400 |  | 66% | 1359 | 1341 | 1334 | 1358 | 1367 | 1379 | 1341 | 1330
| 67% | 529 | 518 | 536 | 541 | 540 | 542 | 528 | 560 |  | 67% | 1337 | 1311 | 1375 | 1400 | 1393 | 1384 | 1309 | 1450 |  | 67% | 1609 | 1580 | 1622 | 1644 | 1644 | 1656 | 1574 | 1400 |  | 67% | 1349 | 1330 | 1324 | 1347 | 1357 | 1373 | 1330 | 1330
| 68% | 526 | 515 | 533 | 539 | 538 | 540 | 522 | 560 |  | 68% | 1319 | 1301 | 1363 | 1386 | 1375 | 1370 | 1288 | 1450 |  | 68% | 1599 | 1565 | 1599 | 1627 | 1626 | 1633 | 1558 | 1400 |  | 68% | 1342 | 1319 | 1315 | 1341 | 1346 | 1362 | 1314 | 1330
| 69% | 526 | 515 | 533 | 539 | 538 | 540 | 522 | 560 |  | 69% | 1319 | 1301 | 1363 | 1386 | 1375 | 1370 | 1288 | 1450 |  | 69% | 1599 | 1565 | 1599 | 1627 | 1626 | 1633 | 1558 | 1400 |  | 69% | 1342 | 1319 | 1315 | 1341 | 1346 | 1362 | 1314 | 1330
| 70% | 526 | 513 | 530 | 536 | 535 | 537 | 516 | 560 |  | 70% | 1301 | 1290 | 1347 | 1374 | 1370 | 1356 | 1266 | 1450 |  | 70% | 1587 | 1554 | 1582 | 1602 | 1618 | 1611 | 1538 | 1400 |  | 70% | 1334 | 1310 | 1308 | 1331 | 1338 | 1352 | 1300 | 1330
| 71% | 524 | 511 | 528 | 533 | 532 | 532 | 512 | 560 |  | 71% | 1295 | 1277 | 1335 | 1359 | 1357 | 1343 | 1248 | 1450 |  | 71% | 1573 | 1537 | 1574 | 1583 | 1597 | 1583 | 1508 | 1400 |  | 71% | 1324 | 1307 | 1299 | 1318 | 1327 | 1342 | 1286 | 1330
| 72% | 520 | 508 | 524 | 530 | 529 | 528 | 506 | 560 |  | 72% | 1282 | 1263 | 1324 | 1344 | 1343 | 1331 | 1226 | 1450 |  | 72% | 1554 | 1525 | 1569 | 1572 | 1575 | 1574 | 1490 | 1400 |  | 72% | 1316 | 1298 | 1289 | 1310 | 1323 | 1334 | 1269 | 1330
| 73% | 516 | 506 | 521 | 527 | 527 | 524 | 503 | 560 |  | 73% | 1266 | 1253 | 1312 | 1334 | 1329 | 1317 | 1210 | 1450 |  | 73% | 1539 | 1510 | 1552 | 1559 | 1564 | 1561 | 1467 | 1400 |  | 73% | 1307 | 1292 | 1279 | 1300 | 1313 | 1326 | 1247 | 1330
| 74% | 512 | 503 | 518 | 523 | 524 | 519 | 499 | 560 |  | 74% | 1254 | 1240 | 1299 | 1320 | 1315 | 1302 | 1199 | 1450 |  | 74% | 1522 | 1493 | 1538 | 1548 | 1552 | 1552 | 1434 | 1400 |  | 74% | 1300 | 1283 | 1270 | 1294 | 1303 | 1312 | 1232 | 1330
| 75% | 507 | 501 | 515 | 520 | 522 | 515 | 494 | 560 |  | 75% | 1236 | 1222 | 1283 | 1305 | 1301 | 1289 | 1185 | 1450 |  | 75% | 1511 | 1476 | 1523 | 1527 | 1537 | 1538 | 1429 | 1400 |  | 75% | 1288 | 1275 | 1261 | 1281 | 1296 | 1302 | 1232 | 1330
| 76% | 503 | 499 | 511 | 517 | 520 | 513 | 491 | 560 |  | 76% | 1227 | 1208 | 1272 | 1291 | 1289 | 1275 | 1172 | 1450 |  | 76% | 1499 | 1454 | 1508 | 1506 | 1516 | 1518 | 1412 | 1400 |  | 76% | 1279 | 1266 | 1247 | 1270 | 1286 | 1293 | 1216 | 1330
| 77% | 498 | 496 | 506 | 515 | 518 | 509 | 485 | 560 |  | 77% | 1212 | 1192 | 1257 | 1280 | 1275 | 1260 | 1152 | 1450 |  | 77% | 1482 | 1439 | 1497 | 1492 | 1499 | 1501 | 1380 | 1400 |  | 77% | 1276 | 1259 | 1235 | 1261 | 1275 | 1281 | 1196 | 1330
| 78% | 495 | 494 | 504 | 512 | 515 | 506 | 482 | 560 |  | 78% | 1195 | 1179 | 1240 | 1265 | 1260 | 1244 | 1127 | 1450 |  | 78% | 1464 | 1433 | 1480 | 1477 | 1483 | 1485 | 1352 | 1400 |  | 78% | 1263 | 1248 | 1232 | 1252 | 1261 | 1270 | 1178 | 1330
| 79% | 489 | 491 | 502 | 508 | 513 | 502 | 479 | 560 |  | 79% | 1175 | 1165 | 1223 | 1252 | 1245 | 1228 | 1127 | 1450 |  | 79% | 1449 | 1421 | 1458 | 1459 | 1461 | 1467 | 1323 | 1400 |  | 79% | 1257 | 1239 | 1218 | 1239 | 1248 | 1255 | 1160 | 1330
| 80% | 486 | 488 | 499 | 505 | 509 | 499 | 475 | 560 |  | 80% | 1160 | 1144 | 1210 | 1240 | 1226 | 1210 | 1108 | 1450 |  | 80% | 1432 | 1409 | 1437 | 1439 | 1442 | 1442 | 1290 | 1400 |  | 80% | 1245 | 1231 | 1206 | 1232 | 1235 | 1241 | 1140 | 1330
| 81% | 483 | 484 | 497 | 503 | 506 | 496 | 471 | 560 |  | 81% | 1153 | 1132 | 1200 | 1220 | 1212 | 1208 | 1087 | 1450 |  | 81% | 1418 | 1387 | 1423 | 1429 | 1429 | 1429 | 1265 | 1400 |  | 81% | 1238 | 1218 | 1196 | 1223 | 1226 | 1232 | 1118 | 1330
| 82% | 479 | 480 | 494 | 500 | 503 | 493 | 469 | 560 |  | 82% | 1148 | 1119 | 1188 | 1210 | 1202 | 1198 | 1062 | 1450 |  | 82% | 1403 | 1368 | 1404 | 1409 | 1412 | 1413 | 1227 | 1400 |  | 82% | 1225 | 1206 | 1182 | 1208 | 1216 | 1216 | 1091 | 1330
| 83% | 475 | 477 | 491 | 497 | 500 | 488 | 464 | 560 |  | 83% | 1134 | 1106 | 1178 | 1197 | 1193 | 1187 | 1044 | 1450 |  | 83% | 1380 | 1353 | 1381 | 1389 | 1391 | 1393 | 1186 | 1400 |  | 83% | 1212 | 1193 | 1169 | 1196 | 1199 | 1201 | 1067 | 1330
| 84% | 470 | 475 | 487 | 494 | 497 | 483 | 457 | 560 |  | 84% | 1117 | 1093 | 1157 | 1182 | 1181 | 1174 | 1009 | 1450 |  | 84% | 1365 | 1336 | 1362 | 1368 | 1368 | 1368 | 1148 | 1400 |  | 84% | 1191 | 1178 | 1151 | 1185 | 1185 | 1186 | 1040 | 1330
| 85% | 463 | 471 | 483 | 490 | 493 | 483 | 448 | 560 |  | 85% | 1101 | 1070 | 1141 | 1164 | 1168 | 1163 | 972 | 1450 |  | 85% | 1363 | 1308 | 1337 | 1350 | 1341 | 1343 | 1097 | 1400 |  | 85% | 1186 | 1164 | 1135 | 1170 | 1173 | 1170 | 1008 | 1330
| 86% | 460 | 467 | 482 | 485 | 490 | 481 | 439 | 560 |  | 86% | 1089 | 1054 | 1127 | 1147 | 1149 | 1143 | 947 | 1450 |  | 86% | 1338 | 1288 | 1314 | 1325 | 1318 | 1318 | 1065 | 1400 |  | 86% | 1180 | 1152 | 1128 | 1154 | 1156 | 1155 | 982 | 1330
| 87% | 459 | 462 | 478 | 482 | 489 | 477 | 428 | 560 |  | 87% | 1073 | 1045 | 1106 | 1127 | 1142 | 1127 | 886 | 1450 |  | 87% | 1302 | 1275 | 1290 | 1294 | 1295 | 1290 | 1026 | 1400 |  | 87% | 1155 | 1138 | 1109 | 1139 | 1139 | 1138 | 957 | 1330
| 88% | 455 | 457 | 475 | 478 | 483 | 474 | 428 | 560 |  | 88% | 1059 | 1030 | 1091 | 1106 | 1134 | 1105 | 886 | 1450 |  | 88% | 1284 | 1245 | 1267 | 1274 | 1274 | 1264 | 966 | 1400 |  | 88% | 1143 | 1118 | 1092 | 1121 | 1122 | 1118 | 924 | 1330
| 89% | 451 | 452 | 470 | 472 | 480 | 471 | 428 | 560 |  | 89% | 1036 | 1011 | 1075 | 1089 | 1119 | 1084 | 886 | 1450 |  | 89% | 1256 | 1215 | 1236 | 1246 | 1246 | 1233 | 966 | 1400 |  | 89% | 1116 | 1099 | 1072 | 1102 | 1100 | 1097 | 924 | 1330
| 90% | 446 | 448 | 467 | 469 | 476 | 466 | 428 | 560 |  | 90% | 1016 | 991 | 1051 | 1061 | 1099 | 1058 | 886 | 1450 |  | 90% | 1222 | 1188 | 1201 | 1211 | 1210 | 1198 | 966 | 1400 |  | 90% | 1102 | 1078 | 1050 | 1082 | 1076 | 1071 | 924 | 1330
| 91% | 442 | 446 | 462 | 464 | 471 | 462 | 417 | 560 |  | 91% | 987 | 970 | 1025 | 1053 | 1079 | 1049 | 851 | 1450 |  | 91% | 1194 | 1162 | 1166 | 1182 | 1173 | 1164 | 966 | 1400 |  | 91% | 1075 | 1058 | 1033 | 1059 | 1053 | 1050 | 917 | 1330
| 92% | 439 | 442 | 456 | 456 | 468 | 455 | 401 | 560 |  | 92% | 979 | 959 | 993 | 1025 | 1053 | 1028 | 784 | 1450 |  | 92% | 1157 | 1133 | 1128 | 1154 | 1162 | 1126 | 890 | 1400 |  | 92% | 1050 | 1034 | 1011 | 1034 | 1046 | 1027 | 865 | 1330
| 93% | 425 | 428 | 442 | 441 | 452 | 439 | 376 | 560 |  | 93% | 924 | 911 | 931 | 951 | 1008 | 944 | 699 | 1450 |  | 93% | 1085 | 1055 | 1053 | 1096 | 1097 | 1054 | 804 | 1400 |  | 93% | 996 | 982 | 950 | 993 | 1008 | 980 | 791 | 1330
| 94% | 425 | 428 | 442 | 441 | 452 | 439 | 376 | 560 |  | 94% | 924 | 911 | 931 | 951 | 1008 | 944 | 699 | 1450 |  | 94% | 1085 | 1055 | 1053 | 1096 | 1097 | 1054 | 804 | 1400 |  | 94% | 996 | 982 | 950 | 993 | 1008 | 980 | 791 | 1330
| 95% | 417 | 426 | 430 | 428 | 442 | 428 | 363 | 560 |  | 95% | 884 | 889 | 903 | 910 | 951 | 886 | 657 | 1450 |  | 95% | 1040 | 1020 | 1003 | 1036 | 1055 | 1013 | 762 | 1400 |  | 95% | 970 | 945 | 917 | 964 | 973 | 939 | 748 | 1330
| 96% | 407 | 417 | 421 | 423 | 428 | 426 | 332 | 560 |  | 96% | 845 | 871 | 866 | 886 | 886 | 886 | 570 | 1450 |  | 96% | 979 | 980 | 951 | 988 | 1001 | 966 | 654 | 1400 |  | 96% | 929 | 924 | 881 | 924 | 924 | 924 | 674 | 1330
| 97% | 405 | 401 | 406 | 407 | 420 | 412 | 302 | 560 |  | 97% | 805 | 812 | 828 | 832 | 871 | 845 | 506 | 1450 |  | 97% | 911 | 951 | 928 | 948 | 951 | 951 | 614 | 1400 |  | 97% | 878 | 903 | 844 | 897 | 905 | 898 | 628 | 1330
| 98% | 397 | 381 | 397 | 393 | 399 | 399 | 255 | 560 |  | 98% | 794 | 748 | 760 | 763 | 784 | 773 | 386 | 1450 |  | 98% | 898 | 874 | 863 | 880 | 880 | 880 | 452 | 1400 |  | 98% | 865 | 826 | 799 | 844 | 859 | 846 | 477 | 1330
| 99% | 374 | 361 | 354 | 354 | 372 | 369 | 255 | 560 |  | 99% | 707 | 673 | 657 | 657 | 698 | 685 | 386 | 1450 |  | 99% | 793 | 800 | 800 | 797 | 804 | 789 | 452 | 1400 |  | 99% | 772 | 765 | 752 | 752 | 791 | 752 | 477 | 1330
99% rounded |  | 370 | 360 | 350 | 350 | 370 | 360 |  |  | 99% rounded |  | 700 | 670 | 650 | 650 | 690 | 680 | 380 |  | 99% rounded |  | 790 | 800 | 800 | 790 | 800 | 780 | 450 |  | 99% rounded |  | 770 | 760 | 750 | 750 | 790 | 750 | 470

## 2021 TAS Inertia
2021 Tasmania inertia
This is the 2020 inertia projection duration curve data for the Tasmania region of the National Electricity Market. These charts are used in the 2020 System Strength and Inertia Report and the 2021 Notice of Tasmania system strength and inertia shortfalls.
| 2020-21 (MWs) | 2021-22 (MWs) | 2022-23 (MWs) | 2023-24 (MWs) | 2024-25 (MWs) | 2025-26 (MWs) | 2029-30 (MWs) | Minimum Threshold (MWs) | Secure Level (MWs)
0.1% | 8958.7066 | 8916.2721 | 8885.7426 | 8802.7168 | 8270.1188 | 8632.2708 | 8827.8546 | 3200 | 3800
1% | 8355.1148 | 8425.0723 | 8483.5124 | 8389.4548 | 8080.2548 | 8068.2948 | 8129.4523 | 3200 | 3800
3% | 7719.0148 | 7849.9099 | 7978.4098 | 7911.7348 | 7638.7924 | 7541.7948 | 7690.3148 | 3200 | 3800
4.9% | 7226.5448 | 7362.3223 | 7489.0928 | 7477.1668 | 7139.9386 | 6940.6026 | 7226.8746 | 3200 | 3800
5.9% | 6989.9768 | 7128.5408 | 7185.5231 | 7268.8068 | 6909.4548 | 6810.9048 | 7012.3028 | 3200 | 3800
6.9% | 6848.7908 | 6957.4314 | 6949.1449 | 7058.1308 | 6753.5906 | 6728.4948 | 6871.7818 | 3200 | 3800
7.9% | 6771.7968 | 6831.8091 | 6816.6986 | 6923.5988 | 6657.1066 | 6673.0748 | 6746.5916 | 3200 | 3800
8.9% | 6720.8468 | 6734.9463 | 6714.3506 | 6812.3908 | 6579.8666 | 6625.1708 | 6655.4473 | 3200 | 3800
9.9% | 6672.3608 | 6670.5266 | 6629.3803 | 6729.8488 | 6539.9013 | 6589.5806 | 6592.3356 | 3200 | 3800
10.9% | 6616.9506 | 6608.3786 | 6566.6788 | 6681.3048 | 6501.1056 | 6549.5606 | 6533.2128 | 3200 | 3800
11.9% | 6580.5366 | 6562.9866 | 6526.9571 | 6637.9148 | 6462.9566 | 6514.6924 | 6488.9298 | 3200 | 3800
12.9% | 6528.2088 | 6514.5888 | 6466.4631 | 6594.5506 | 6432.1703 | 6490.5023 | 6448.3836 | 3200 | 3800
13.9% | 6495.1966 | 6490.534 | 6408.5153 | 6542.9826 | 6401.2723 | 6452.6966 | 6400.8892 | 3200 | 3800
14.9% | 6446.0906 | 6455.3726 | 6344.7813 | 6481.0168 | 6361.0293 | 6409.5123 | 6349.2801 | 3200 | 3800
15.9% | 6389.8368 | 6408.7319 | 6300.3551 | 6431.1728 | 6316.4474 | 6358.7461 | 6299.9036 | 3200 | 3800
16.9% | 6349.4688 | 6369.1071 | 6239.6868 | 6387.0948 | 6269.3823 | 6323.9461 | 6249.8734 | 3200 | 3800
17.9% | 6302.3181 | 6321.6546 | 6190.7166 | 6348.7508 | 6245.4846 | 6285.8403 | 6207.5413 | 3200 | 3800
18.9% | 6250.5498 | 6284.7926 | 6130.9306 | 6307.4133 | 6217.3988 | 6245.4706 | 6156.5408 | 3200 | 3800
19.9% | 6198.6786 | 6244.0828 | 6080.0871 | 6285.0193 | 6181.3228 | 6207.1968 | 6120.2826 | 3200 | 3800
20.9% | 6125.2568 | 6202.0086 | 6042.0311 | 6238.4628 | 6130.3106 | 6164.4428 | 6085.9578 | 3200 | 3800
21.9% | 6049.3986 | 6126.0983 | 5968.6791 | 6180.5228 | 6058.5806 | 6096.3768 | 6035.6778 | 3200 | 3800
22.9% | 5945.7846 | 6034.4773 | 5859.3971 | 6123.7826 | 5968.7728 | 6041.7928 | 5982.0523 | 3200 | 3800
23.9% | 5809.7066 | 5947.0713 | 5728.8649 | 6059.7426 | 5903.3828 | 5985.3026 | 5920.2063 | 3200 | 3800
24.9% | 5638.1193 | 5841.6986 | 5579.0308 | 5950.8888 | 5808.4106 | 5919.0873 | 5847.4853 | 3200 | 3800
25.9% | 5467.6856 | 5664.8576 | 5455.1551 | 5838.6856 | 5656.3793 | 5824.5133 | 5775.0211 | 3200 | 3800
26.9% | 5274.0766 | 5510.5743 | 5271.7173 | 5719.4779 | 5518.3353 | 5706.1786 | 5691.7781 | 3200 | 3800
27.9% | 5071.4373 | 5333.0841 | 5120.5528 | 5564.7891 | 5371.1586 | 5594.6986 | 5605.3586 | 3200 | 3800
28.9% | 4869.8536 | 5163.8781 | 4918.5823 | 5377.7008 | 5260.8293 | 5434.0813 | 5497.8208 | 3200 | 3800
29.9% | 4711.3128 | 4975.9294 | 4710.9661 | 5234.0608 | 5113.4693 | 5300.6874 | 5373.3876 | 3200 | 3800
30.9% | 4532.6546 | 4779.6844 | 4500.9218 | 5054.0186 | 4978.5816 | 5134.8046 | 5263.7917 | 3200 | 3800
31.9% | 4373.3946 | 4563.5426 | 4344.0123 | 4870.7646 | 4783.0436 | 4962.5446 | 5139.7747 | 3200 | 3800
32.9% | 4208.5488 | 4390.4856 | 4161.1999 | 4717.7068 | 4644.5168 | 4827.3069 | 5006.0006 | 3200 | 3800
33.9% | 4108.7968 | 4226.3367 | 4008.1318 | 4541.0656 | 4468.4028 | 4721.8461 | 4888.1282 | 3200 | 3800
34.9% | 3962.6176 | 4043.4986 | 3872.1472 | 4408.4941 | 4367.0966 | 4565.2898 | 4753.7066 | 3200 | 3800
35.9% | 3827.4661 | 3903.8016 | 3836.9445 | 4300.6973 | 4200.8473 | 4534.6012 | 4604.9653 | 3200 | 3800
36.9% | 3708.2593 | 3771.2288 | 3764.2127 | 4147.8088 | 4088.1756 | 4449.8868 | 4428.2068 | 3200 | 3800
37.9% | 3631.5666 | 3689.5048 | 3677.2471 | 4003.8754 | 3965.5448 | 4323.3193 | 4333.4468 | 3200 | 3800
38.9% | 3555.2526 | 3615.2296 | 3591.9118 | 3867.1791 | 3854.3648 | 4202.4016 | 4190.1848 | 3200 | 3800
39.9% | 3469.1308 | 3527.3376 | 3552.9761 | 3766.5063 | 3796.9886 | 4088.8993 | 4023.5468 | 3200 | 3800
40.9% | 3377.3606 | 3459.6991 | 3549.5948 | 3673.0873 | 3727.1966 | 3921.9761 | 3893.9428 | 3200 | 3800
41.9% | 3365.0206 | 3422.7731 | 3549.5948 | 3561.0136 | 3639.8248 | 3833.6723 | 3771.9726 | 3200 | 3800
42.9% | 3364.6748 | 3406.7836 | 3465.0363 | 3549.5948 | 3549.5948 | 3549.5948 | 3549.5948 | 3200 | 3800
43.9% | 3364.6748 | 3419.3948 | 3486.9404 | 3549.5948 | 3549.5948 | 3549.5948 | 3549.5948 | 3200 | 3800
44.9% | 3364.6748 | 3419.3948 | 3524.5366 | 3549.5948 | 3549.5948 | 3556.8791 | 3549.5948 | 3200 | 3800
45.9% | 3364.6748 | 3419.3948 | 3549.5948 | 3549.5948 | 3549.5948 | 3635.3151 | 3557.5956 | 3200 | 3800
46.9% | 3364.6748 | 3419.3948 | 3549.5948 | 3549.5948 | 3557.7268 | 3758.6716 | 3642.6233 | 3200 | 3800
47.9% | 3350.9048 | 3371.5873 | 3425.3112 | 3524.5366 | 3549.5948 | 3549.5948 | 3549.5948 | 3200 | 3800
48.9% | 3316.7386 | 3345.1186 | 3390.0474 | 3500.4043 | 3532.135 | 3549.5948 | 3549.5948 | 3200 | 3800
49.9% | 3299.8846 | 3333.8086 | 3358.0806 | 3466.5323 | 3501.2486 | 3519.8746 | 3522.5656 | 3200 | 3800
50.9% | 3280.1426 | 3299.6966 | 3304.6766 | 3453.5667 | 3475.3186 | 3486.5529 | 3477.4716 | 3200 | 3800
51.9% | 3250.7795 | 3260.3568 | 3248.0266 | 3423.1006 | 3464.0086 | 3465.0508 | 3464.0086 | 3200 | 3800
52.9% | 3231.1396 | 3224.4606 | 3215.5706 | 3389.5923 | 3426.3641 | 3429.8966 | 3429.8966 | 3200 | 3800
53.9% | 3204.4368 | 3174.6141 | 3180.7731 | 3340.1523 | 3398.5885 | 3403.5506 | 3390.5568 | 3200 | 3800
54.9% | 3170.1208 | 3157.1445 | 3140.0223 | 3299.8423 | 3376.7826 | 3362.7891 | 3308.3623 | 3200 | 3800
55.9% | 3119.4188 | 3114.5954 | 3100.7333 | 3241.5903 | 3306.6506 | 3305.0393 | 3265.6521 | 3200 | 3800
56.9% | 3075.1958 | 3085.1573 | 3052.5722 | 3207.4543 | 3261.4636 | 3246.1073 | 3210.8693 | 3200 | 3800
57.9% | 3044.8436 | 3036.5916 | 2999.3721 | 3154.6187 | 3226.9119 | 3215.3573 | 3119.3266 | 3200 | 3800
58.9% | 3006.4293 | 2985.4943 | 2960.7793 | 3108.3543 | 3181.7212 | 3159.5511 | 3041.5963 | 3200 | 3800
59.9% | 2963.7868 | 2935.8617 | 2918.6236 | 3066.0185 | 3122.8634 | 3119.4934 | 2951.3797 | 3200 | 3800
60.9% | 2921.3522 | 2887.8386 | 2879.754 | 3003.2858 | 3078.7068 | 3074.7856 | 2890.9851 | 3200 | 3800
61.9% | 2885.6689 | 2859.9313 | 2858.4746 | 2957.313 | 3012.2305 | 3002.4475 | 2836.0536 | 3200 | 3800
62.9% | 2844.3996 | 2833.2783 | 2824.5897 | 2915.3367 | 2966.4169 | 2964.1956 | 2785.8996 | 3200 | 3800
63.9% | 2796.3836 | 2799.9011 | 2802.6574 | 2876.6606 | 2927.8048 | 2926.587 | 2727.3782 | 3200 | 3800
64.9% | 2760.8406 | 2781.7164 | 2775.5701 | 2837.1221 | 2884.9596 | 2879.034 | 2677.1069 | 3200 | 3800
65.9% | 2727.1406 | 2744.6442 | 2741.2288 | 2800.3476 | 2834.1688 | 2827.7707 | 2621.4786 | 3200 | 3800
66.9% | 2699.2589 | 2706.2374 | 2707.7996 | 2772.0537 | 2792.9736 | 2793.518 | 2570.7324 | 3200 | 3800
67.9% | 2661.5676 | 2673.7828 | 2672.3157 | 2736.0756 | 2747.0973 | 2754.5189 | 2522.3173 | 3200 | 3800
68.9% | 2636.0936 | 2643.5237 | 2638.8848 | 2695.3136 | 2694.043 | 2707.2211 | 2498.4036 | 3200 | 3800
69.9% | 2617.4858 | 2608.8326 | 2600.8633 | 2661.0336 | 2659.1606 | 2668.1242 | 2447.9366 | 3200 | 3800
70.9% | 2587.8546 | 2571.9966 | 2552.6486 | 2620.5123 | 2631.6723 | 2625.6756 | 2410.7206 | 3200 | 3800
71.9% | 2550.3441 | 2539.9516 | 2520.5173 | 2584.1917 | 2600.5423 | 2582.0479 | 2353.0428 | 3200 | 3800
72.9% | 2509.0911 | 2515.6727 | 2511.0081 | 2539.6154 | 2557.2198 | 2534.1218 | 2310.9868 | 3200 | 3800
73.9% | 2466.7881 | 2483.4112 | 2476.0873 | 2519.2513 | 2521.0211 | 2518.6736 | 2251.7337 | 3200 | 3800
74.9% | 2434.0873 | 2446.0741 | 2443.8541 | 2492.4366 | 2492.4366 | 2493.8653 | 2190.623 | 3200 | 3800
75.9% | 2382.8648 | 2410.3291 | 2404.8861 | 2455.5693 | 2460.2765 | 2455.7395 | 2139.9536 | 3200 | 3800
76.9% | 2360.5846 | 2389.2431 | 2376.2541 | 2410.4903 | 2428.4307 | 2424.7499 | 2089.7143 | 3200 | 3800
77.9% | 2335.1876 | 2362.7114 | 2347.1449 | 2374.5937 | 2383.693 | 2376.8867 | 2079.8539 | 3200 | 3800
78.9% | 2309.6833 | 2338.1571 | 2311.6575 | 2338.7756 | 2346.2046 | 2339.948 | 2041.3374 | 3200 | 3800
79.9% | 2281.4561 | 2304.7071 | 2269.9181 | 2304.6521 | 2322.523 | 2309.9238 | 1985.687 | 3200 | 3800
80.9% | 2239.6503 | 2281.3137 | 2240.4442 | 2262.6701 | 2281.0035 | 2269.4277 | 1933.6269 | 3200 | 3800
81.9% | 2191.2201 | 2248.9272 | 2200.3686 | 2225.5077 | 2237.9981 | 2222.973 | 1876.255 | 3200 | 3800
82.9% | 2152.2323 | 2212.482 | 2161.9307 | 2187.7494 | 2200.8797 | 2187.3914 | 1816.1172 | 3200 | 3800
83.9% | 2110.2893 | 2176.144 | 2100.8124 | 2154.7257 | 2163.6827 | 2148.3019 | 1740.9599 | 3200 | 3800
84.9% | 2037.5555 | 2131.6955 | 2060.6004 | 2095.5109 | 2117.6414 | 2096.5387 | 1684.2975 | 3200 | 3800
85.9% | 2027.1886 | 2088.9301 | 2012.7781 | 2066.5315 | 2086.3898 | 2062.8843 | 1608.601 | 3200 | 3800
86.9% | 1992.3539 | 2038.2761 | 1969.2612 | 2021.6215 | 2052.0975 | 2032.0712 | 1543.789 | 3200 | 3800
87.9% | 1944.4556 | 1980.2314 | 1915.7017 | 1975.2919 | 2048.615 | 1980.1072 | 1483.419 | 3200 | 3800
88.9% | 1898.9137 | 1951.1641 | 1873.6154 | 1930.8446 | 2009.897 | 1927.281 | 1477.415 | 3200 | 3800
89.9% | 1852.4754 | 1912.3422 | 1834.704 | 1877.3699 | 1960.9032 | 1874.585 | 1477.415 | 3200 | 3800
90.9% | 1783.5258 | 1859.0241 | 1777.161 | 1828.4905 | 1912.3392 | 1807.0056 | 1461.449 | 3200 | 3800
91.9% | 1746.4957 | 1803.6514 | 1718.2257 | 1762.5482 | 1856.915 | 1735.1317 | 1359.595 | 3200 | 3800
92.9% | 1701.253 | 1741.0586 | 1657.9686 | 1723.002 | 1787.0034 | 1682.627 | 1317.821 | 3200 | 3800
93.9% | 1638.5787 | 1684.6035 | 1579.2907 | 1642.7049 | 1733.1095 | 1608.475 | 1229.0838 | 3200 | 3800
94.9% | 1594.5619 | 1605.847 | 1509.5093 | 1587.2704 | 1641.4721 | 1523.9034 | 1173.1962 | 3200 | 3800
95.9% | 1502.4462 | 1549.5559 | 1431.7797 | 1487.8792 | 1544.896 | 1481.2095 | 1087.4383 | 3200 | 3800
96.9% | 1403.4917 | 1477.956 | 1379.2515 | 1431.0087 | 1467.2307 | 1431.0087 | 934.7682 | 3200 | 3800
97.9% | 1371.7237 | 1359.553 | 1282.6676 | 1333.04 | 1348.633 | 1310.9247 | 801.62 | 3200 | 3800
98.9% | 1183.67 | 1220.207 | 1178.4847 | 1183.5087 | 1238.987 | 1181.0515 | 788.6 | 3200 | 3800

## 2019 TAS System strength
2019 Tasmania system strength
This is the 2019 fault level projection duration curve data for each fault level node in the Tasmania region of the National Electricity Market. These charts are used in the 2019 Notice of inertia and fault level shortfalls in Tasmania.
| 2019 Waddamana 220kV Fault Levels | [8 empty] | 2019 Risdon 220kV Fault Levels | [8 empty] | 2019 Burnie 220kV Fault Levels | [8 empty] | 2019 George Town 220kV Fault Levels
| 2019-20 Fault Levels (MVA) | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | Pre-Contingent Requirement |  | 2019-20 Fault Levels (MVA) | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | Pre-Contingent Requirement |  | 2019-20 Fault Levels (MVA) | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | Pre-Contingent Requirement |  | 2019-20 Fault Levels (MVA) | 2020-21 Fault Levels (MVA) | 2021-22 Fault Levels (MVA) | 2022-23 Fault Levels (MVA) | 2023-24 Fault Levels (MVA) | 2024-25 Fault Levels (MVA) | 2025-26 Fault Levels (MVA) | Pre-Contingent Requirement
0% | 3412 | 3415 | 3444 | 3425 | 3425 | 3433 | 3464 | 1400 | 0% | 2402 | 2406 | 2413 | 2408 | 2410 | 2404 | 2402 | 1330 | 0% | 1207 | 1202 | 1195 | 1202 | 1207 | 1196 | 1197 | 750 | 0% | 3407 | 3110 | 3086 | 3384 | 3260 | 3086 | 3106 | 1450
1% | 3303 | 3313 | 3320.81 | 3326 | 3330 | 3323.81 | 3318 | 1400 | 1% | 2373 | 2373 | 2376 | 2375 | 2380 | 2376 | 2375 | 1330 | 1% | 1180 | 1171 | 1173 | 1175 | 1176 | 1173 | 1169 | 750 | 1% | 2958.81 | 2866.81 | 2913.81 | 2961 | 2961 | 2948.81 | 2875.81 | 1450
2% | 3273 | 3281 | 3287 | 3289 | 3287 | 3286 | 3286 | 1400 | 2% | 2360 | 2363 | 2363 | 2364.62 | 2366 | 2364 | 2366 | 1330 | 2% | 1174 | 1163 | 1165 | 1165 | 1166 | 1165 | 1163 | 750 | 2% | 2865.62 | 2791 | 2826 | 2863 | 2876 | 2846 | 2800.62 | 1450
3% | 3245 | 3261 | 3263 | 3265 | 3265 | 3263 | 3264 | 1400 | 3% | 2352 | 2354 | 2356 | 2357 | 2358 | 2358 | 2356 | 1330 | 3% | 1167.43 | 1154 | 1157 | 1156 | 1159 | 1158 | 1157 | 750 | 3% | 2813.43 | 2750 | 2767 | 2810.43 | 2811.43 | 2795 | 2756 | 1450
4% | 3225 | 3245 | 3245 | 3246.24 | 3245.24 | 3245 | 3245 | 1400 | 4% | 2345 | 2348 | 2349 | 2351 | 2350 | 2352 | 2349 | 1330 | 4% | 1159.24 | 1149 | 1151 | 1151 | 1153 | 1152 | 1152 | 750 | 4% | 2774 | 2721 | 2744 | 2762 | 2756.24 | 2758 | 2740 | 1450
5% | 3209 | 3229 | 3227 | 3233 | 3227 | 3233 | 3226 | 1400 | 5% | 2339 | 2343 | 2343 | 2345 | 2345 | 2347 | 2343 | 1330 | 5% | 1154 | 1143 | 1146 | 1146 | 1148 | 1148 | 1148 | 750 | 5% | 2744 | 2700 | 2718 | 2736.05 | 2738 | 2737 | 2720 | 1450
6% | 3195 | 3212 | 3212 | 3218 | 3212 | 3220 | 3211 | 1400 | 6% | 2333 | 2338 | 2337 | 2339 | 2340 | 2341 | 2339 | 1330 | 6% | 1149 | 1140 | 1142 | 1142 | 1143 | 1144 | 1143 | 750 | 6% | 2714 | 2680 | 2690 | 2707 | 2711.86 | 2718 | 2695.86 | 1450
7% | 3179 | 3197 | 3198 | 3203 | 3197 | 3208 | 3196 | 1400 | 7% | 2328.67 | 2333 | 2332 | 2334 | 2335 | 2336.67 | 2334 | 1330 | 7% | 1144 | 1136 | 1138 | 1139 | 1141 | 1141 | 1141 | 750 | 7% | 2696 | 2665 | 2671.67 | 2689 | 2691 | 2695 | 2677 | 1450
8% | 3166 | 3185 | 3187 | 3187.48 | 3186 | 3196 | 3185 | 1400 | 8% | 2323 | 2328 | 2327 | 2328 | 2331 | 2331 | 2330 | 1330 | 8% | 1141 | 1132 | 1134 | 1135 | 1138 | 1138 | 1138 | 750 | 8% | 2675 | 2649 | 2659.48 | 2668 | 2674 | 2679 | 2664 | 1450
9% | 3154 | 3175 | 3175.29 | 3175 | 3173 | 3183 | 3174 | 1400 | 9% | 2317 | 2324 | 2323 | 2323 | 2326 | 2326 | 2324 | 1330 | 9% | 1137 | 1129 | 1131 | 1131 | 1134 | 1135 | 1135 | 750 | 9% | 2657 | 2633 | 2641 | 2655 | 2662 | 2665 | 2651 | 1450
10% | 3139 | 3164 | 3166 | 3164 | 3161 | 3173 | 3165 | 1400 | 10% | 2312 | 2320 | 2319 | 2319 | 2321 | 2322 | 2320 | 1330 | 10% | 1132 | 1126 | 1127 | 1128 | 1131 | 1132 | 1131 | 750 | 10% | 2636 | 2621 | 2628 | 2637 | 2643 | 2651 | 2640 | 1450
11% | 3126 | 3152.91 | 3155 | 3153 | 3151 | 3162 | 3155 | 1400 | 11% | 2308 | 2316 | 2315 | 2315 | 2317 | 2318 | 2316 | 1330 | 11% | 1127 | 1123 | 1124 | 1125 | 1127 | 1130 | 1128 | 750 | 11% | 2620 | 2608 | 2612 | 2626 | 2629 | 2638 | 2627 | 1450
12% | 3115 | 3142 | 3142 | 3142 | 3141 | 3153 | 3146 | 1400 | 12% | 2302 | 2312 | 2311 | 2312 | 2314 | 2314 | 2312 | 1330 | 12% | 1123 | 1120 | 1121 | 1121 | 1124 | 1126.72 | 1126 | 750 | 12% | 2604 | 2595 | 2595 | 2610 | 2616 | 2625 | 2613 | 1450
13% | 3100.53 | 3132 | 3132 | 3132 | 3133 | 3142 | 3135 | 1400 | 13% | 2297 | 2308 | 2306 | 2308 | 2310 | 2309 | 2309 | 1330 | 13% | 1118 | 1116 | 1117 | 1118 | 1121 | 1123 | 1123 | 750 | 13% | 2588 | 2583 | 2582 | 2597 | 2601 | 2613 | 2602.53 | 1450
14% | 3088 | 3122 | 3120 | 3123 | 3123 | 3133 | 3126 | 1400 | 14% | 2292 | 2304 | 2302 | 2303 | 2305 | 2304 | 2306 | 1330 | 14% | 1113 | 1113 | 1113 | 1115 | 1117 | 1120 | 1120 | 750 | 14% | 2570 | 2573 | 2567 | 2586 | 2586 | 2601 | 2588 | 1450
15% | 3071 | 3113 | 3109 | 3113 | 3114 | 3123 | 3116 | 1400 | 15% | 2286 | 2299 | 2298 | 2299 | 2301 | 2300 | 2301 | 1330 | 15% | 1107 | 1110 | 1110 | 1112 | 1114 | 1117 | 1116 | 750 | 15% | 2553 | 2563 | 2555 | 2575 | 2575 | 2592 | 2578 | 1450
16% | 3058 | 3103 | 3099.96 | 3102 | 3102 | 3111 | 3108 | 1400 | 16% | 2281 | 2296 | 2294 | 2295 | 2296 | 2295 | 2298 | 1330 | 16% | 1102 | 1107 | 1106 | 1108 | 1110 | 1113 | 1113 | 750 | 16% | 2535 | 2552 | 2539 | 2563 | 2564 | 2580 | 2568 | 1450
17% | 3045 | 3092 | 3088 | 3090 | 3094 | 3100 | 3099 | 1400 | 17% | 2276 | 2291 | 2289 | 2290 | 2292 | 2290 | 2294 | 1330 | 17% | 1095 | 1103 | 1102 | 1104 | 1106 | 1109 | 1109 | 750 | 17% | 2522 | 2538 | 2525 | 2550 | 2552 | 2569 | 2557 | 1450
18% | 3032 | 3080 | 3074 | 3079 | 3084 | 3088 | 3089 | 1400 | 18% | 2270.58 | 2286 | 2284 | 2286 | 2287 | 2284 | 2290 | 1330 | 18% | 1090 | 1099 | 1099 | 1100 | 1102 | 1104 | 1106 | 750 | 18% | 2506.58 | 2525 | 2511 | 2540 | 2539 | 2555 | 2546 | 1450
19% | 3019 | 3068 | 3060.39 | 3068 | 3073 | 3073 | 3077 | 1400 | 19% | 2265 | 2281 | 2279 | 2281 | 2284 | 2278 | 2285 | 1330 | 19% | 1086 | 1095 | 1095 | 1097 | 1098 | 1099 | 1102 | 750 | 19% | 2489 | 2512.39 | 2501 | 2528 | 2527 | 2543 | 2535 | 1450
20% | 3005 | 3055 | 3048 | 3056 | 3062 | 3061 | 3068 | 1400 | 20% | 2260 | 2277 | 2275 | 2277 | 2279 | 2274 | 2281 | 1330 | 20% | 1081 | 1091 | 1091 | 1093 | 1094 | 1095 | 1098 | 750 | 20% | 2471 | 2494 | 2487 | 2516 | 2517 | 2529 | 2521 | 1450
21% | 2991 | 3043 | 3035 | 3043 | 3052 | 3049 | 3058 | 1400 | 21% | 2254 | 2272 | 2271 | 2273 | 2274 | 2269 | 2277 | 1330 | 21% | 1077 | 1088 | 1087 | 1090 | 1090 | 1091 | 1094 | 750 | 21% | 2453 | 2481 | 2473 | 2503 | 2505 | 2513 | 2510 | 1450
22% | 2977 | 3031 | 3023 | 3031 | 3041 | 3034 | 3046 | 1400 | 22% | 2249 | 2268 | 2266 | 2268 | 2270 | 2263 | 2273 | 1330 | 22% | 1073 | 1084 | 1082 | 1086 | 1087 | 1087 | 1089 | 750 | 22% | 2437 | 2466 | 2460 | 2488.82 | 2493 | 2501 | 2499 | 1450
23% | 2963 | 3018 | 3010 | 3019 | 3027 | 3021.63 | 3036 | 1400 | 23% | 2243 | 2264 | 2261 | 2263 | 2266 | 2259 | 2269 | 1330 | 23% | 1069 | 1080 | 1079 | 1083 | 1084 | 1083 | 1085 | 750 | 23% | 2420 | 2455 | 2448 | 2477 | 2483 | 2489 | 2487 | 1450
24% | 2948 | 3005 | 2996 | 3008 | 3015 | 3007.44 | 3024 | 1400 | 24% | 2238 | 2259 | 2256 | 2258 | 2261 | 2253 | 2263 | 1330 | 24% | 1065 | 1076 | 1075 | 1080 | 1080 | 1080 | 1081 | 750 | 24% | 2403 | 2443 | 2436 | 2462.44 | 2470 | 2475 | 2475 | 1450
25% | 2931 | 2992 | 2980 | 2995 | 3000 | 2991 | 3013 | 1400 | 25% | 2233 | 2254 | 2249 | 2253 | 2255 | 2247 | 2258 | 1330 | 25% | 1061 | 1073 | 1072 | 1077 | 1077 | 1077 | 1078 | 750 | 25% | 2386 | 2430 | 2423 | 2450 | 2457 | 2458 | 2461 | 1450
26% | 2913 | 2979 | 2967 | 2981 | 2987 | 2977 | 3001 | 1400 | 26% | 2226.06 | 2249 | 2243.06 | 2247 | 2250 | 2240 | 2253 | 1330 | 26% | 1057 | 1070 | 1068 | 1074 | 1073 | 1074 | 1075 | 750 | 26% | 2368 | 2415 | 2409 | 2437 | 2446 | 2446 | 2448 | 1450
27% | 2895 | 2965 | 2949.87 | 2967 | 2973 | 2959.87 | 2987 | 1400 | 27% | 2220 | 2243 | 2237 | 2240.87 | 2244 | 2233 | 2247 | 1330 | 27% | 1052 | 1067 | 1065 | 1071 | 1070 | 1071 | 1072 | 750 | 27% | 2352 | 2401 | 2393 | 2423 | 2435 | 2432 | 2437 | 1450
28% | 2878.68 | 2949 | 2934 | 2952 | 2958.68 | 2940.68 | 2972 | 1400 | 28% | 2213 | 2237 | 2230 | 2234 | 2238 | 2226 | 2242 | 1330 | 28% | 1048 | 1064 | 1061 | 1069 | 1067 | 1067.68 | 1069 | 750 | 28% | 2335 | 2386 | 2377 | 2410 | 2421 | 2418 | 2426 | 1450
29% | 2862 | 2935 | 2914.49 | 2934 | 2943 | 2922 | 2956 | 1400 | 29% | 2206 | 2231 | 2223 | 2228 | 2231 | 2219 | 2236 | 1330 | 29% | 1044 | 1060 | 1057 | 1065 | 1064 | 1065 | 1066 | 750 | 29% | 2320 | 2370 | 2363 | 2397 | 2406.49 | 2403 | 2411 | 1450
30% | 2844 | 2917 | 2897 | 2917 | 2926 | 2899.3 | 2941 | 1400 | 30% | 2198 | 2225 | 2216 | 2221 | 2224 | 2212 | 2229 | 1330 | 30% | 1040 | 1055 | 1053 | 1062 | 1061 | 1061 | 1062 | 750 | 30% | 2302 | 2355 | 2348 | 2384 | 2389 | 2388.3 | 2396 | 1450
31% | 2826 | 2901 | 2879 | 2901 | 2910 | 2882 | 2925 | 1400 | 31% | 2189 | 2218 | 2209 | 2214 | 2218 | 2204 | 2222 | 1330 | 31% | 1036 | 1051 | 1050 | 1058 | 1058 | 1058 | 1058 | 750 | 31% | 2286 | 2340 | 2330.11 | 2368 | 2373 | 2372 | 2380 | 1450
32% | 2803 | 2882.92 | 2859 | 2885 | 2894 | 2864 | 2905 | 1400 | 32% | 2181 | 2210 | 2201 | 2206 | 2211 | 2197.92 | 2215 | 1330 | 32% | 1032 | 1047 | 1047 | 1055.92 | 1055 | 1054 | 1055 | 750 | 32% | 2270 | 2326 | 2315.92 | 2355 | 2355 | 2355 | 2365.92 | 1450
33% | 2779 | 2864 | 2839.73 | 2867 | 2875 | 2847 | 2888 | 1400 | 33% | 2172 | 2202 | 2192 | 2198 | 2203 | 2191 | 2207 | 1330 | 33% | 1028 | 1043 | 1043 | 1052 | 1051 | 1050 | 1052 | 750 | 33% | 2250.73 | 2306 | 2301 | 2339 | 2337 | 2340 | 2349 | 1450
34% | 2757 | 2844 | 2819 | 2847 | 2854 | 2830 | 2867 | 1400 | 34% | 2161 | 2193 | 2183 | 2189 | 2194 | 2182 | 2199 | 1330 | 34% | 1023 | 1040 | 1040 | 1049 | 1047 | 1047 | 1048 | 750 | 34% | 2232 | 2290 | 2284 | 2325 | 2320 | 2323 | 2331 | 1450
35% | 2734 | 2817.35 | 2799 | 2825 | 2833.35 | 2807 | 2844 | 1400 | 35% | 2150 | 2183 | 2173.35 | 2181 | 2185 | 2173 | 2190 | 1330 | 35% | 1018 | 1036 | 1036 | 1044 | 1044 | 1044 | 1044 | 750 | 35% | 2211 | 2274 | 2268 | 2309 | 2305 | 2306 | 2312 | 1450
36% | 2710 | 2795 | 2773 | 2802 | 2811 | 2784.16 | 2819.16 | 1400 | 36% | 2140 | 2173 | 2162 | 2172 | 2176 | 2164 | 2182 | 1330 | 36% | 1013 | 1032 | 1032 | 1040 | 1040 | 1039.16 | 1040 | 750 | 36% | 2195 | 2256 | 2254 | 2293 | 2291 | 2292 | 2292 | 1450
37% | 2689 | 2768 | 2748 | 2776 | 2788 | 2761 | 2795.97 | 1400 | 37% | 2127 | 2162 | 2151 | 2163 | 2167 | 2153 | 2171 | 1330 | 37% | 1008 | 1029 | 1029 | 1036 | 1036 | 1036 | 1037 | 750 | 37% | 2177 | 2240 | 2238 | 2277 | 2275 | 2275 | 2275 | 1450
38% | 2663 | 2743 | 2721 | 2752 | 2765 | 2736 | 2770.78 | 1400 | 38% | 2114 | 2152 | 2138 | 2152 | 2156 | 2143 | 2160.78 | 1330 | 38% | 1003.78 | 1024 | 1025 | 1033 | 1032 | 1032 | 1032 | 750 | 38% | 2161 | 2225 | 2222 | 2260 | 2260 | 2258 | 2260 | 1450
39% | 2637 | 2716 | 2694 | 2725 | 2739 | 2711 | 2740.59 | 1400 | 39% | 2101 | 2139.59 | 2126 | 2140 | 2143 | 2131 | 2149 | 1330 | 39% | 999 | 1020 | 1021 | 1028 | 1027 | 1027 | 1029 | 750 | 39% | 2143.59 | 2207 | 2205 | 2243 | 2239 | 2243 | 2243 | 1450
40% | 2612 | 2689 | 2667 | 2701 | 2708.4 | 2687 | 2710 | 1400 | 40% | 2085 | 2126 | 2114 | 2128 | 2131 | 2119 | 2135 | 1330 | 40% | 994 | 1015 | 1017 | 1024 | 1023 | 1024 | 1023 | 750 | 40% | 2124 | 2189 | 2188 | 2223 | 2218 | 2227 | 2225 | 1450
41% | 2583 | 2665 | 2640 | 2674 | 2684 | 2661 | 2686 | 1400 | 41% | 2072 | 2110 | 2097 | 2113 | 2116.21 | 2103 | 2121.21 | 1330 | 41% | 989 | 1012 | 1013 | 1020 | 1018.21 | 1019 | 1019 | 750 | 41% | 2109 | 2172 | 2174 | 2207 | 2203 | 2211 | 2205.21 | 1450
42% | 2556 | 2636.02 | 2616 | 2642.02 | 2655.02 | 2632 | 2658.02 | 1400 | 42% | 2059 | 2096 | 2084 | 2098 | 2102 | 2087 | 2104 | 1330 | 42% | 984 | 1008 | 1009 | 1015 | 1014 | 1014 | 1014 | 750 | 42% | 2090 | 2154 | 2159 | 2189 | 2186 | 2194 | 2188.02 | 1450
43% | 2529 | 2605 | 2590 | 2616.83 | 2627 | 2608 | 2626 | 1400 | 43% | 2044 | 2077 | 2068 | 2082.83 | 2085 | 2070 | 2084.83 | 1330 | 43% | 977 | 1004 | 1004 | 1011 | 1009 | 1010 | 1009 | 750 | 43% | 2073 | 2136 | 2141.83 | 2174 | 2169 | 2179 | 2175 | 1450
44% | 2501.64 | 2573 | 2560 | 2588 | 2600 | 2582.64 | 2595 | 1400 | 44% | 2027 | 2057 | 2051 | 2066 | 2066 | 2055 | 2063 | 1330 | 44% | 973 | 998 | 1000 | 1006 | 1004 | 1004 | 1005 | 750 | 44% | 2055 | 2116 | 2123 | 2156 | 2152 | 2162 | 2157 | 1450
45% | 2474 | 2538 | 2533.45 | 2559 | 2573 | 2554 | 2562 | 1400 | 45% | 2013 | 2035 | 2033 | 2045 | 2049 | 2040 | 2044 | 1330 | 45% | 966.45 | 994 | 995 | 1002 | 999 | 999 | 1000 | 750 | 45% | 2034.45 | 2102 | 2107 | 2137 | 2133 | 2147 | 2137 | 1450
46% | 2447 | 2506 | 2507 | 2531 | 2540 | 2527.26 | 2536 | 1400 | 46% | 1997 | 2013 | 2013 | 2025 | 2031 | 2021 | 2026 | 1330 | 46% | 960 | 989 | 989 | 995 | 994 | 994 | 994 | 750 | 46% | 2016 | 2088 | 2090 | 2118 | 2115 | 2126 | 2120 | 1450
47% | 2415 | 2477 | 2479 | 2498 | 2513 | 2502 | 2504 | 1400 | 47% | 1979 | 1989.07 | 1994 | 2007 | 2012 | 2001.07 | 2005 | 1330 | 47% | 955 | 983 | 985 | 989 | 988 | 988 | 989 | 750 | 47% | 1995 | 2070 | 2075 | 2100 | 2100 | 2111 | 2098 | 1450
48% | 2389 | 2449 | 2454 | 2469 | 2481 | 2473 | 2473 | 1400 | 48% | 1961.88 | 1966 | 1976 | 1987 | 1995 | 1985 | 1984 | 1330 | 48% | 949 | 979 | 980 | 983 | 982 | 983 | 983 | 750 | 48% | 1976 | 2050 | 2057 | 2081 | 2080 | 2091 | 2080 | 1450
49% | 2363 | 2420 | 2426 | 2442 | 2453.69 | 2442 | 2442.69 | 1400 | 49% | 1946 | 1950 | 1957 | 1970 | 1973 | 1968 | 1967.69 | 1330 | 49% | 943 | 973 | 975 | 978 | 977 | 977 | 976 | 750 | 49% | 1956 | 2032.69 | 2035 | 2060 | 2061 | 2075 | 2059 | 1450
50% | 2337 | 2390 | 2399 | 2414 | 2419 | 2417 | 2416 | 1400 | 50% | 1928 | 1932 | 1939 | 1953 | 1953 | 1951 | 1948 | 1330 | 50% | 938 | 967 | 970 | 971 | 972 | 971 | 971 | 750 | 50% | 1939 | 2013 | 2016 | 2034.5 | 2042.5 | 2054 | 2036 | 1450
51% | 2310 | 2362 | 2375 | 2387 | 2392 | 2392 | 2387 | 1400 | 51% | 1914 | 1916 | 1923 | 1936.31 | 1934 | 1934 | 1932 | 1330 | 51% | 933 | 962 | 965 | 966 | 966 | 966 | 965 | 750 | 51% | 1921 | 1995.31 | 2000 | 2015 | 2024 | 2038 | 2016 | 1450
52% | 2283 | 2338.12 | 2348 | 2360 | 2362 | 2367.12 | 2360 | 1400 | 52% | 1898 | 1902.12 | 1908 | 1922 | 1918 | 1920 | 1916 | 1330 | 52% | 927 | 957 | 959 | 959 | 960 | 960 | 959 | 750 | 52% | 1902.12 | 1977 | 1982 | 1993 | 2007 | 2017 | 1993 | 1450
53% | 2260 | 2310 | 2322 | 2334 | 2333 | 2346 | 2336 | 1400 | 53% | 1883 | 1889 | 1894 | 1906 | 1900 | 1904 | 1901 | 1330 | 53% | 922 | 952 | 954 | 953 | 954 | 954 | 953 | 750 | 53% | 1884 | 1958 | 1964 | 1972 | 1987 | 1996 | 1974 | 1450
54% | 2240 | 2285 | 2299 | 2314 | 2308 | 2320 | 2310.74 | 1400 | 54% | 1869.74 | 1875 | 1880 | 1891 | 1884 | 1891 | 1886 | 1330 | 54% | 917 | 946 | 947 | 947 | 948 | 948 | 946 | 750 | 54% | 1867 | 1937 | 1945 | 1954 | 1970 | 1977 | 1953 | 1450
55% | 2220.55 | 2262 | 2277 | 2293.55 | 2283 | 2297 | 2288 | 1400 | 55% | 1858 | 1860 | 1866 | 1878 | 1869.55 | 1880 | 1874 | 1330 | 55% | 912 | 941 | 941 | 941 | 942 | 941 | 939 | 750 | 55% | 1850 | 1916 | 1925 | 1933 | 1950 | 1958 | 1931 | 1450
56% | 2203 | 2243 | 2254 | 2271 | 2260 | 2277 | 2267 | 1400 | 56% | 1847 | 1848 | 1854 | 1863.36 | 1857 | 1868 | 1858 | 1330 | 56% | 907 | 934 | 935 | 935 | 936 | 936 | 932 | 750 | 56% | 1835 | 1897.36 | 1907 | 1913 | 1931 | 1936 | 1910.36 | 1450
57% | 2183 | 2223 | 2235.17 | 2250 | 2242 | 2254 | 2244 | 1400 | 57% | 1836 | 1837 | 1843.17 | 1851 | 1845 | 1855 | 1848 | 1330 | 57% | 903 | 928 | 929 | 928 | 930 | 929 | 925.17 | 750 | 57% | 1819 | 1878 | 1891 | 1895 | 1914 | 1921 | 1892 | 1450
58% | 2165 | 2204 | 2216 | 2229 | 2221 | 2235 | 2223 | 1400 | 58% | 1826 | 1825 | 1833 | 1839 | 1834 | 1844.98 | 1837 | 1330 | 58% | 898 | 923 | 923 | 922 | 924 | 923 | 920 | 750 | 58% | 1805 | 1860 | 1872 | 1878 | 1898 | 1902.98 | 1873 | 1450
59% | 2148 | 2187 | 2198 | 2209.79 | 2203 | 2215 | 2204 | 1400 | 59% | 1816 | 1816 | 1823 | 1828.79 | 1822 | 1835 | 1828 | 1330 | 59% | 895 | 917 | 918 | 916 | 919 | 918 | 914 | 750 | 59% | 1789 | 1840.79 | 1855 | 1859 | 1881 | 1885 | 1855 | 1450
60% | 2133 | 2167 | 2179 | 2187 | 2186 | 2196 | 2183 | 1400 | 60% | 1806 | 1805 | 1813 | 1817 | 1811.6 | 1825 | 1819 | 1330 | 60% | 890 | 912 | 913 | 911 | 914 | 913 | 908 | 750 | 60% | 1774 | 1824 | 1836 | 1843 | 1863 | 1868 | 1835.6 | 1450
61% | 2117 | 2149 | 2158 | 2167 | 2168 | 2179 | 2163 | 1400 | 61% | 1797 | 1796 | 1804 | 1807 | 1801 | 1815 | 1809 | 1330 | 61% | 886 | 906 | 909 | 905 | 909 | 908 | 902.41 | 750 | 61% | 1761 | 1807 | 1816.41 | 1824 | 1843 | 1849 | 1817 | 1450
62% | 2102.22 | 2130 | 2141 | 2150 | 2149 | 2160 | 2145 | 1400 | 62% | 1789 | 1786 | 1794 | 1797 | 1791 | 1806 | 1799 | 1330 | 62% | 881.22 | 900 | 904 | 900 | 903 | 903 | 897 | 750 | 62% | 1747.22 | 1789 | 1799 | 1807 | 1826 | 1835 | 1800 | 1450
63% | 2089 | 2116 | 2124.03 | 2130 | 2131.03 | 2147 | 2128 | 1400 | 63% | 1780 | 1777 | 1783 | 1788 | 1781.03 | 1797 | 1789 | 1330 | 63% | 877 | 894 | 898 | 894 | 899 | 898 | 892 | 750 | 63% | 1735 | 1772 | 1783 | 1790 | 1807 | 1819 | 1782 | 1450
64% | 2077 | 2102 | 2106 | 2111.84 | 2114 | 2132 | 2111 | 1400 | 64% | 1773 | 1769 | 1775 | 1778 | 1772 | 1788 | 1779 | 1330 | 64% | 873 | 888 | 893 | 889 | 893 | 894 | 886 | 750 | 64% | 1720 | 1755 | 1763 | 1774 | 1787 | 1802 | 1763 | 1450
65% | 2062 | 2089 | 2091 | 2096 | 2098.65 | 2118 | 2097 | 1400 | 65% | 1764.65 | 1761 | 1767 | 1770 | 1764 | 1779 | 1770 | 1330 | 65% | 869 | 883 | 889 | 884 | 888 | 889 | 881 | 750 | 65% | 1708.65 | 1739 | 1746 | 1757 | 1769 | 1785 | 1747 | 1450
66% | 2049 | 2074 | 2076 | 2079 | 2082 | 2104 | 2079 | 1400 | 66% | 1758 | 1753 | 1758 | 1762 | 1756 | 1772 | 1761 | 1330 | 66% | 865 | 877 | 883 | 879 | 883 | 884 | 876 | 750 | 66% | 1694 | 1727 | 1732 | 1741 | 1750.46 | 1768 | 1731 | 1450
67% | 2035 | 2059 | 2061 | 2064 | 2066 | 2089 | 2064 | 1400 | 67% | 1750 | 1746 | 1751 | 1753 | 1748 | 1764 | 1753 | 1330 | 67% | 861 | 873 | 879 | 875 | 878 | 880 | 872 | 750 | 67% | 1682 | 1712.27 | 1715 | 1725 | 1735 | 1752 | 1716 | 1450
68% | 2019 | 2044 | 2047 | 2051 | 2050 | 2075 | 2050.08 | 1400 | 68% | 1743 | 1737 | 1743 | 1744 | 1740 | 1757 | 1744 | 1330 | 68% | 857 | 869 | 873 | 870 | 873 | 875 | 867 | 750 | 68% | 1668 | 1699 | 1699 | 1708 | 1719.08 | 1741 | 1701 | 1450
69% | 2007.89 | 2031 | 2033 | 2035 | 2035 | 2061 | 2036 | 1400 | 69% | 1736 | 1730 | 1735 | 1736 | 1733 | 1749 | 1737 | 1330 | 69% | 854 | 864 | 868 | 865 | 869 | 871 | 863 | 750 | 69% | 1657 | 1686 | 1682 | 1690 | 1706 | 1727 | 1687.89 | 1450
70% | 1995 | 2016 | 2020 | 2021 | 2020 | 2047 | 2022 | 1400 | 70% | 1729 | 1722 | 1726 | 1728 | 1725 | 1742 | 1728 | 1330 | 70% | 849 | 860 | 863 | 860 | 863 | 867 | 858 | 750 | 70% | 1645 | 1672 | 1668 | 1674 | 1691 | 1713 | 1669.7 | 1450
71% | 1982 | 2001 | 2006 | 2007 | 2007 | 2033 | 2007 | 1400 | 71% | 1720 | 1713 | 1718 | 1719 | 1718 | 1734 | 1720 | 1330 | 71% | 846 | 856 | 858 | 855 | 858 | 863 | 854 | 750 | 71% | 1632 | 1658 | 1657 | 1662 | 1676 | 1699 | 1655 | 1450
72% | 1968 | 1987 | 1994 | 1992 | 1994 | 2019 | 1991 | 1400 | 72% | 1713 | 1707 | 1710 | 1711 | 1710 | 1727 | 1711 | 1330 | 72% | 842 | 851 | 853 | 850 | 853 | 859 | 849 | 750 | 72% | 1621 | 1645 | 1642 | 1647 | 1662 | 1685 | 1642 | 1450
73% | 1955 | 1975 | 1980 | 1976 | 1980 | 2007 | 1976 | 1400 | 73% | 1706 | 1699 | 1702 | 1704 | 1702 | 1717 | 1702.13 | 1330 | 73% | 837 | 847 | 849 | 845 | 848 | 855 | 843 | 750 | 73% | 1610 | 1629 | 1627 | 1632 | 1648 | 1672 | 1627 | 1450
74% | 1943 | 1962 | 1966 | 1962 | 1968 | 1991 | 1961 | 1400 | 74% | 1699 | 1691.94 | 1693 | 1696 | 1693 | 1710.94 | 1694 | 1330 | 74% | 833 | 842 | 843 | 839 | 843 | 850 | 839 | 750 | 74% | 1598 | 1613.94 | 1612 | 1615 | 1633 | 1658 | 1612 | 1450
75% | 1929 | 1948 | 1951.75 | 1948 | 1952 | 1976 | 1946 | 1400 | 75% | 1692 | 1683 | 1684 | 1688 | 1686 | 1702.75 | 1685 | 1330 | 75% | 829 | 837 | 838 | 834 | 839 | 845 | 834 | 750 | 75% | 1587 | 1601 | 1598 | 1599 | 1614 | 1641 | 1598 | 1450
76% | 1917 | 1933 | 1937 | 1934 | 1938 | 1961 | 1931 | 1400 | 76% | 1685 | 1676 | 1677 | 1679 | 1679 | 1693.56 | 1675.56 | 1330 | 76% | 824 | 833 | 833.56 | 830 | 834 | 840 | 828 | 750 | 76% | 1574 | 1588 | 1585 | 1584 | 1598 | 1626 | 1581 | 1450
77% | 1904 | 1920 | 1923 | 1919 | 1923 | 1948 | 1917 | 1400 | 77% | 1677 | 1669 | 1668 | 1670 | 1672 | 1685 | 1666 | 1330 | 77% | 819 | 828 | 828 | 824.37 | 829 | 835 | 824 | 750 | 77% | 1563 | 1573 | 1571 | 1569 | 1581 | 1610.37 | 1566 | 1450
78% | 1891.18 | 1906 | 1908 | 1904 | 1906 | 1932 | 1899 | 1400 | 78% | 1669 | 1660 | 1660 | 1662 | 1663 | 1675 | 1657 | 1330 | 78% | 814 | 824 | 823 | 819 | 825 | 830 | 819 | 750 | 78% | 1551 | 1556 | 1556 | 1554 | 1568 | 1595 | 1552 | 1450
79% | 1878 | 1892 | 1889 | 1888 | 1891 | 1916.99 | 1881 | 1400 | 79% | 1661 | 1650 | 1651 | 1653 | 1655 | 1667 | 1648 | 1330 | 79% | 809 | 818 | 818 | 813 | 819 | 825 | 814 | 750 | 79% | 1543 | 1541 | 1540 | 1540 | 1552 | 1578.99 | 1538 | 1450
80% | 1864 | 1877 | 1874.8 | 1873 | 1876 | 1902 | 1863 | 1400 | 80% | 1654 | 1642 | 1643 | 1645 | 1647 | 1657 | 1639 | 1330 | 80% | 805 | 813 | 813 | 809 | 814 | 820 | 810 | 750 | 80% | 1530.8 | 1526 | 1528 | 1525 | 1536 | 1563 | 1521 | 1450
81% | 1851 | 1861 | 1858.61 | 1856 | 1860.61 | 1886 | 1848 | 1400 | 81% | 1646 | 1632 | 1634 | 1633 | 1638 | 1647 | 1629 | 1330 | 81% | 801 | 808 | 807 | 803 | 809 | 814 | 804 | 750 | 81% | 1519 | 1511 | 1511 | 1511 | 1521 | 1546 | 1507 | 1450
82% | 1838 | 1846 | 1845 | 1843 | 1845 | 1869 | 1831 | 1400 | 82% | 1639 | 1622 | 1624 | 1623 | 1629 | 1636 | 1619 | 1330 | 82% | 797 | 802 | 802 | 798 | 803 | 808 | 798 | 750 | 82% | 1507.42 | 1499 | 1498 | 1497 | 1506 | 1530 | 1491 | 1450
83% | 1828 | 1830 | 1831.23 | 1826 | 1829 | 1851 | 1813 | 1400 | 83% | 1631 | 1612 | 1613 | 1614 | 1621 | 1626 | 1607 | 1330 | 83% | 792 | 796 | 795 | 791 | 796 | 803 | 791 | 750 | 83% | 1494 | 1482 | 1485 | 1481 | 1491 | 1511 | 1476.23 | 1450
84% | 1814 | 1813 | 1814 | 1804 | 1813 | 1830 | 1796 | 1400 | 84% | 1622 | 1602 | 1604 | 1603 | 1612 | 1615 | 1597 | 1330 | 84% | 787 | 789 | 789 | 784 | 790 | 797 | 784 | 750 | 84% | 1480 | 1466 | 1473 | 1466.04 | 1475 | 1495 | 1461 | 1450
85% | 1801 | 1796 | 1798 | 1785 | 1799 | 1814 | 1773 | 1400 | 85% | 1612 | 1591 | 1594 | 1590 | 1601 | 1602 | 1583.85 | 1330 | 85% | 783 | 782 | 782 | 778 | 782 | 790 | 777 | 750 | 85% | 1466 | 1449 | 1458 | 1449 | 1459 | 1478 | 1447 | 1450
86% | 1784 | 1779 | 1781 | 1766 | 1780 | 1799 | 1753 | 1400 | 86% | 1602 | 1577 | 1582 | 1577 | 1590 | 1587 | 1570 | 1330 | 86% | 778 | 775 | 776 | 773 | 775 | 782 | 771 | 750 | 86% | 1451 | 1433 | 1442 | 1432 | 1444 | 1459 | 1433 | 1450
87% | 1769 | 1758 | 1761 | 1747 | 1762 | 1776 | 1735 | 1400 | 87% | 1593 | 1565 | 1570 | 1564 | 1577 | 1570 | 1557 | 1330 | 87% | 772 | 768 | 770 | 766 | 768 | 776 | 764 | 750 | 87% | 1435 | 1416 | 1423 | 1414 | 1428 | 1438 | 1414 | 1450
88% | 1751 | 1739 | 1740 | 1727 | 1744 | 1753 | 1717 | 1400 | 88% | 1582 | 1554 | 1560 | 1551 | 1563 | 1557.28 | 1541 | 1330 | 88% | 766 | 761 | 764 | 760 | 762 | 769 | 757 | 750 | 88% | 1417 | 1400 | 1407 | 1395 | 1409 | 1420 | 1396 | 1450
89% | 1737 | 1720 | 1722 | 1707 | 1725.09 | 1731 | 1696 | 1400 | 89% | 1568 | 1541 | 1548 | 1535 | 1551 | 1542 | 1520 | 1330 | 89% | 759 | 754 | 757 | 753 | 755 | 761 | 749 | 750 | 89% | 1402 | 1383 | 1388 | 1379 | 1394 | 1403 | 1378 | 1450
90% | 1718.9 | 1696 | 1705.9 | 1683 | 1703 | 1710 | 1673 | 1400 | 90% | 1557 | 1523.9 | 1533 | 1516 | 1535 | 1523 | 1503 | 1330 | 90% | 752 | 748 | 748 | 746 | 747 | 753 | 742 | 750 | 90% | 1385 | 1364 | 1366.9 | 1360 | 1376 | 1382 | 1353 | 1450
91% | 1696 | 1671 | 1683 | 1661 | 1681 | 1681.71 | 1647 | 1400 | 91% | 1543 | 1505 | 1516 | 1499.71 | 1516 | 1503 | 1483 | 1330 | 91% | 745 | 739.71 | 741 | 738 | 741 | 744 | 734 | 750 | 91% | 1367 | 1340 | 1344 | 1337 | 1353.71 | 1356 | 1328 | 1450
92% | 1678 | 1646 | 1661 | 1631 | 1659 | 1650 | 1617 | 1400 | 92% | 1528 | 1486 | 1498 | 1478 | 1497 | 1480 | 1464 | 1330 | 92% | 739 | 731 | 732 | 730 | 732 | 733 | 725 | 750 | 92% | 1349 | 1317 | 1322.52 | 1316 | 1334 | 1330 | 1304 | 1450
93% | 1656.33 | 1615 | 1634 | 1601 | 1630 | 1612 | 1588 | 1400 | 93% | 1509 | 1467.33 | 1481 | 1455 | 1475 | 1453 | 1439 | 1330 | 93% | 730 | 723 | 723 | 722 | 723 | 723 | 713 | 750 | 93% | 1329 | 1295 | 1297.33 | 1293 | 1308 | 1302 | 1275 | 1450
94% | 1628.14 | 1583 | 1606 | 1555.14 | 1602 | 1574 | 1545 | 1400 | 94% | 1491 | 1437.14 | 1462 | 1426.14 | 1446 | 1417 | 1414.14 | 1330 | 94% | 721 | 714 | 713 | 711 | 714 | 711.14 | 702 | 750 | 94% | 1307 | 1267 | 1268 | 1260 | 1282.14 | 1273 | 1245 | 1450
95% | 1599.95 | 1541 | 1565.95 | 1519 | 1558 | 1525 | 1507 | 1400 | 95% | 1473 | 1406 | 1435 | 1389.95 | 1416 | 1376.95 | 1374 | 1330 | 95% | 714 | 702 | 701 | 698.95 | 703 | 698.95 | 691 | 750 | 95% | 1283 | 1241 | 1241 | 1227.95 | 1250 | 1241 | 1213 | 1450
96% | 1561 | 1494 | 1523.76 | 1471 | 1516 | 1461 | 1448 | 1400 | 96% | 1450 | 1355 | 1396 | 1335 | 1379 | 1330.76 | 1316 | 1330 | 96% | 705 | 691.76 | 691 | 684.76 | 693 | 684.76 | 677 | 750 | 96% | 1253 | 1207 | 1211 | 1194 | 1223 | 1204 | 1173 | 1450
97% | 1523 | 1415.57 | 1463 | 1405 | 1448.57 | 1387.57 | 1370.57 | 1400 | 97% | 1408 | 1283.57 | 1325 | 1268 | 1318 | 1257.57 | 1238.57 | 1330 | 97% | 693 | 676 | 674 | 665 | 675 | 661 | 653 | 750 | 97% | 1217.57 | 1169.57 | 1173 | 1151 | 1182 | 1150 | 1121 | 1450
98% | 1456.38 | 1338 | 1368.38 | 1330 | 1362 | 1292.38 | 1244.38 | 1400 | 98% | 1361.38 | 1209 | 1234 | 1186.38 | 1212.38 | 1178.38 | 1153 | 1330 | 98% | 671.38 | 651 | 654 | 645 | 653 | 634 | 623 | 750 | 98% | 1173.38 | 1101.76 | 1123.38 | 1106 | 1123.38 | 1081.38 | 1042.38 | 1450
99% | 1353 | 1155.38 | 1217 | 1206.19 | 1203 | 1117.95 | 1089 | 1400 | 99% | 1215 | 1062 | 1110.19 | 1066 | 1066 | 1032 | 1011.57 | 1330 | 99% | 651 | 601.19 | 620 | 606 | 612 | 582.19 | 571 | 750 | 99% | 1116.19 | 980.19 | 1026.19 | 1007.19 | 1030.19 | 970 | 924.19 | 1450

## 2019 TAS Inertia
2019 Tasmania inertia
This is the 2019 inertia projection duration curve data for the Tasmania region of the National Electricity Market. These charts are used in the 2019 Notice of inertia and fault level shortfalls in Tasmania.
2019 Tasmania Inertia Levels projections
| 2020-21 (MWs) | 2021-22 (MWs) | 2022-23 (MWs) | 2023-24 (MWs) | 2024-25 (MWs) | 2025-26 (MWs) | Secure Level (MWs) | Minimum Threshold (MWs)
0% | 8891.6 | 9023.4 | 9105.3 | 9055.8 | 9023.4 | 8913.3 | 3800 | 3200
1% | 8326.729 | 8378.2 | 8355.8 | 8328.958 | 8352.2 | 8291.9 | 3800 | 3200
2% | 8239.5 | 8262.828 | 8249.72 | 8252.168 | 8255.1 | 8207.16 | 3800 | 3200
3% | 8151.2 | 8183.7 | 8177.3 | 8181.6 | 8179.7 | 8140.435 | 3800 | 3200
4% | 8082 | 8114.2 | 8105.288 | 8125.7 | 8114.2 | 8081.776 | 3800 | 3200
5% | 8028.5 | 8035.972 | 8028.5 | 8045.5 | 8055.9 | 8028.5 | 3800 | 3200
6% | 7955.54 | 7977.796 | 7976.9 | 7965.4 | 8004.648 | 7967.172 | 3800 | 3200
7% | 7896.7 | 7903.729 | 7903.2 | 7905.1 | 7939.779 | 7903.2 | 3800 | 3200
8% | 7833.98 | 7834.03 | 7849.91 | 7844.2 | 7900.12 | 7853.55 | 3800 | 3200
9% | 7771.4 | 7761.2 | 7779.991 | 7790.137 | 7836.219 | 7801.5 | 3800 | 3200
10% | 7700.4 | 7692.8 | 7720.9 | 7734.7 | 7771.344 | 7744.848 | 3800 | 3200
11% | 7628.406 | 7639.353 | 7656.5 | 7669.153 | 7727.3 | 7690.642 | 3800 | 3200
12% | 7573 | 7583.2 | 7609.4 | 7617.87 | 7661.338 | 7637.502 | 3800 | 3200
13% | 7520.66 | 7520.1 | 7547.9 | 7561.835 | 7605.98 | 7581.62 | 3800 | 3200
14% | 7470.3 | 7455.208 | 7484.2 | 7503.9 | 7544.5 | 7532.3 | 3800 | 3200
15% | 7417.7 | 7398.977 | 7432.677 | 7453.039 | 7490.316 | 7479.2 | 3800 | 3200
16% | 7370.064 | 7344.274 | 7375.3 | 7398.454 | 7434.9 | 7432.516 | 3800 | 3200
17% | 7322.7 | 7273.251 | 7320.7 | 7339.434 | 7378.278 | 7388.3 | 3800 | 3200
18% | 7265.26 | 7234.92 | 7261.3 | 7287.8 | 7315.92 | 7335.66 | 3800 | 3200
19% | 7207.503 | 7174.6 | 7207.5 | 7237.11 | 7247.31 | 7284.203 | 3800 | 3200
20% | 7151 | 7125.4 | 7155.2 | 7176.392 | 7178.4 | 7239.3 | 3800 | 3200
21% | 7097.03 | 7069.352 | 7109.1 | 7123.9 | 7113.989 | 7189.363 | 3800 | 3200
22% | 7043.392 | 7011.752 | 7058.2 | 7065.584 | 7067.2 | 7124.644 | 3800 | 3200
23% | 6986.05 | 6955.3 | 7015.1 | 7010.9 | 7015.025 | 7075.7 | 3800 | 3200
24% | 6920 | 6901.6 | 6946.142 | 6945.5 | 6963.8 | 7032.36 | 3800 | 3200
25% | 6865.801 | 6848.9 | 6896.6 | 6888.4 | 6903.8 | 6980.3 | 3800 | 3200
26% | 6811.004 | 6794.5 | 6847.044 | 6848.18 | 6843.744 | 6921.3 | 3800 | 3200
27% | 6753.8 | 6722.196 | 6787.849 | 6795.149 | 6780.2 | 6869 | 3800 | 3200
28% | 6694.53 | 6652.27 | 6733.2 | 6745.8 | 6712.79 | 6808.7 | 3800 | 3200
29% | 6636.832 | 6590.2 | 6677.1 | 6694.6 | 6649.355 | 6746.088 | 3800 | 3200
30% | 6588.268 | 6533.2 | 6609.6 | 6634.1 | 6590.6 | 6691.652 | 3800 | 3200
31% | 6532.219 | 6484.773 | 6547.673 | 6572.873 | 6531.546 | 6629.573 | 3800 | 3200
32% | 6475.4 | 6432.016 | 6488.542 | 6507.3 | 6474.94 | 6562.5 | 3800 | 3200
33% | 6410.1 | 6359.1 | 6435.1 | 6434.405 | 6405.5 | 6501.775 | 3800 | 3200
34% | 6358.1 | 6289.864 | 6363 | 6362.58 | 6332 | 6442.116 | 3800 | 3200
35% | 6290.891 | 6220.4 | 6291.5 | 6291.494 | 6257.8 | 6359.985 | 3800 | 3200
36% | 6198.6 | 6157.57 | 6237.7 | 6218.9 | 6186.346 | 6290.19 | 3800 | 3200
37% | 6121.003 | 6084.772 | 6166.2 | 6156.6 | 6115.477 | 6219.859 | 3800 | 3200
38% | 6045.32 | 6014.1 | 6092.02 | 6079.64 | 6049.44 | 6135.62 | 3800 | 3200
39% | 5961.431 | 5941.084 | 6021.3 | 6006.1 | 5977.21 | 6049.131 | 3800 | 3200
40% | 5870.838 | 5864.4 | 5935.5 | 5930.106 | 5893 | 5962.52 | 3800 | 3200
41% | 5796.83 | 5786.483 | 5863.366 | 5852.283 | 5819.7 | 5881.581 | 3800 | 3200
42% | 5711.848 | 5699.176 | 5777.864 | 5768.948 | 5744.5 | 5804.628 | 3800 | 3200
43% | 5609.435 | 5619.66 | 5706.77 | 5669.2 | 5654.945 | 5705 | 3800 | 3200
44% | 5525.456 | 5525.734 | 5623.464 | 5584.278 | 5571.252 | 5612.952 | 3800 | 3200
45% | 5406.3 | 5435.284 | 5542.949 | 5495.142 | 5483.249 | 5506.2 | 3800 | 3200
46% | 5324.708 | 5351.588 | 5457.6 | 5405.676 | 5391.928 | 5401.564 | 3800 | 3200
47% | 5236.8 | 5272.5 | 5341.552 | 5325.7 | 5298.966 | 5320.645 | 3800 | 3200
48% | 5146.55 | 5184.95 | 5257.9 | 5237.2 | 5200.6 | 5233.1 | 3800 | 3200
49% | 5050.672 | 5098.731 | 5172.41 | 5147.172 | 5116.493 | 5136.2 | 3800 | 3200
50% | 4980.1 | 5013.996 | 5085.148 | 5062.1 | 5028.356 | 5051.924 | 3800 | 3200
51% | 4906.7 | 4933.393 | 5006.93 | 4965.623 | 4955.565 | 4968.286 | 3800 | 3200
52% | 4835 | 4858.07 | 4924.562 | 4876.474 | 4874.9 | 4899.496 | 3800 | 3200
53% | 4764.855 | 4781.55 | 4851.2 | 4819.6 | 4805.755 | 4834.655 | 3800 | 3200
54% | 4706.304 | 4721.3 | 4771.156 | 4746.136 | 4743.6 | 4761.324 | 3800 | 3200
55% | 4637.134 | 4658.685 | 4708.268 | 4684.534 | 4689.934 | 4692.451 | 3800 | 3200
56% | 4592.494 | 4601.692 | 4645.798 | 4619.996 | 4634.192 | 4634.498 | 3800 | 3200
57% | 4535.837 | 4554.237 | 4592.958 | 4560.479 | 4570 | 4570.995 | 3800 | 3200
58% | 4487.9 | 4504.68 | 4531.52 | 4505.1 | 4526.4 | 4512 | 3800 | 3200
59% | 4434.082 | 4460.7 | 4477.146 | 4458.7 | 4473.064 | 4460.482 | 3800 | 3200
60% | 4391.9 | 4411.222 | 4426.332 | 4412.666 | 4426.366 | 4409.122 | 3800 | 3200
61% | 4391.9 | 4411.222 | 4426.332 | 4412.666 | 4426.366 | 4409.122 | 3800 | 3200
62% | 4349.63 | 4367.624 | 4371.806 | 4368.703 | 4383.203 | 4364.712 | 3800 | 3200
63% | 4304.372 | 4331.952 | 4318.852 | 4326.668 | 4336.284 | 4323.5 | 3800 | 3200
64% | 4266.6 | 4290.8 | 4273.9 | 4283.56 | 4296.895 | 4280.1 | 3800 | 3200
65% | 4233 | 4250.146 | 4228.592 | 4247.4 | 4259.076 | 4246.968 | 3800 | 3200
66% | 4197.481 | 4211.181 | 4188.327 | 4209.754 | 4222.462 | 4201.481 | 3800 | 3200
67% | 4166.408 | 4178.424 | 4151.1 | 4171.024 | 4184.116 | 4161.724 | 3800 | 3200
68% | 4134 | 4143.2 | 4111.978 | 4128.812 | 4151.1 | 4127.378 | 3800 | 3200
69% | 4095.9 | 4107.2 | 4070.61 | 4096.46 | 4114.77 | 4095.42 | 3800 | 3200
70% | 4060.253 | 4075.551 | 4038.302 | 4059.102 | 4081.6 | 4055 | 3800 | 3200
71% | 4028.888 | 4046.2 | 4000.5 | 4026.864 | 4049.7 | 4023.124 | 3800 | 3200
72% | 3993.913 | 4006.008 | 3965.6 | 3993.1 | 4022.313 | 3990.791 | 3800 | 3200
73% | 3961.082 | 3967.776 | 3932.464 | 3957.382 | 3989.794 | 3955.9 | 3800 | 3200
74% | 3930.8 | 3938.05 | 3894.3 | 3931.25 | 3955 | 3924.15 | 3800 | 3200
75% | 3894.724 | 3904.256 | 3858.704 | 3898.512 | 3920.8 | 3887.356 | 3800 | 3200
76% | 3859.9 | 3862.5 | 3822.737 | 3862.8 | 3884.111 | 3855.937 | 3800 | 3200
77% | 3817.872 | 3820.6 | 3799 | 3821.472 | 3844.854 | 3817.5 | 3800 | 3200
78% | 3787.197 | 3794.1 | 3762.192 | 3791.097 | 3808.4 | 3784.5 | 3800 | 3200
79% | 3749.76 | 3750.52 | 3724.38 | 3756.5 | 3770.7 | 3742.32 | 3800 | 3200
80% | 3712.7 | 3708.644 | 3683.298 | 3713.7 | 3727.183 | 3705.3 | 3800 | 3200
81% | 3675.4 | 3671.31 | 3636.794 | 3677.636 | 3681.242 | 3661.1 | 3800 | 3200
82% | 3628.723 | 3631.6 | 3595.246 | 3637.7 | 3641 | 3610.223 | 3800 | 3200
83% | 3579.2 | 3578.704 | 3550.808 | 3593.532 | 3590.112 | 3560.7 | 3800 | 3200
84% | 3526.625 | 3523.27 | 3490.3 | 3549.4 | 3539.325 | 3481.725 | 3800 | 3200
85% | 3475.4 | 3475.4 | 3445.03 | 3494.1 | 3477 | 3425.7 | 3800 | 3200
86% | 3423.9 | 3425.7 | 3389.482 | 3447.2 | 3425.7 | 3378.1 | 3800 | 3200
87% | 3373.656 | 3366.9 | 3334.5 | 3393.5 | 3353.728 | 3310.628 | 3800 | 3200
88% | 3328.2 | 3329.709 | 3258.5 | 3340.4 | 3289.718 | 3242.063 | 3800 | 3200
89% | 3251.1 | 3266.4 | 3208.2 | 3266.8 | 3224.9 | 3180.99 | 3800 | 3200
90% | 3194.352 | 3220.013 | 3134.4 | 3208.2 | 3143 | 3116.1 | 3800 | 3200
91% | 3127.652 | 3134.4 | 3071.1 | 3129.2 | 3088.104 | 3043.9 | 3800 | 3200
92% | 3052.5 | 3083.766 | 3002.6 | 3058.6 | 2989.794 | 2963.633 | 3800 | 3200
93% | 2987.684 | 3008 | 2880.162 | 2990.766 | 2870.8 | 2841.6 | 3800 | 3200
94% | 2813.94 | 2920.67 | 2714.715 | 2850.685 | 2740.59 | 2662.305 | 3800 | 3200
95% | 2617.768 | 2779.236 | 2514.8 | 2680.776 | 2532.816 | 2453.68 | 3800 | 3200
96% | 2374.377 | 2554.119 | 2281.612 | 2450.505 | 2247.683 | 2116.5 | 3800 | 3200
97% | 1889.568 | 2134.888 | 1883.2 | 1946.8 | 1838.7 | 1796.1 | 3800 | 3200
98% | 1529.1 | 1653.6 | 1529.1 | 1490.9 | 1490.9 | 1447.2 | 3800 | 3200
99% | 1099.4 | 1099.4 | 1099.4 | 1080.6 | 1099.4 | 1099.4 | 3800 | 3200