## Index
The National Electricity Market Constraint Report 2022
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Ad-Hoc | 1 | 1 | 0 | 0 | 0 | 0
Constraint Automation - Real Time | 29805 | 37744 | 32817 | 53504 | 40710 | 48882
Constraint Automation | 20 | 48 | 49 | 39 | 23 | 67
DATASNAP | 44 | 92 | 90 | 62 | 60 | 67
FCAS | 267 | 486 | 1192 | 730 | 418 | 700
NSW | 2455 | 8206 | 5092 | 7926 | 6562 | 3873
Negative Residue | 0 | 0 | 0 | 12 | 0 | 0
Non-Conformance | 52 | 35 | 29 | 31 | 40 | 52
Other | 0 | 3 | 1 | 0 | 16 | 0
Outage Ramping | 16928 | 19368 | 25718 | 23622 | 33118 | 28264
PASA | 0 | 0 | 0 | 0 | 1 | 1
Qld | 246 | 1716 | 582 | 937 | 1305 | 1850
Quick | 386 | 1032 | 865 | 1072 | 862 | 2592
SA | 1775 | 3239 | 7132 | 2309 | 6564 | 4980
Tas | 134 | 193 | 629 | 25 | 351 | 115
Vic | 1376 | 6280 | 5656 | 1418 | 2312 | 2115
Total constraint eqns | 11660 | 11578 | 11467 | 12348 | 13127 | 13127
Total changes without outage ramping and CA-RT | 6756 | 21331 | 21317 | 14561 | 18514 | 16412
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578 | 11467 | 12348 | 13127 | 14297 | 15160
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917 | 4036 | 4390 | 4603 | 4973 | 5498
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387 | 505 | 585 | 588 | 641 | 638
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82 | -111 | 881 | 779 | 1170 | 863

## Binding
Constraint Equation ID | 2022 Hours | 2021 Hours | Description | Type | Limit Type | Region
#BLUEGSF1_E | 4535.0833 | 0 | QCBS1B.ENERGY * 1 <= 148 (Wt = 360) | Other | DEFAULT | Quick
N^N-LS_SVC | 4518 | 69.5 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; Swamp out when three directlink cables are O/S; TG formulation only | Outage | Voltage Stability | NSW
#TORRB3_D_E | 2167.3333 | 1939.75 | STSB3.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
N>NIL_94T | 1657 | 843.9167 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | NIL | Thermal | NSW
#TORRB4_D_E | 1590.8333 | 1622.4167 | STSB4.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
S>NIL_MHNW1_MHNW2 | 1558.5833 | 1723.9167 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
N^^N_NIL_3 | 1522.0833 | 1245.9167 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL | Voltage Stability | NSW
N>NIL_969 | 1303.4167 | 183.5 | Out= Nil, avoid O/L Gunnedah to Tamworth (969) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
#TORRB2_D_E | 1179.0833 | 2726.0833 | STSB2.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
N_TARALGAWF_ZERO | 1036.8333 | 23.9167 | Taralga WF upper limit of 0 MW | Outage | Unit Zero | NSW
Q_STR_7C2K_HASF_4 | 1029.5 | 0 | No limit to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
Q>NIL_EMCM_6056 | 969.5833 | 475.5833 | Out= NIL, avoid thermal overload on Emerald to Comet (6056) 66 kV Feeder | NIL | Thermal | Qld
N>NIL_94K_1 | 907.5833 | 0 | Out= Nil, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | NIL | Thermal | NSW
V^^V_NIL_KGTS V^^V_NIL_KGTS_2 | 863.75 | 349.5833 | Out= Nil, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | NIL | Voltage Stability | Vic
#MRTLSWF1_E | 861.5833 | 0 | VTG21M.ENERGY * 1 <= 32 (Wt = 360) | Other | DEFAULT | Quick
T>T_X_NTH_STH_B | 705.25 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit southern generators to >= southern load - 15 MW | Outage | Thermal | Tas
N>NIL_997_99A | 686.9167 | 234.8333 | Out= Nil, avoid O/L Corowa to Albury 132kV line (997/1) on trip of Finley to Uranquinty 132kV line (99A), Feedback | NIL | Thermal | NSW
Q_KEP-HYB_25MW | 645.4167 | 0 | Kennedy Energy Park upper limit of 25MW | Outage | Discretionary | Qld
N>NIL_PKTX_LV | 631.0833 | 394.4167 | Out= Nil, avoid O/L either Parkes 132kV/66kV Transformer on NIL trip, Feedback. | NIL | Thermal | NSW
SVML_ZERO | 619.75 | 1008.3333 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
Q>NIL_YLMR | 604.5833 | 562.25 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
V_KIAMSF_0 | 514.75 | 25.25 | Out = Kiamal Syncon, limit Kiamal solar farm to 0 MW | Outage | Discretionary | Vic
#WARWSF2_E | 506.75 | 1509.3333 | QMRY4W.ENERGY * 1 <= 16 (Wt = 360) | Other | DEFAULT | Quick
V>>V_NIL_18 | 488.0833 | 228.1667 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
#BRYB2WF2_E | 484.5833 | 0 | VBBT2B.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
SVML^NIL_MH-CAP_ON | 472.25 | 283 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL | Voltage Stability | SA
N_X_MBTE_3A & N_X_MBTE_3B | 441.9167 | 321.5833 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
#GSTONE1_E | 439.1667 | 0 | QGLD1.ENERGY * 1 <= 260 (Wt = 35) | Other | DEFAULT | Quick
NSA_S_PORxxx | 421.6667 | 0 | Port Lincoln >= 15 MW for Network Support Agreement | Outage | Network Support | SA
V^^N_NIL_1 | 402 | 875 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
V_BANSF_BBD_60 | 384.1667 | 199.9167 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
N^^Q_LS_VC_B1, 2, 3, 4, 5, 6 | 382.1667 | 9.4167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
S>NIL_HUWT_STBG3 | 379.0833 | 16 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Constraint Swamped when Wattle PT when generating >=60 MW) | NIL | Thermal | SA
N_TARALGAWF_005 | 359.9167 | 0 | Taralga WF upper limit of 5 MW | Outage | Discretionary | NSW
S^NIL_CRK+MTM_95 | 347.5 | 0 | Out= Nil, upper limit for Cathedral Rocks WF + Mt Millar WF <= 95 MW to maintain voltage stability limits | NIL | Voltage Stability | SA
V::N_DDSM_xxx | 318.0833 | 132.25 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q_STR_7C0K_HASF | 306.5833 | 0 | No limit to Haughton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N>NIL_9R6_9R5 | 300.6667 | 0 | Out= Nil, avoid O/L Wagga North to Wagga132 (9R6) on trip of Wagga North to Wagga330 (9R5) line, Feedback | NIL | Thermal | NSW
N::N_UTRV_2 | 288.8333 | 4.25 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
T::T_NIL_1 | 282.6667 | 1427.5 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
S_ISLE_CRK_10 | 281.5 | 0 | Discretionary upper limit on Cathedral Rocks windfarm<=10 MW when 2-4 syn cons I/S for SA is at risk of islanding or in islanded mode(Note: this equation is swamped when 0-1 sync cons are I/S) | Outage | Discretionary | SA
Q^^N_NIL_SRAR | 279.25 | 134 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
#QPS5_D_E | 260.4167 | 22.4167 | SQPS5Q.ENERGY * 1 = 74 (Wt = 755) | Other | DEFAULT | Direction
#BOLIVPS1_E | 259.5833 | 0 | SPGG1B.ENERGY * 1 <= 96 (Wt = 360) | Other | DEFAULT | Quick
Q_KEP-HYB_20MW | 257.0833 | 0 | Kennedy Energy Park upper limit of 20MW | Outage | Discretionary | Qld
#WEMENSF1_E | 251.5 | 255 | VWES2W.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 251.4167 | 411.5 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | Voltage Stability | NSW
T_WIND_NTH_100 | 243.3333 | 0 | 100 MW upper limit on TAS North Wind Generation | Outage | Transient Stability | Tas
T_MRWF_100 | 241.8333 | 0 | Discretionary 100 MW upper limit on Musselroe Wind Farm | Outage | Discretionary | Tas
Q_KEP-HYB_ZERO | 234.75 | 0 | Kennedy Energy Park upper limit of 0MW | Outage | Unit Zero | Qld
Q_STR_7C2K_HASF_5 | 231.8333 | 0 | No limit to Haughton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
T_CTHLWF_100 | 228.0833 | 0 | Wild Cattle Hill Wind Farm upper limit of 100 MW | Outage | Discretionary | Tas
V>V_NIL_17 | 226.3333 | 283.8333 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
#STOCKYD1_E | 223.6667 | 126.8333 | VHGT1S.ENERGY * 1 <= 400 (Wt = 360) | Other | DEFAULT | Quick
S>NIL_NWRB2_NWRB1 | 220.4167 | 0 | Out= NIL, avoid O/L North West Bend-Roberstown #1 132kV line on trip of North West Bend-Robertstown #2 132kV line (this trips MWP1-3 SFs), Feedback | NIL | Thermal | SA
S:V_PA_SVC_470 | 219.25 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 470 MW | Outage | Oscillatory Stability | SA
#OAKEY1_E | 215.75 | 0 | QOKY1.ENERGY * 1 <= 173 (Wt = 360) | Other | DEFAULT | Quick
V_T_NIL_FCSPS | 207.4167 | 238.1667 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
Q_YARANSF1_RB | 206.25 | 30.5 | Yarrranlea Run Back limit | NIL | Discretionary | Qld
T_NTH_ROCOF_1 | 197.1667 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit non-synchronous generation and Basslink import to limit instantaneous Rate of Change of Frequency to < 3 Hz/sec in Nth TAS | Outage | ROC Frequency | Tas
V::N_X_SMSC_xxx | 191.75 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
N^^Q_NIL_A | 175.8333 | 39.25 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | Voltage Stability | NSW
N>NIL_LSDU | 172.25 | 270.3333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
N_CG2_ZERO_E | 171 | 0 | Direction to zero for Colongra #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_CG3_ZERO_E | 171 | 0 | Direction to zero for Colongra #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_CG4_ZERO_E | 171 | 0 | Direction to zero for Colongra #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
T>T_X_NTH_STH_A | 170.75 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit southern generators to <= southern load + 15 MW | Outage | Thermal | Tas
N_URANQ11_ZERO_E | 170 | 0 | Direction to zero for Uranquinty #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_URANQ12_ZERO_E | 170 | 0 | Direction to zero for Uranquinty #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_URANQ13_ZERO_E | 170 | 0 | Direction to zero for Uranquinty #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_URANQ14_ZERO_E | 170 | 0 | Direction to zero for Uranquinty #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
SA_TBSE1 | 169.8333 | 0 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS) Vic-SA Flow = South East Area Load - Local Generation | Outage | Region Separation | SA
SV_420_DYN | 168.25 | 335.4167 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
S_ISLE_LKB1+2+3_60 | 167.1667 | 0 | Discretionary upper limit on Lake Bonney (1+2+3) windfarms<=60 MW & No. in-service wind turbines for LKB at 41 Turbines.(Note otherwise, LKB 2+3 +1 will be constrained to 0 MW) | Outage | Discretionary | SA
Q_STR_SYN_HASF_ZERO | 166.5 | 0 | Limit 0MW to Haughton Solar farm if Haughton Syncon is OFF, swamp if Haughton Syncon is ON | Outage | System Strength | Qld
N_SITHE01_ZERO_E | 165.5833 | 0 | Direction to zero for Sithe for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
S_TORRB2_ZERO_E | 165 | 0 | Direction to zero for Torrens Island B #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_TORRB3_ZERO_E | 165 | 0 | Direction to zero for Torrens Island B #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
N_CG1_ZERO_E | 163 | 0 | Direction to zero for Colongra #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
#URANQ11_O_E | 160.9167 | 0 | NURQ1U.ENERGY * 1 >= 150 (Wt = 65) | Other | DEFAULT | Direction
Q_MARYRSF1_RB | 160.3333 | 26.5833 | Maryrorough Run Back limit | NIL | Discretionary | Qld
N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 159.25 | 0 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
#URANQ13_O_E | 157.0833 | 0 | NURQ3U.ENERGY * 1 >= 150 (Wt = 65) | Other | DEFAULT | Direction
V_NPS_ZERO_E | 156.5 | 0 | Direction to zero for Newport for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLA02_ZERO_E | 155.4167 | 0 | Direction to zero for Jeeralang A2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLA04_ZERO_E | 155.4167 | 0 | Direction to zero for Jeeralang A4 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLA01_ZERO_E | 155 | 0 | Direction to zero for Jeeralang A1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
N_SHGEN_ZERO_E | 154.3333 | 0 | Direction to zero for Shoalhaven for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
#URANQ14_O_E | 153.5 | 0 | NURQ4U.ENERGY * 1 >= 150 (Wt = 65) | Other | DEFAULT | Direction
V_JLB01_ZERO_E | 153.0833 | 0 | Direction to zero for Jeeralang B1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLB02_ZERO_E | 153.0833 | 0 | Direction to zero for Jeeralang B2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLB03_ZERO_E | 153.0833 | 0 | Direction to zero for Jeeralang B3 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
#URANQ12_O_E | 151.75 | 0 | NURQ2U.ENERGY * 1 >= 150 (Wt = 65) | Other | DEFAULT | Direction
V_MCKAY1_ZERO_E | 149.25 | 0 | Direction to zero for McKay Creek for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_DARTM1_ZERO_E | 147.75 | 0 | Direction to zero for Dartmouth for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
#WARWSF1_E | 142.9167 | 383.4167 | QMRY3W.ENERGY * 1 <= 32 (Wt = 360) | Other | DEFAULT | Quick
Q>>BCST_BCST_CLWU | 141.9167 | 89.3333 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line, avoid O/L the remaining Stanwell to Bouldercombe 848 or 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q>NIL_EMBW_EMLV_DS | 141.1667 | 11.5833 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
#CTHLWF1_E | 141.0833 | 0.083333 | TWC11C.ENERGY * 1 <= 15 (Wt = 360) | Other | DEFAULT | Quick
V>>V_DDSM_1 | 136.9167 | 91.5 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Thermal | Vic
S_PPCCGT_ZERO_E | 136.5 | 0 | Direction to zero for Pelican Point for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
V^^N_DTKV_1 | 136 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V>>V_NIL_25 | 134.6667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V>>N_NIL_65_66 | 133 | 103.3333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
SV_470_DYN | 132.6667 | 0 | SA to Victoria on Heywood upper transfer limit of 470 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
V>>V_NIL_9 | 131.75 | 75.75 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
#TORRB2_O_E | 131.25 | 0 | STSB2.ENERGY * 1 >= 70 (Wt = 755) | Other | DEFAULT | Direction
V^^V_MLNK_KGTS | 128.0833 | 221.9167 | Out= Murraylink, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | Outage | Voltage Stability | Vic
#KEPWF1_E | 123.75 | 40.75 | QROW1K.ENERGY * 1 <= 25 (Wt = 360) | Other | DEFAULT | Quick
T::T_NIL_3 | 120.8333 | 16.25 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
T_GRANVH_100 | 120.0833 | 0 | Discretionary 100 MW upper limit on Granville Harbour Wind Farm | Outage | Discretionary | Tas
#TORRB3_O_E | 119.6667 | 0 | STSB3.ENERGY * 1 >= 50 (Wt = 65) | Other | DEFAULT | Direction
V_LNGS1_ZERO_E | 119.5 | 0 | Direction to zero for Laverton North #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_LNGS2_ZERO_E | 119.5 | 0 | Direction to zero for Laverton North #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_VPGS2_ZERO_E | 116 | 0 | Direction to zero for Valley Power GT #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_VPGS3_ZERO_E | 116 | 0 | Direction to zero for Valley Power GT #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_VPGS5_ZERO_E | 116 | 0 | Direction to zero for Valley Power GT #5 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_VPGS6_ZERO_E | 116 | 0 | Direction to zero for Valley Power GT #6 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
T_MRWF_GCS | 113.8333 | 4.1667 | Musselroe wind farm Generator Control Scheme (GCS) constraint to maintain TAS FOS for a Tasmania generator event. Limit Musselroe wind farm based on load available/armed by Musselroe GCS | NIL | Other | Tas
V>>V_NIL_7 | 113.8333 | 81.5 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
N_SHPUMP_ZERO_E | 113.75 | 0 | Direction to zero for Shoalhaven Pump for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
#PPCCGT_O_E | 109.3333 | 0 | SPPT.ENERGY * 1 >= 246 (Wt = 65) | Other | DEFAULT | Direction
V_VPGS4_ZERO_E | 108.75 | 0 | Direction to zero for Valley Power GT #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
#SITHE01_O_E | 108.1667 | 0 | NSYW1.ENERGY * 1 >= 80 (Wt = 65) | Other | DEFAULT | Direction
T_V_BL_ZERO_E | 108 | 0 | Direction to zero for Basslink (Tas to Vic) for Dispatch and Predispatch and NOT PASA | Outage | Other | Tas
S::V_TBSE_TBSE | 107 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
T>T_X_LIPM_WACB_B | 106.9167 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, with associated 220kV CB at WA O/S, limit southern generators to >= southern load - 15 MW | Outage | Thermal | Tas
T>T_X_LIPM_TWO_F | 102.5 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L Chapel St to New Norfolk 110kV for loss of Creek Road to New Norfolk 110kV line and Nyrstar load declared credible, Feedback | Outage | Thermal | Tas
N_MBTE1_B | 102.4167 | 175.75 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
VT_ZERO | 100.3333 | 71.25 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Interconnector Zero | Vic
V::N_X_SMSC_O1 | 99.3333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
NSA_Q_GSTONE34_xxx | 99.0833 | 18.9167 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
#GANGARR1_E | 99 | 0.16667 | QWSS1G.ENERGY * 1 <= 120 (Wt = 360) | Other | DEFAULT | Quick
N::N_LTYS_2 | 98.8333 | 41 | Out = Lower Tumut-Yass (03), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
S_DVRB_270 | 98.8333 | 0 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
V_SHWF_FLT_286 | 97.25 | 3.3333 | Limit Stockyard Hill wind farm to 286 MW if Heywood flow is above 450 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
V::N_X_SMSC_O2 | 94.9167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
N>NIL_94T_947 | 94.5833 | 407 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947) line, Feedback | NIL | Thermal | NSW
V_MORTLK11_ZERO_E | 93.8333 | 0 | Direction to zero for Mortlake #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_MORTLK12_ZERO_E | 93.8333 | 0 | Direction to zero for Mortlake #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
S:V_PA_SVC_420 | 93.5833 | 176.5 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
#T-V-MNSP1_E_O_E | 93.4167 | 0 | T-V-MNSP1.ENERGY * 1 >= 150 (Wt = 65) | Other | DEFAULT | Direction
N_NIL_TE_B | 93 | 26.8333 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
N_BROKENH1_ZERO | 91.8333 | 135.5 | Broken Hill Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>>RBTX_WEWT_RBTX | 90.6667 | 66.75 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
Q_STR_8C_7C2K_RGUSF | 88.0833 | 0 | No limit to Rugby Run SF to if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8+ one SVC(Dysart or Nebo or Strathmore) OS OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2+Dysart SVC OS ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
Q_STR_7C2K_MEWF_3 | 86.25 | 0 | No limit to Mt Emerald Windfarm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
T_WIND_100 | 84.0833 | 0 | Limit output of TAS wind generation to less than 100 MW. Note, due to 144 MW rating of Non-Scheduled Woolnorth Wind Farm, directions may be required to reduce Woolnorth MW output if this constraint violates | Outage | Transient Stability | Tas
V>>V_NIL_27 | 84 | 0 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
N_SNOWYP_ZERO_E | 82.8333 | 0 | Direction to zero for Snowy Pumps for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_TUMUT3_ZERO_E | 82.8333 | 0 | Direction to zero for Tumut 3 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
S_ISLE_CANUNDA_35 | 81.9167 | 0 | Discretionary upper limit on Canunda windfarm<=35MW & No. in-service wind turbines for canunda at 23 Turbines.(Note otherwise,Canunda will be constrained to 0 MW) | Outage | Discretionary | SA
V^^SML_NSWRB_2 | 81.75 | 59.3333 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
#LGAPWF2_E | 81 | 68.6667 | SLGW4L.ENERGY * 1 <= 43 (Wt = 360) | Other | DEFAULT | Quick
S>>BWMP_TWPA_TPRS | 80.75 | 2.8333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
#MOUSF1_E | 80.5 | 0 | QMRR1M.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
NRM_NSW1_VIC1 | 80.4167 | 23.75 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
N>N-NIL_JUTX_LV | 80.25 | 0 | Out= Nil, avoid O/L Junee#3 132/66kV transformer on trip of Nil, Feedback. 90% of Rating is used as operating margin. | NIL | Thermal | NSW
#KABANWF1_E | 79.8333 | 0 | QTMW1K.ENERGY * 1 <= 76 (Wt = 360) | Other | DEFAULT | Quick
SVML_ROC_80 | 79.0833 | 102.3333 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
S_QPS5_ZERO_E | 78.75 | 0 | Direction to zero for Quarantine #5 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
N>NIL_9ML | 77.75 | 26.75 | Out= Nil, avoid O/L Crudine Ridge to Ilford Tee (9ML) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
#PAREPS1_E | 77.1667 | 0 | SDAP2P.ENERGY * 1 <= 80 (Wt = 360) | Other | DEFAULT | Quick
S>RBTX1_RBTX2_WEMWP4 | 76.3333 | 3.8333 | Out= Robertstown 275/132kV TX1, avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, | Outage | Thermal | SA
N>>LDNC_964_82 | 75.1667 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, Swamps if 964 O/S, Feedback | Outage | Thermal | NSW
S>DVTX_NIL_DVTX | 74.0833 | 40.75 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | NIL | Thermal | SA
VSML_ROC_80 | 73.1667 | 84.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
N>>NIL_86_8U_S | 73.0833 | 11.75 | Out= Nil, avoid O/L Armidale to Tamworth (8U or 86) on trip of the other Armidale to Tamworth line (86 or 8U), Feedback | NIL | Thermal | NSW
V_MURRAWRWF_FLT_90 | 72.3333 | 164.9167 | Limit Murra Warra Wind Farm 1+2 upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N::N_NIL_63 | 72.3333 | 52.25 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
V::S_SETB_TBSE_2 | 71 | 30.8333 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Transient Stability | SA
V_NUMURKAH_ZERO | 70.75 | 88 | Numurkah Solar Farm upper limit of 0 MW | NIL | Unit Zero | Vic
Q_CS_1100 | 70.6667 | 0 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary) | Outage | Discretionary | Qld
#WOOLGSF1_E | 70.1667 | 0 | QWLS1W.ENERGY * 1 <= 176 (Wt = 360) | Other | DEFAULT | Quick
#BRAEMAR3_O_E | 69.5 | 0 | QBRA3.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
V_VS_LB_CAN_50 | 68.6667 | 128.0833 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. Constraint swamp out when 2-4 syncons I/S | Outage | System Strength | SA
S_OSB-AG_ZERO_E | 68.5 | 0 | Direction to zero for Osborne for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#CG3_O_E | 67 | 0 | NCLG3D.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
#CG1_O_E | 66.3333 | 0 | NCLG1D.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
Q_BRAEMAR2_ZERO_E | 65.3333 | 0 | Direction to zero for Braemar #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
#SHPUMP_O_E | 64.3333 | 0 | NSHP1.ENERGY * 1 >= 200 (Wt = 65) | Other | DEFAULT | Direction
V::N_SMSC_xxx | 64.1667 | 0 | Out = One South Morang 330 kV series capacitor bank, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
Q_BRAEMAR3_ZERO_E | 64 | 0 | Direction to zero for Braemar #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
V:S_600_HY_TEST | 64 | 46.9167 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
Q_BRAEMAR6_ZERO_E | 61.8333 | 0 | Direction to zero for Braemar #6 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
#MSTUART1_E | 61.3333 | 0 | QMSP1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
S>>X_RBTU+RBTX_15 | 61.25 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
Q>>WOPW_WOSP_WOGP_2 | 60.75 | 28.5 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
#NPS_O_E | 60.3333 | 0 | VNPS.ENERGY * 1 >= 500 (Wt = 65) | Other | DEFAULT | Direction
#LNGS1_O_E | 60.25 | 0 | VAT21L.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
#MSTUART2_E | 60.25 | 0 | QMSP2.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#SNOWYP_O_E | 60 | 0 | NLTS3.ENERGY * 1 >= 193 (Wt = 65) | Other | DEFAULT | Direction
#KEPSF1_E | 59.0833 | 57.8333 | QROW2K.ENERGY * 1 <= 15 (Wt = 360) | Other | DEFAULT | Quick
N>Q-NIL_757_758 | 58.9167 | 115.25 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL | Thermal | NSW
V:S_600_HY_TEST_DYN | 58.5 | 42.5 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
#CG2_O_E | 58.0833 | 0 | NCLG2D.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
#BARCALDN_E | 57.5833 | 0 | QBCG.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#BRAEMAR3_E | 57.5 | 0.25 | QBRA3.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#BRAEMAR2_O_E | 57.3333 | 0 | QBRA2.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
Q-SMSF_MVAR | 56.6667 | 0 | Constraint to violate if Reactive power output of Sun Metals Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
V::S_NIL_MAXG_xxx | 56.6667 | 18.3333 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
Q-HAUSF_MVAR | 56.5833 | 0 | Constraint to violate if Reactive power output of Haughton Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
#YABULU_E | 56.4167 | 0 | QTYP.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
Q_STR_7C2K_MEWF_5 | 56.4167 | 0 | No limit to Mt Emerald Windfarm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q-MEWF_MVAR | 56.25 | 0 | Constraint to violate if Reactive power output of Mt Emerald Wind farm Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
N::N_RVYS_2 | 56.1667 | 0 | Out = Ravine -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
#BRAEMAR2_E | 55.6667 | 0 | QBRA2.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#CG4_O_E | 54.9167 | 0 | NCLG4D.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
#W/HOE#1_E | 54.75 | 0 | QWIV1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
T_MRWF_QLIM_xx | 54.6667 | 58.0833 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
#LNGS2_O_E | 54.4167 | 0 | VAT22L.ENERGY * 1 >= 170 (Wt = 65) | Other | DEFAULT | Direction
#W/HOE#2_E | 54.4167 | 0 | QWIV2.ENERGY * 1 >= 160 (Wt = 35) | Other | DEFAULT | Quick
#OSB-AG_O_E | 53.5 | 0 | SNBN1.ENERGY * 1 >= 185 (Wt = 65) | Other | DEFAULT | Direction
V^^N_DDSM_1 | 53.0833 | 0 | Out = Dederang to South Morang 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^N_DTMN_1 | 52.3333 | 5.25 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_BRAEMAR7_ZERO_E | 51.3333 | 0 | Direction to zero for Braemar #7 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_WIV1_ZERO_E | 50.8333 | 0 | Direction to zero for Wivenhoe #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_WIV2_ZERO_E | 50.8333 | 0 | Direction to zero for Wivenhoe #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
#DEVILS_G_E | 50.6667 | 566.5833 | TDG11.ENERGY * 1 <= 64 (Wt = 360) | Other | DEFAULT | Quick
S>>MKRB_TWPA_TPRS | 50.5 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBPA+RBTX2_06 | 50.5 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
T_JBUTTERS_100 | 50.1667 | 0 | Discretionary 100 MW upper limit on John Butters | Outage | Discretionary | Tas
T>T_NIL_110_1 | 49.75 | 41.9167 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
V_KARADSF_FLT_25 | 49.6667 | 209.0833 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>>NIL_TWPA_TPRS | 48.8333 | 7.8333 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
N>NIL_MBDU | 48.75 | 56.8333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
Q_BARCALDN_ZERO_E | 48.4167 | 0 | Direction to zero for Barcaldine for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
N>>99F_994_63 | 48 | 0 | Out= Uranquinty to Narrandera (99F) 132kV line, avoid O/L Yanco to Wagga330 (994) on trip of Darlington Point to Wagga330 (63) 330kV line, (Note: Option C on OM521) | Outage | Thermal | NSW
TV_350 | 47.9167 | 0 | Tas to Vic on Basslink upper limit of 350 MW | Outage | Discretionary | Tas
Q_MSTUART1_ZERO_E | 47.5833 | 0 | Direction to zero for Mt Stuart #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_MSTUART2_ZERO_E | 47.5833 | 0 | Direction to zero for Mt Stuart #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_YABULU_ZERO_E | 47.5 | 0 | Direction to zero for Yabulu for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
NC_Q_MPP_2 | 47.3333 | 6.5 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance | Non-Conformance
#TORRB2_P_E | 46.25 | 0 | STSB2.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
NQ_600_DYN_TEST | 45.75 | 0 | NSW to QLD on QNI upper transfer limit of 600 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
#BRAEMAR6_O_E | 45.4167 | 0 | QBRA6B.ENERGY * 1 >= 173 (Wt = 65) | Other | DEFAULT | Direction
Q-HAYSF_MVAR | 44.5 | 0 | Constraint to violate if Reactive power output of Hayman Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-RRSF_MVAR | 44.4167 | 0 | Constraint to violate if Reactive power output of Ross River Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-HAMSF_MVAR | 44.25 | 46 | Constraint to violate if Reactive power output of Hamilton Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-WHTSF_MVAR | 44.25 | 46 | Constraint to violate if Reactive power output of Whitsundays Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-CLRSF_MVAR | 44.1667 | 46 | Constraint to violate if Reactive power output of Clare Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
S_DRYCGT3_ZERO_E | 44 | 0 | Direction to zero for Dry Creek #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#TORRB2_O_L6 | 43.75 | 0 | STSB2.LOWER6SEC * 1 = 10 (Wt = 60) | Other | DEFAULT | Quick
#TORRB2_O_L60 | 43.75 | 0 | STSB2.LOWER60SEC * 1 = 10 (Wt = 60) | Other | DEFAULT | Quick
#TORRB2_O_LR | 43.75 | 0 | STSB2.LOWERREG * 1 = 10 (Wt = 60) | Other | DEFAULT | Quick
#TORRB2_O_R6 | 43.75 | 0 | STSB2.RAISE6SEC * 1 = 15 (Wt = 60) | Other | DEFAULT | Quick
#TORRB2_O_RR | 43.75 | 0 | STSB2.RAISEREG * 1 = 15 (Wt = 60) | Other | DEFAULT | Quick
#TORRB2_P_L5 | 43.75 | 0 | (STSB2.LOWER5MIN + STSB2.LOWERREG) * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_L6 | 43.75 | 0 | STSB2.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_L60 | 43.75 | 0 | STSB2.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_LR | 43.75 | 0 | STSB2.LOWERREG * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_R5 | 43.75 | 0 | (STSB2.RAISE5MIN + STSB2.RAISEREG) * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_R6 | 43.75 | 0 | STSB2.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_R60 | 43.75 | 0 | STSB2.RAISE60SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB2_P_RR | 43.75 | 0 | STSB2.RAISEREG * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
V_YATPSF_FLT_25 | 43.25 | 216.4167 | Limit Yatpool solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#BRAEMAR6_E | 43 | 0 | QBRA6B.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#BRAEMAR7_E | 43 | 0 | QBRA7B.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
S_DRYCGT2_ZERO_E | 43 | 0 | Direction to zero for Dry Creek #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
V>V_X_HWRO12_3 | 42.9167 | 0 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, avoid O/L Yallourn to Rowville No. 5 220 kV line on trip of Yallourn to Rowville No. 6,7 or 8 220 kV lines, feedback, YWG1 on 220 kV, Radial mode | Outage | Thermal | Vic
#SHGEN_O_E | 42.6667 | 0 | NSHL.ENERGY * 1 >= 200 (Wt = 65) | Other | DEFAULT | Direction
N>>NIL_84_88_S | 42.3333 | 0 | Out= NIL, avoid O/L Tamworth to Liddell (84) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL | Thermal | NSW
#TORRB2_O_L5 | 42.1667 | 0 | (STSB2.LOWER5MIN + STSB2.LOWERREG) * 1 = 20 (Wt = 60) | Other | DEFAULT | Quick
S_DRYCGT1_ZERO_E | 42 | 0 | Direction to zero for Dry Creek #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#SHGEN_E | 41.9167 | 0 | NSHL.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
S^NIL_PL_MAX | 41.9167 | 1.5833 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
V^^N_LTYS_1 | 41.5 | 98 | Out = Lower Tumut - Yass (3) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q-RGBSF_MVAR | 41.25 | 0 | Constraint to violate if Reactive power output of Rugby Run Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
#CG1_E | 41 | 0 | NCLG1D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#CG2_E | 41 | 0 | NCLG2D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
S:V_PA_SVC_270 | 40.9167 | 45.5 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
T_CTHLWF_ZERO | 40.5833 | 16.6667 | Wild Cattle Hill Wind Farm upper limit of 0 MW | Outage | Unit Zero | Tas
#TORRB2_O_R5 | 40.5 | 0 | (STSB2.RAISE5MIN + STSB2.RAISEREG) * 1 = 25 (Wt = 60) | Other | DEFAULT | Quick
#TORRB2_O_R60 | 40.5 | 0 | STSB2.RAISE60SEC * 1 = 30 (Wt = 60) | Other | DEFAULT | Quick
N>>N-DP_TIETX_D | 40.5 | 0 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (220 KV to 330 kV) on Kerang-Bendigo trip; Feedback | Outage | Thermal | NSW
Q>NIL_757_758_ECS | 40.5 | 0 | Out= Nil, ECS for managing Mudgeeraba to Terranora (757 or 758) 110kV lines, Summer and Winter ECS ratings selected by SCADA status | NIL | Thermal | Qld
T_BLINK_TV_NGZ | 40.5 | 4.25 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | NIL | Other | Tas
N>N-MOON_945_94K | 40.0833 | 0 | Out= Molong to Orange North (94T) 132kV line, avoid O/L Molong to Wellington (945/1) on trip of Parkes to Wellington (94K) line, Feedback | Outage | Thermal | NSW
N^^V_CNCW_1 | 40.0833 | 113.5833 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V::N_SETB_xxx | 40.0833 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
S_BARKIPS1_ZERO_E | 39.6667 | 0 | Direction to zero for Barker Inlet for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#CG3_E | 39.1667 | 0 | NCLG3D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#URANQ11_E | 39.1667 | 0 | NURQ1U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#URANQ12_E | 39.1667 | 0 | NURQ2U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#URANQ13_E | 39.1667 | 0 | NURQ3U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
#URANQ14_E | 39.1667 | 0 | NURQ4U.ENERGY * 1 >= 166 (Wt = 65) | Other | DEFAULT | Quick
#CG4_E | 39.0833 | 0 | NCLG4D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
S>>X_RBPA+RBTX2_22 | 38.1667 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo-Templers 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
V_BULGANAWF_FLT_0 | 37.75 | 3.75 | Limit Bulgana Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_NQ_SEMI_RAMP_ZERO | 37.4167 | 0 | Ramp North Qld semi-scheduled generators to zero and hold at zero | Outage | Unit Zero | Qld
N>N-WLTX_A | 37.0833 | 0 | Out= one of the Wellington 123/330kV Transformers, avoid O/L on Molong to Orange North (94T) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
N_CRWF1_ZERO | 37 | 0.33333 | Crudine Ridge wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
#TORRB4_P_E | 36.6667 | 0 | STSB4.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#OSB-AG_D_E | 35.9167 | 575.9167 | SNBN1.ENERGY * 1 = 145 (Wt = 755) | Other | DEFAULT | Direction
V::N_ESTN_TBSE_xxx | 35.6667 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
S^NIL_CRK_VCS_STATUS | 35.25 | 0 | Out= Nil, upper limit for Cathedral Rocks WF based on Mt Millar Voltage Control System (VCS) availability, (Note: CRK <=55 MW when VCS OFF; CRK<= 60 MW when VCS ON) | NIL | Voltage Stability | SA
Q>>BCRG_CLWU_BCCP | 35 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
#MAPS2PV1_E | 34.9167 | 928.4167 | SMA21M.ENERGY * 1 <= 10.5 (Wt = 360) | Other | DEFAULT | Quick
#TORRB4_O_L6 | 34.75 | 0 | STSB4.LOWER6SEC * 1 = 10 (Wt = 60) | Other | DEFAULT | Quick
#TORRB4_O_L60 | 34.75 | 0 | STSB4.LOWER60SEC * 1 = 10 (Wt = 60) | Other | DEFAULT | Quick
#TORRB4_O_R6 | 34.75 | 0 | STSB4.RAISE6SEC * 1 = 5 (Wt = 60) | Other | DEFAULT | Quick
#TORRB4_P_L5 | 34.75 | 0 | (STSB4.LOWER5MIN + STSB4.LOWERREG) * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_L6 | 34.75 | 0 | STSB4.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_L60 | 34.75 | 0 | STSB4.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_LR | 34.75 | 0 | STSB4.LOWERREG * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_R5 | 34.75 | 0 | (STSB4.RAISE5MIN + STSB4.RAISEREG) * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_R6 | 34.75 | 0 | STSB4.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_R60 | 34.75 | 0 | STSB4.RAISE60SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#TORRB4_P_RR | 34.75 | 0 | STSB4.RAISEREG * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
NC_Q_MPP_1 | 34.75 | 1 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_W/HOE#2 | 34.6667 | 0 | Non Conformance Constraint for Wivenhoe No 2 Power Station | Other | Non-Conformance | Non-Conformance
#TORRB4_O_R5 | 34.5 | 0 | (STSB4.RAISE5MIN + STSB4.RAISEREG) * 1 = 25 (Wt = 60) | Other | DEFAULT | Quick
QNTE_ROC | 34.5 | 60.0833 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
#TORRB4_O_LR | 34.1667 | 0 | STSB4.LOWERREG * 1 = 10 (Wt = 60) | Other | DEFAULT | Quick
NRM_QLD1_NSW1 | 34 | 100.0833 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
T^V_NIL_9 | 33.4167 | 9.1667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
N^^Q_TW_330_BUS3_B1 | 33.25 | 31.5833 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
S>>CNRB+BRTW_02 | 33 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Claire North 132 to Brinkworth 132 kV line on trip of Mokota-Robertstown 275kV line(this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
#SNOWYP_P_E | 32.8333 | 0 | NLTS3.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
S>>X_RBTU+RBTX_14 | 32.75 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
Q_MARYRSF1_10 | 32.5833 | 4.6667 | Maryrorough Solar Farm upper limit of 10 MW | Outage | Discretionary | Qld
NQTE_ROC | 32.4167 | 63.4167 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
S>>NIL_RBTU_WTTP | 32.3333 | 0.5 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | NIL | Thermal | SA
#PAREPW1_E | 32.0833 | 0 | SDAP1P.ENERGY * 1 <= 210 (Wt = 360) | Other | DEFAULT | Quick
S_AGLHAL_P_ZERO_E | 32.0833 | 0 | Direction to zero for Hallett GT for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
Q_KEP-HYB_30MW | 32 | 0 | Kennedy Energy Park upper limit of 30MW | Outage | Discretionary | Qld
V_GANWRSF_FLT_30 | 31.9167 | 79.9167 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S_SNUG1_ZERO_E | 31.75 | 0 | Direction to zero for Snuggery for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#DDPS1_E | 31.5833 | 0 | QBRA8D.ENERGY * 1 <= 350 (Wt = 29) | Other | DEFAULT | Quick
Q-DAYSF_MVAR | 31.5 | 0 | Constraint to violate if Reactive power output of Daydream Solar farm is greater than +/- 10Mvar at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
S>>PARB_RBTU_WEWT | 31.5 | 56.3333 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
#TORRB4_O_R60 | 31.4167 | 0 | STSB4.RAISE60SEC * 1 = 30 (Wt = 60) | Other | DEFAULT | Quick
N^^V_NIL_ARWBBA | 31.3333 | 22 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
S_POR01_ZERO_E | 31.25 | 0 | Direction to zero for Port Lincoln #1 and #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_POR03_ZERO_E | 31.25 | 0 | Direction to zero for Port Lincoln #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#ER02_O_E | 31.0833 | 0 | NEPS2.ENERGY * 1 >= 500 (Wt = 65) | Other | DEFAULT | Direction
NC_Q_W/HOE#1 | 31.0833 | 0.083333 | Non Conformance Constraint for Wivenhoe No 1 Power Station | Other | Non-Conformance | Non-Conformance
V_BANNERTSF_FLT_45 | 30.9167 | 98 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#ER01_O_E | 30.5833 | 0 | NEPS1.ENERGY * 1 >= 500 (Wt = 65) | Other | DEFAULT | Direction
#MORTLK12_O_E | 30.5833 | 0 | VM0P2O.ENERGY * 1 >= 275 (Wt = 65) | Other | DEFAULT | Direction
#ER04_O_E | 30.5 | 0 | NEPS4.ENERGY * 1 >= 500 (Wt = 65) | Other | DEFAULT | Direction
Q_STR_KBWF_N-2 | 30.5 | 0 | Out = Nil, Loss of 858 and 857 declared credible. Limit Kaban WF to 1% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7, Kar>= 2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
#ER03_O_E | 30.3333 | 0 | NEPS3.ENERGY * 1 >= 500 (Wt = 65) | Other | DEFAULT | Direction
#TORRB4_O_RR | 30.3333 | 0 | STSB4.RAISEREG * 1 = 15 (Wt = 60) | Other | DEFAULT | Quick
V_BANSF_BBD_80 | 30.3333 | 86.0833 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
S_QPS1_ZERO_E | 30.25 | 0 | Direction to zero for Quarantine #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_QPS2_ZERO_E | 30.25 | 0 | Direction to zero for Quarantine #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_QPS3_ZERO_E | 30.25 | 0 | Direction to zero for Quarantine #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_QPS4_ZERO_E | 30.25 | 0 | Direction to zero for Quarantine #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#SA1_E_20220916 | 29.75 | 0 | Multiple SA1 LHS <= 226 (Wt = 35) | Other | DEFAULT | Quick
NC_V_MCKAY1 | 29.25 | 0 | Non Conformance Constraint for McKay Creek & Bogong Power Stations (aggregated unit) | Other | Non-Conformance | Non-Conformance
S>>CNRB_BWPA_HUWT | 29.25 | 0.41667 | Out= Canowie-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
NC_N_SUNTPSF1 | 28.9167 | 0 | Non Conformance Constraint for SUNTOP SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_N_CG4 | 28.75 | 0 | Non Conformance Constraint for Colongra 4 Power Station | Other | Non-Conformance | Non-Conformance
Q-X_STR_7C8C_HAUSF | 28.75 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Haughton Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
#ER01_P_E | 28.25 | 0 | NEPS1.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Direction
#ER02_P_E | 28.25 | 0 | NEPS2.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Direction
#ER04_P_E | 28.25 | 0 | NEPS4.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Direction
#ER03_P_E | 28.1667 | 0 | NEPS3.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Direction
V::N_BYPASS_HW_SY_xxx | 28.1667 | 12.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Transient Stability | Vic
S>>X_RBPA+RBTX2_16 | 28 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
NC_V_DARTM1 | 27.9167 | 0 | Non Conformance Constraint for Dartmouth Power Station | Other | Non-Conformance | Non-Conformance
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 27.9167 | 34.25 | Out= Nil, avoid overloading Mudgeeraba to Terranora (757) 110kV line, swamped out when ECS is in service | NIL | Thermal | Qld
VS_050_DYN | 27.9167 | 12.75 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
N>N_968_969_NIL | 27.5 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_HASF_6 | 27.3333 | 0 | No limit to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
V_KIAMSF_FLT_50 | 27.3333 | 211.8333 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_WRWSF_055 | 27.0833 | 43.0833 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | System Strength | NSW
#MSTUART1_O_E | 27.0833 | 0 | QMSP1.ENERGY * 1 >= 138 (Wt = 65) | Other | DEFAULT | Direction
V>>NIL_ELML_BAML2 | 26.6667 | 0 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL | Thermal | Vic
#MUWAWF2_E | 26.5833 | 0 | VMRT2M.ENERGY * 1 <= 150 (Wt = 360) | Other | DEFAULT | Quick
SVML_FLT_130 | 26.5 | 19.1667 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
S:V_XPAVC_310 | 26.4167 | 60.25 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
T_GO3_100 | 26.25 | 0 | Discretionary 100 MW upper limit on Gordon unit 3. DS only. | Outage | Discretionary | Tas
N_BANGOWF1_ZERO | 26 | 0 | Bango 973 wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>>CNRB_TWPA_TPRS | 26 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
#TORRB4_O_L5 | 25.8333 | 0 | (STSB4.LOWER5MIN + STSB4.LOWERREG) * 1 = 20 (Wt = 60) | Other | DEFAULT | Quick
NC_S_SNUG1 | 25.8333 | 0.41667 | Non Conformance Constraint for Snuggery 1 Power Station | Other | Non-Conformance | Non-Conformance
Q>>NIL_BCCP_RGLC | 25.8333 | 21.3333 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
#MOORAWF1_E | 25.75 | 46.4167 | VELT2M.ENERGY * 1 <= 305 (Wt = 360) | Other | DEFAULT | Quick
#BRAEMAR7_O_E | 25.4167 | 0 | QBRA7B.ENERGY * 1 >= 80 (Wt = 65) | Other | DEFAULT | Direction
S>>CNRB_BWPA_RHBR-T | 25.4167 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
#SHPUMP_P_E | 25.3333 | 0 | NSHP1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
NC_N_TUMUT3 | 25.0833 | 0 | Non Conformance Constraint for Lower Tumut Power Station | Other | Non-Conformance | Non-Conformance
NSA_Q_BARCALDN | 25 | 23.25 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
S>>X_RBTU+RBTX_13 | 25 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
#BARKIPS1_O_E | 24.9167 | 0 | SBPS1B.ENERGY * 1 >= 100 (Wt = 65) | Other | DEFAULT | Direction
#DDPS1_O_E | 24.9167 | 0 | QBRA8D.ENERGY * 1 >= 620 (Wt = 65) | Other | DEFAULT | Direction
V>>V_NIL_24 | 24.8333 | 6.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
NC_S_POR03 | 24.5833 | 0 | Non Conformance Constraint for Port Lincoln unit 3 | Other | Non-Conformance | Non-Conformance
V^T_NIL_9 | 24.4167 | 6.3333 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL | Voltage Stability | Vic
#WSTWYSF1_E | 24.3333 | 0 | NWGJ3W.ENERGY * 1 <= 30 (Wt = 360) | Other | DEFAULT | Quick
V_MACWF_FLT_0 | 24.1667 | 72.4167 | Limit Macarthur Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>>RBTX_TWPA_TPRS | 24.0833 | 0 | Out= one Robertstown 275/132kV transforme, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
NC_S_POR01 | 24 | 0 | Non Conformance Constraint for Port Lincoln Power Station | Other | Non-Conformance | Non-Conformance
#JLB03_O_E | 23.8333 | 0 | VJLGB3.ENERGY * 1 >= 68 (Wt = 65) | Other | DEFAULT | Direction
S_ISLE_CANUNDA_10 | 23.75 | 0 | Discretionary upper limit on Canunda windfarm<=10 MW & No. in-service wind turbines for canunda at 5 Turbines.(Note otherwise,Canunda will be constrained to 0 MW) | Outage | Discretionary | SA
T>T_X_LIPM_TWO_D | 23.75 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L Tungatinah to Meadowbank Tee 1 on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
V::N_NIL_xxx | 23.75 | 44.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL | Transient Stability | Vic
#MSTUART2_O_E | 23.5833 | 0 | QMSP2.ENERGY * 1 >= 135 (Wt = 65) | Other | DEFAULT | Direction
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 23.5 | 31.0833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Thermal | Vic
V>>V_NIL_23 | 23.4167 | 10.5 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
#MORTLK11_O_E | 23.25 | 0 | VM0P1O.ENERGY * 1 >= 275 (Wt = 65) | Other | DEFAULT | Direction
S>>CNRB+BRTW_03 | 23.25 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Blyth West-Munno Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S_SNAPPER1_ZERO_E | 23.25 | 0 | Direction to zero for Snapper Point for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
V_S_HEYWOOD_UFLS | 23.25 | 110 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC. Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
NC_Q_MSTUART2 | 22.9167 | 0 | Non Conformance Constraint for Mt Stuart 2 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_DDSM1 | 22.6667 | 72.5833 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
#STAN-4_E | 22.5833 | 0 | QSTN4.ENERGY * 1 <= 220 (Wt = 29) | Other | DEFAULT | Quick
N>>994_99F_63 | 22.5833 | 0 | Out= Yanco to Wagga (994) 132kV line, avoid O/L Yanco to Uranquinty (99F) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,[Note: assumed X5 trip scheme disarmed, Wagga-Darlington Pt 132kV Solid)] | Outage | Thermal | NSW
#JLB01_O_E | 22.3333 | 0 | VJLGB1.ENERGY * 1 >= 78 (Wt = 65) | Other | DEFAULT | Direction
NC_V_VPGS3 | 22.25 | 0 | Non Conformance Constraint for Valley Power - unit 3 | Other | Non-Conformance | Non-Conformance
NC_V_VPGS4 | 22.25 | 0 | Non Conformance Constraint for Valley Power - unit 4 | Other | Non-Conformance | Non-Conformance
NC_V_VPGS5 | 22.25 | 0 | Non Conformance Constraint for Valley Power - unit 5 | Other | Non-Conformance | Non-Conformance
Q_KWF1_ZERO | 22.25 | 0 | Kaban Wind Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V::S_2SE+PAVC_MAXG | 22.1667 | 0.16667 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
NC_V_VPGS2 | 22 | 0 | Non Conformance Constraint for Valley Power - unit 2 | Other | Non-Conformance | Non-Conformance
T_REECE2_100 | 21.9167 | 0 | Discretionary 100 MW upper limit on Reece unit 2 | Outage | Discretionary | Tas
N_SUNRSF1_ZERO | 21.9167 | 81.75 | Sunraysia 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
NC_V_VPGS6 | 21.75 | 0 | Non Conformance Constraint for Valley Power - unit 6 | Other | Non-Conformance | Non-Conformance
V^^N_UTRV_1 | 21.5833 | 1.4167 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
NC_Q_YABULU | 21.25 | 0 | Non Conformance Constraint for Yabulu Power Station | Other | Non-Conformance | Non-Conformance
NC_S_DRYCGT3 | 21.25 | 0 | Non Conformance Constraint for Dry Creek 3 Power Station | Other | Non-Conformance | Non-Conformance
N::N_SDUT_2 | 21.1667 | 42.75 | Out = Upper Tumut-Stockdill (1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
NC_N_CG2 | 21.1667 | 0.083333 | Non Conformance Constraint for Colongra 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_DRYCGT2 | 21.1667 | 0 | Non Conformance Constraint for Dry Creek 2 Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_KBWF_4 | 21.1667 | 0 | Limit Kaban Solar Farm to 60% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG) with Haughton syncon ON, (1% if Haughton syncon OFF) Zero otherwise. | Outage | System Strength | Qld
N_STWF1_ZERO | 21.1667 | 25.3333 | Silverton wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
#JLB02_O_E | 21 | 0 | VJLGB2.ENERGY * 1 >= 78 (Wt = 65) | Other | DEFAULT | Direction
Q_KEP-HYB_15MW | 20.9167 | 0 | Kennedy Energy Park upper limit of 15MW | Outage | Discretionary | Qld
T>T_X_LIPM_TWO_C | 20.8333 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Thermal | Tas
V_S_NIL_ROCOF | 20.75 | 326.9167 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
#DRYCGT3_D_E | 20.6667 | 0.66667 | SDCA3.ENERGY * 1 = 5 (Wt = 755) | Other | DEFAULT | Direction
S>>X_RBTU+RBTX_10 | 20.6667 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Templers- Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
Q_STR_7C2K_HAYSF_7 | 20.5833 | 0 | Limit to Hayman Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V^^V_NIL_SWVIC | 20.5833 | 0 | Out = Nil, manage flow towards Moorabool across Haunted Gully to Moorabool and Mortlake to Moorabool 500kV lines to avoid voltage instability for the loss of Haunted Gully to Moorabool 500kV line and both APD potlines | NIL | Voltage Stability | Vic
#VPGS6_O_E | 20.4167 | 0 | VLYP012.ENERGY * 1 >= 55 (Wt = 65) | Other | DEFAULT | Direction
NC_S_QPS2 | 20.3333 | 0 | Non Conformance Constraint for Quarantine QPS2 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_QPS4 | 20.3333 | 0.083333 | Non Conformance Constraint for Quarantine QPS4 Power Station | Other | Non-Conformance | Non-Conformance
N>NIL_COTX_LV | 20.25 | 14.8333 | Out= Nil, avoid O/L either Corowa 22kV/132kV Transformer on NIL trip, Feedback. NOTE: System normal is only one transformer in service. 90% of Rating and no operating margin is used as per Essential Energy advice. | NIL | Thermal | NSW
S>>CNRB_BWPA_WTTP | 20.1667 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_RBTU_WEWT | 20.1667 | 5.8333 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
#JLA01_O_E | 19.8333 | 0 | VJLGA1.ENERGY * 1 >= 54 (Wt = 65) | Other | DEFAULT | Direction
NC_Q_MSTUART1 | 19.8333 | 0 | Non Conformance Constraint for Mt Stuart 1 Power Station | Other | Non-Conformance | Non-Conformance
S>>PARB_RBTU_WTTP | 19.6667 | 31.5833 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
NC_S_DRYCGT1 | 19.5833 | 0 | Non Conformance Constraint for Dry Creek 1 Power Station | Other | Non-Conformance | Non-Conformance
#JLA04_O_E | 19.5 | 0 | VJLGA4.ENERGY * 1 >= 54 (Wt = 65) | Other | DEFAULT | Direction
Q-KIDSF_MVAR | 19.5 | 0 | Constraint to violate if Reactive power output of Kidston Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q>>CPST_CLWU_RGLC | 19.5 | 101.9167 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q_STR_7C2K_KIDSF_7 | 19.5 | 0 | Limit to Kidston Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V>>V_NIL_5 | 19.3333 | 1 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Thermal | Vic
#TUMUT3_O_E | 19.25 | 0 | NLTS8.ENERGY * 1 >= 120 (Wt = 65) | Other | DEFAULT | Direction
#CPSA_E | 19.1667 | 0 | QCND1C.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
N>N-MOON_947_72 | 19.1667 | 0 | Out= Molong to Orange North (94T) 132kV line, avoid O/L Wellington to Orange North (947) 132kV line on trip of Wellington to Mt Piper (72) 330kV line, Feedback | Outage | Thermal | NSW
V_WEMENSF_FLT_45 | 19.0833 | 25 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#PPCCGT_D_E | 19 | 2479.75 | SPPT.ENERGY * 1 = 175 (Wt = 755) | Other | DEFAULT | Direction
Q_STR_7C2K_RRSF_7 | 19 | 0 | Limit to Ross River Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S-MTM_0 | 19 | 0 | Discretionary upper limit for Mt Millar windfarm generation of 0 MW | Outage | Unit Zero | SA
#VPGS3_O_E | 18.6667 | 0 | VLYP09.ENERGY * 1 >= 58 (Wt = 65) | Other | DEFAULT | Direction
#TORRB4_O_E | 18.5833 | 0 | STSB4.ENERGY * 1 >= 70 (Wt = 755) | Other | DEFAULT | Direction
Q_STR_7C2K_RUGSF_7 | 18.5 | 0 | Limit to Rugby Run Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>MKRB_BWMP_HUWT | 18.25 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
#W/HOE#1_O_E | 18.1667 | 0 | QWIV1.ENERGY * 1 >= 165 (Wt = 65) | Other | DEFAULT | Direction
Q_YARANSF1_37 | 17.8333 | 2.8333 | Yarranlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
#BARCALDN_O_E | 17.75 | 0 | QBCG.ENERGY * 1 >= 37 (Wt = 65) | Other | DEFAULT | Direction
N^^V_NIL_1 | 17.75 | 114.8333 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
NC_N_SITHE01 | 17.6667 | 0 | Non Conformance Constraint for Smithfield Energy Facility | Other | Non-Conformance | Non-Conformance
S_WATERLWF_RB | 17.5833 | 6.75 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
S>>BWMP_DVBR_RHBG-T | 17.5 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBPA+RBTX2_23 | 17.5 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
#VIC1_E_20200811 | 17.4167 | 745.0833 | Multiple VIC1 LHS <= 300 (Wt = 360) | Other | DEFAULT | Quick
NC_V_NPS | 17.4167 | 0.25 | Non Conformance Constraint for Newport Power Station | Other | Non-Conformance | Non-Conformance
#DRYCGT2_D_E | 17.0833 | 6.6667 | SDCA2.ENERGY * 1 = 5 (Wt = 755) | Other | DEFAULT | Direction
#MCKAY1_O_E | 17 | 0 | VMKP1.ENERGY * 1 >= 300 (Wt = 65) | Other | DEFAULT | Direction
NC_Q_BARCALDN | 17 | 0 | Non Conformance Constraint for Barcaldine Power Station | Other | Non-Conformance | Non-Conformance
N^^Q_ARTW_B1 | 17 | 40.8333 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
Q-X_STR_7C8C_MEWF | 16.9167 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Mt Emerald windfarm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_7 | 16.6667 | 0 | Limit to Daydream Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
#VPGS5_O_E | 16.5833 | 0 | VLYP011.ENERGY * 1 >= 55 (Wt = 65) | Other | DEFAULT | Direction
V^SML_BUDP_3 | 16.5833 | 88.8333 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
N>>N-NIL_94K_3 | 16.4167 | 0 | Out= Nil, avoid O/L on Suntop Solar Farm to Wellington Suntop Tee 94K/3 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
S>>RBTU_RBPA_WEWT | 16.25 | 3.25 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
T_GO1_100 | 16.0833 | 0 | Discretionary 100 MW upper limit on Gordon unit 1 | Outage | Discretionary | Tas
Q_STR_7C2K_CLRSF_7 | 16 | 0 | Limit to Clare Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_COLSF_7 | 15.9167 | 0 | Limit to Collinsville Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
NQ_700_DYN_TEST | 15.5833 | 0 | NSW to QLD on QNI upper transfer limit of 700 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
V>V_X_HWRO12_5 | 15.4167 | 0 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, avoid O/L Yallourn to Rowville No. 6,7 or 8 220 kV lines on trip of Yallourn to Rowville No. 6, 7 or 8 220 kV lines, feedback, YWG1 on 220 kV, Radial mode | Outage | Thermal | Vic
#JLA02_O_E | 15.3333 | 0 | VJLGA2.ENERGY * 1 >= 54 (Wt = 65) | Other | DEFAULT | Direction
S>NIL_RBMWP3_RBNW1 | 15.1667 | 0 | Out= Nil, avoid O/L Robertstown-North West Bend #1 132kV line on trip of Robertstown-Morgan Pipeline 3-Morgan Pipeline 2-Morgan Pipeline 1-North West Bend 132kV #2 line, Feedback | NIL | Thermal | SA
Q_STR_7C2K_HAMSF_7 | 15.1667 | 0 | Limit to Hamilton Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
#QPS1_O_E | 15.0833 | 0 | SQPS1.ENERGY * 1 >= 29 (Wt = 65) | Other | DEFAULT | Direction
NC_V_JLA01 | 15.0833 | 0.083333 | Non Conformance Constraint for Jeeralang A - 01 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLB01 | 15 | 0.33333 | Non Conformance Constraint for Jeeralang B - 01 Power Station | Other | Non-Conformance | Non-Conformance
S_LADBROK1_ZERO_E | 15 | 0 | Direction to zero for Ladbroke Grove #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_TORRB4_ZERO_E | 15 | 0 | Direction to zero for Torrens Island B #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
#QPS3_O_E | 14.9167 | 0 | SQPS3.ENERGY * 1 >= 29 (Wt = 65) | Other | DEFAULT | Direction
#VPGS4_O_E | 14.9167 | 0 | VLYP010.ENERGY * 1 >= 55 (Wt = 65) | Other | DEFAULT | Direction
NC_V_JLB02 | 14.9167 | 0 | Non Conformance Constraint for Jeeralang B - 02 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLB03 | 14.9167 | 0 | Non Conformance Constraint for Jeeralang B - 03 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLA02 | 14.8333 | 0.083333 | Non Conformance Constraint for Jeeralang A - 02 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLA04 | 14.8333 | 0 | Non Conformance Constraint for Jeeralang A - 04 Power Station | Other | Non-Conformance | Non-Conformance
V::N_ESTN_TBSE_O1 | 14.8333 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
#VPGS2_O_E | 14.6667 | 0 | VLYP08.ENERGY * 1 >= 58 (Wt = 65) | Other | DEFAULT | Direction
V^S_HYCP | 14.5833 | 0 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL | Voltage Stability | Vic
#CALL_B_1_E | 14.5 | 0 | QCAB1.ENERGY * 1 <= 335 (Wt = 35) | Other | DEFAULT | Quick
Q>>PWSP_WOSP_PWSP | 14.5 | 0 | Out= Palmwoods to South Pine (808) line, avoid O/L on parallel 110kV lines between Palmwoods and South Pine(745 /746) on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
V>S_460 | 14.4167 | 4.0833 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage | Thermal | Vic
#QPS5_P_E | 14.1667 | 0 | SQPS5Q.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#ER04_E | 14.0833 | 0 | NEPS4.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Quick
#QPS5_O_L6 | 14.0833 | 0 | SQPS5Q.LOWER6SEC * 1 = 12 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_O_L60 | 14.0833 | 0 | SQPS5Q.LOWER60SEC * 1 = 25 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_O_LR | 14.0833 | 0 | SQPS5Q.LOWERREG * 1 = 25 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_O_R6 | 14.0833 | 0 | SQPS5Q.RAISE6SEC * 1 = 12 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_O_R60 | 14.0833 | 0 | SQPS5Q.RAISE60SEC * 1 = 18 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_O_RR | 14.0833 | 0 | SQPS5Q.RAISEREG * 1 = 25 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_P_L5 | 14.0833 | 0 | (SQPS5Q.LOWER5MIN + SQPS5Q.LOWERREG) * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_L6 | 14.0833 | 0 | SQPS5Q.LOWER6SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_L60 | 14.0833 | 0 | SQPS5Q.LOWER60SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_LR | 14.0833 | 0 | SQPS5Q.LOWERREG * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_R5 | 14.0833 | 0 | (SQPS5Q.RAISE5MIN + SQPS5Q.RAISEREG) * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_R6 | 14.0833 | 0 | SQPS5Q.RAISE6SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_R60 | 14.0833 | 0 | SQPS5Q.RAISE60SEC * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
#QPS5_P_RR | 14.0833 | 0 | SQPS5Q.RAISEREG * 1 <= 0 (Wt = 12) | Other | DEFAULT | Quick
Q>>CLWU_BCCP_BCRG | 14 | 0 | Out = Calvale to Wurdong (871), avoid O/L Bouldercombe to Raglan (811) or Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
T_GO2_100 | 14 | 0 | Discretionary 100 MW upper limit on Gordon unit 2. DS only. | Outage | Discretionary | Tas
#ER03_E | 13.9167 | 0 | NEPS3.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Quick
N^^Q_ARDM_B1 | 13.9167 | 9.5 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
#ER02_E | 13.8333 | 0 | NEPS2.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Quick
#PUMP1_O_E | 13.8333 | 0 | QWIP1.ENERGY * 1 >= 243 (Wt = 65) | Other | DEFAULT | Direction
#QPS5_O_R5 | 13.75 | 0 | (SQPS5Q.RAISE5MIN + SQPS5Q.RAISEREG) * 1 = 50 (Wt = 60) | Other | DEFAULT | Quick
#QPS5_O_E | 13.6667 | 0 | SQPS5Q.ENERGY * 1 >= 85 (Wt = 755) | Other | DEFAULT | Direction
NC_N_SHGEN | 13.6667 | 0 | Non Conformance Constraint for Shoalhaven Power Station | Other | Non-Conformance | Non-Conformance
#ER01_E | 13.5833 | 0 | NEPS1.ENERGY * 1 <= 210 (Wt = 29) | Other | DEFAULT | Quick
NQ_600_TEST | 13.5 | 0 | NSW to Qld on QNI upper transfer limit of 600 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
Q_STR_7C2K_SMSF_7 | 13.5 | 0 | Limit to Sun Metals Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>PATW_BWPA_TPRS | 13.5 | 5.4167 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N_WRWSF_125 | 13.4167 | 0 | White Rock wind farm and White Rock solar farm upper limit of 125 MW | Outage | System Strength | NSW
T>T_NIL_BL_IMP_7C | 13.4167 | 1 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
V_ELAINEWF_ZERO | 13.4167 | 2.25 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
Q_STR_7C2K_WHTSF_7 | 13.3333 | 0 | Limit to Whitsunday Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V>V_NIL_8 | 13.3333 | 21.9167 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
NRM_SA1_VIC1 | 13.25 | 0 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue | Negative Residue
#SNAPPER1_O_E | 13.1667 | 0 | SNPT1S.ENERGY * 1 >= 150 (Wt = 65) | Other | DEFAULT | Direction
T_V_NIL_BL1 | 13.0833 | 6.9167 | Out=Nil, Basslink no go zone limits Tas to Vic. Limit Basslink upper limit to 125 MW on 1st DI out of no go zone. i.e. BL <= 125 MW | NIL | Other | Tas
T_FARC1_2 | 13 | 1.25 | Out=Farrell - Reece 1 220KV line. Discretionary 144 MW limit on Reece 2 + Granville Harbour WF | Outage | Discretionary | Tas
V_MC_SH_WF_600 | 13 | 0 | Limit the total MW from Macarthur and Stockyard Hill WF <= 600 MW to maintain generation contingency size in Victoria. | Outage | Discretionary | Vic
T>T_NIL_BL_IMP_7CC | 12.9167 | 1.8333 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
Q_YARANSF1_37MW_N-1 | 12.75 | 0.83333 | Limit Yarrenlea Solar Farm to 37 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip, Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
N>NIL_94B | 12.5 | 5.4167 | Out= Nil, avoid O/L Beryl to Wellington 132 kV (94B/1) on nil trip, Feedback. Metering at Wellington is used | NIL | Thermal | NSW
S^CNRB+BRTW_SA_NORTH | 12.5 | 0 | Out = Canowie-Robertstown 275kV line+Brinkworth-Templers West + RB SVC, Manage voltage collapse in northern SA for the trip of one 275kV line between Davenport-Para or Davenport-Tungkillo. | Outage | Voltage Stability | SA
N_WRWSF_ZERO | 12.4167 | 1.0833 | White Rock wind farm and White Rock solar farm upper limit of zero MW | Outage | Discretionary | NSW
#DARTM1_O_E | 12.3333 | 0 | VDPS.ENERGY * 1 >= 175 (Wt = 65) | Other | DEFAULT | Direction
#VPGS3_E | 12.3333 | 0 | VLYP09.ENERGY * 1 >= 59 (Wt = 35) | Other | DEFAULT | Quick
VTBL_ROC | 12.3333 | 16.6667 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
#LNGS1_E | 12.25 | 0 | VAT21L.ENERGY * 1 >= 166 (Wt = 35) | Other | DEFAULT | Quick
#VPGS6_E | 12.25 | 0 | VLYP012.ENERGY * 1 >= 49 (Wt = 35) | Other | DEFAULT | Quick
#AGLHAL_O_E | 12.1667 | 0 | SHPS1.ENERGY * 1 >= 122 (Wt = 65) | Other | DEFAULT | Direction
V::N_HYSE_xxx | 12.1667 | 3.4167 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
NC_V_MORTLK11 | 11.9167 | 0 | Non Conformance Constraint for Mortlake GT unit 1 | Other | Non-Conformance | Non-Conformance
SA_ISLE_HPR_LOW_SOC | 11.9167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is below 30% | Outage | Other | SA
Q:N_1078 | 11.9167 | 3.25 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
V>S_460_DYN | 11.75 | 1.8333 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | Vic
Q-KEP_MVAR | 11.6667 | 0 | Constraint to violate if Reactive power output of Kennedy Solar farm or Kennedy Wind farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
S:VS_PA_SVC_420 | 11.6667 | 2.3333 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
#DRYCGT1_O_E | 11.5833 | 0 | SDCA1.ENERGY * 1 >= 47 (Wt = 65) | Other | DEFAULT | Direction
NC_V_MORTLK12 | 11.5833 | 0.083333 | Non Conformance Constraint for Mortlake GT unit 2 | Other | Non-Conformance | Non-Conformance
#DRYCGT3_O_E | 11.5 | 0 | SDCA3.ENERGY * 1 >= 48 (Wt = 65) | Other | DEFAULT | Direction
#QPS5_O_L5 | 11.5 | 0 | (SQPS5Q.LOWER5MIN + SQPS5Q.LOWERREG) * 1 = 39 (Wt = 60) | Other | DEFAULT | Quick
N>>N-964_DC | 11.3333 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage | Thermal | NSW
V_OWF_TGTSNRBHTN_30 | 11.3333 | 9.9167 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
#LNGS2_E | 11.25 | 0 | VAT22L.ENERGY * 1 >= 166 (Wt = 35) | Other | DEFAULT | Quick
Q-COLSF_MVAR | 11.25 | 45.9167 | Constraint to violate if Reactive power output of Collinsville Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
#SMCSF1_E | 11.1667 | 6.75 | QTZS1S.ENERGY * 1 <= 121 (Wt = 360) | Other | DEFAULT | Quick
Q>>CPST_CLWU_BCST | 11.0833 | 33.8333 | Out = 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Stanwell to Bouldercombe 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
#STAN-3_E | 11 | 0 | QSTN3.ENERGY * 1 <= 350 (Wt = 35) | Other | DEFAULT | Quick
N>>NIL_88_84_S | 11 | 0 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | NIL | Thermal | NSW
#SITHE01_P_E | 10.9167 | 0 | NSYW1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
Q_EMERASF1_ZERO | 10.75 | 4.5833 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q>NIL_TV66 | 10.6667 | 24.5 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Thermal | Qld
#DRYCGT2_O_E | 10.5833 | 0 | SDCA2.ENERGY * 1 >= 40 (Wt = 65) | Other | DEFAULT | Direction
#PUMP1_P_E | 10.5833 | 0 | QWIP1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
N>Q-TEMU_757_758 | 10.5833 | 0 | Out= 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line, avoid O/L on remaining T174 Terranora to H4 Mudgeeraba line (758 or 757), Feedback | Outage | Thermal | NSW
S>NIL_BWMP_RHBR-T | 10.5833 | 0.33333 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
S_DV-RB2_070 | 10.5833 | 0 | Discretionary upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 70 MW | Outage | Discretionary | SA
T_BLINK_VT_BID | 10.5833 | 0 | Out = Nil, limit Basslink to 0 MW if Basslink bid zero. Constraint to swamp otherwise. | NIL | Other | Tas
V>>N_NIL_65 | 10.3333 | 5.6667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
NC_Q_HAYMSF1 | 10.25 | 0 | Non Conformance Constraint for HAYMAN SOLAR FARM | Other | Non-Conformance | Non-Conformance
N_FINLYSF_FLT_50 | 10.25 | 11 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_WRWF1_ZERO | 10.1667 | 0 | White Rock WF upper limit of 0 MW and all turbines disconnected | Outage | Unit Zero | NSW
S:V_550_HY_TEST_DYN | 10.1667 | 43.9167 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
#GUTHEGA_E | 10.0833 | 0 | NGUT8.ENERGY * 1 >= 62 (Wt = 35) | Other | DEFAULT | Quick
#STAN-2_E | 10.0833 | 0 | QSTN2.ENERGY * 1 <= 335 (Wt = 35) | Other | DEFAULT | Quick
S:VS_PA_SVC_570 | 10.0833 | 12.4167 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | Oscillatory Stability | SA
S:VS_PA_SVC_620 | 9.9167 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage | Oscillatory Stability | SA
S>NIL_BWMP_HUWT | 9.9167 | 8 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
S>>CNRB_MKRB_WEMWP4 | 9.8333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
T>>T_NIL_BL_EXP_7C | 9.8333 | 6.5833 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
#QBYNBG1_E | 9.75 | 0 | NQBB1Q.ENERGY * 1 <= 10 (Wt = 360) | Other | DEFAULT | Quick
Q_STR_7C2K_MEWF_80 | 9.75 | 0 | Limit to Mt Emerald Wind Farm to 80% if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,Kar=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S>HUWT_NIL_STBG-T | 9.75 | 0.25 | Out= Hummocks-Waterloo 132kV line, avoid O/L Snowtown-Bungama T 132kV line on Nil trip, Feedback | NIL | Thermal | SA
N_SILVERTWF_FLT_119 | 9.6667 | 0 | Limit Silverton Wind Farm upper limit to 119 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
S>>V_NIL_DVBG_STBG | 9.6667 | 0.41667 | Out= Nil, avoid O/L Snowtown - Bungama 132kV on trip of Davenport - Bungama 275kV line, Feedback | NIL | Thermal | SA
SA_ISLE_HPR_HIGH_SOC | 9.6667 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is above 70% | Outage | Other | SA
V_YATPSF_FLT_49 | 9.6667 | 0 | Limit Yatpool solar Farm upper limit to 49 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#PUMP2_O_E | 9.5833 | 0 | QWIP2.ENERGY * 1 >= 243 (Wt = 65) | Other | DEFAULT | Direction
V_T_NIL_BL1 | 9.5833 | 12.0833 | Out=Nil, Basslink no go zone limits Vic to Tas. Limit Basslink lower limit to -125 MW on 1st DI out of no go zone. i.e. BL >= -125 MW | NIL | Other | Vic
#TARONG#3_E | 9.5 | 0 | QTRN3.ENERGY * 1 <= 330 (Wt = 35) | Other | DEFAULT | Quick
V_KARADSF_FLT_54 | 9.5 | 0 | Limit Karadoc solar Farm upper limit to 54 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#STAN-1_E | 9.4167 | 0 | QSTN1.ENERGY * 1 <= 350 (Wt = 35) | Other | DEFAULT | Quick
#BRAEMAR3_P_E | 9.3333 | 0 | QBRA3.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
S-MWPS2-PV_0 | 9.3333 | 1.1667 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW | Outage | Unit Zero | SA
#LYA1_E | 9.25 | 0 | VLYP1.ENERGY * 1 <= 540 (Wt = 35) | Other | DEFAULT | Quick
S>HUWT_BWPA_RHBR-T | 9.25 | 0 | Out= Hummocks-Waterloo 132kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
#CPSA_O_E | 9.1667 | 0 | QCND1C.ENERGY * 1 >= 45 (Wt = 65) | Other | DEFAULT | Direction
#MORTLK11_E | 9.1667 | 0 | VM0P1O.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
Q>N-MUTE_757 | 9.1667 | 0 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
V_BANNERTSF_FLT_53 | 9.1667 | 0 | Limit Bannerton Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#YABULU_O_E | 9.0833 | 0 | QTYP.ENERGY * 1 >= 83 (Wt = 65) | Other | DEFAULT | Direction
Q_KENSF1_ZERO | 9.0833 | 0 | Kennedy Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
S-MWPS1-PV_0 | 9.0833 | 1.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 1 PV generation of 0 MW | Outage | Unit Zero | SA
#QBYNBL1_E | 9 | 0 | NQBB2Q.ENERGY * 1 <= 10 (Wt = 360) | Other | DEFAULT | Quick
N>>N-PKWL_94K_2 | 9 | 79.4167 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
Q_STR_8C7C2K_LVSF_2 | 9 | 0 | No limit to Lilyvale SF to if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8 ,NQLD>450&470(AVG),Ross_FN>250&270(AVG),or if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_RGBSF | 9 | 3.3333 | No limit to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
S>>BWMP_BRTW_WTTP | 9 | 0.083333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
N>>N-MPWW_ONE_8 | 8.9167 | 53.8333 | Out= Mt. Piper to Wallerawang(70 or 71), avoid O/L Molong to Orange North (94T) on trip of the remaining Mt Piper to Wallerawang (71 or 70) , Feedback | Outage | Thermal | NSW
NC_Q_BRAEMAR6 | 8.9167 | 0 | Non Conformance Constraint for Braemar 6 Power Station | Other | Non-Conformance | Non-Conformance
S_DVRB2_270 | 8.9167 | 7.9167 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
V_BANNERTON_ZERO | 8.9167 | 8.0833 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
#VPGS4_E | 8.8333 | 0 | VLYP010.ENERGY * 1 >= 53 (Wt = 35) | Other | DEFAULT | Quick
S^^V_SETB_1 | 8.75 | 0 | Out= one South East to Tailem Bend 275kV line, voltage collapse equation Tailem Bend-Keith #2 132kV Line <=135 MW on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
T>T_NIL_BL_110_4 | 8.75 | 68.8333 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
V_MURRAWRWF_FLT_80 | 8.75 | 77 | Limit Murra Warra Wind Farm 1+2 upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
#LYA3_E | 8.6667 | 9.25 | VLYP3.ENERGY * 1 <= 540 (Wt = 35) | Other | DEFAULT | Quick
Q^^NIL_CS | 8.6667 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL | Voltage Stability | Qld
#LNGS1_P_E | 8.5833 | 0 | VAT21L.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
T_ROCOF_3 | 8.5833 | 0.58333 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
V_CWWF_FLT_0 | 8.5833 | 79.8333 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KIATAWF_FLT_15 | 8.5833 | 75 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
#LNGS2_P_E | 8.5 | 0 | VAT22L.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#LYA4_E | 8.5 | 0 | VLYP4.ENERGY * 1 <= 540 (Wt = 35) | Other | DEFAULT | Quick
#V-SA_RAMP_I_F | 8.5 | 4.1667 | V-SA >= MIN(-85, InitialFlow + 50) (Wt=35) | Other | Ramping | Quick
S_WP_ISL | 8.4167 | 0 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Wattle Pt WF islanded | Outage | Islanding - Unit | SA
N_DARLSF_FLT_100 | 8.4167 | 7.0833 | Limit Darlington Pt Solar Farm upper limit to 100 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
NC_N_JUNEESF1 | 8.3333 | 0.58333 | Non Conformance Constraint for JUNEE SF | Other | Non-Conformance | Non-Conformance
NC_Q_BRAEMAR2 | 8.3333 | 0 | Non Conformance Constraint for Braemar 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_BRAEMAR7 | 8.3333 | 0 | Non Conformance Constraint for Braemar 7 Power Station | Other | Non-Conformance | Non-Conformance
S_DLBAT-L_ISL | 8.3333 | 0 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Dalrymple Battery (Load Mode) islanded | Outage | Islanding - Unit | SA
NC_N_CG3 | 8.25 | 0 | Non Conformance Constraint for Colongra 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_BRAEMAR3 | 8.0833 | 0 | Non Conformance Constraint for Braemar 3 Power Station | Other | Non-Conformance | Non-Conformance
N_LIMOSF1_FLT_60 | 8.0833 | 136.1667 | Limit Limondale 1 solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_CWWF_FLT_55 | 8.0833 | 64.75 | Limit Crowlands Wind Farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KARADSF_FLT_20 | 8.0833 | 120.3333 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NC_V_VPGS1 | 8 | 0 | Non Conformance Constraint for Valley Power - unit 1 | Other | Non-Conformance | Non-Conformance
#BW01_E | 7.9167 | 0 | NBAY1.ENERGY * 1 <= 630 (Wt = 35) | Other | DEFAULT | Quick
#QPS4_O_E | 7.9167 | 0 | SQPS4.ENERGY * 1 >= 24 (Wt = 65) | Other | DEFAULT | Direction
N>>N-NIL-YS-TX | 7.8333 | 0 | Out= Nil, avoid O/L Either of Yass 132/330 Transformers on trip of Nil, Feedback | NIL | Thermal | NSW
N>N-9GL-999_94U | 7.8333 | 0 | Out= Bango973 WF to Yass 132kV line(9GL), avoid O/L Cowra to Bango999 (999) on trip of line 94U, Feedback | Outage | Thermal | NSW
V::S_KNPW_MAXG | 7.8333 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA.. | Outage | Transient Stability | SA
V>V_NIL_8_1 | 7.8333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF O/S. | NIL | Thermal | Vic
V_ARARATWF_FLT_0 | 7.8333 | 89.0833 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N::N_CNCW_2 | 7.75 | 17.4167 | Out = Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line | Outage | Transient Stability | NSW
S>>NIL_BWMP_TWPA | 7.75 | 7.75 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
#MP1_E | 7.6667 | 0 | NMTP1.ENERGY * 1 <= 700 (Wt = 35) | Other | DEFAULT | Quick
Q_WARWSF1_ZERO | 7.6667 | 0 | Warwick Solar Farm 1 upper limit of 0 MW | Outage | Unit Zero | Qld
V^^N_DPWG_X5_1 | 7.6667 | 73.3333 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_YATPSF_FLT_20 | 7.6667 | 115.4167 | Limit Yatpool solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 7.6667 | 31.5833 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Transient Stability | Qld
#QPS2_O_E | 7.5833 | 0 | SQPS2.ENERGY * 1 >= 24 (Wt = 65) | Other | DEFAULT | Direction
N_DARLSF_FLT_85 | 7.5833 | 18 | Limit Darlington Pt Solar Farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
#BRAEMAR6_P_E | 7.5 | 0 | QBRA6B.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
N>N_9U2_969_NIL | 7.5 | 0 | Out= 9U2 (Moree to Inverell ) 132kV line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
N_FINLYSF_FLT_93 | 7.5 | 0 | Limit Finley solar farm upper limit to 93 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S-RBTX1+RBTX2_MLNK | 7.5 | 0 | Out= Robertstown 132/275kV TX1 + Robertstown 132/275kV TX2 O/S, limit import limit into SA on the Murraylink | Outage | Other | SA
#MORTLK12_E | 7.4167 | 0 | VM0P2O.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
N_FINLYSF_FLT_45 | 7.4167 | 101.0833 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
T>T_HA_TX_2 | 7.4167 | 0 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 110 kV to 220 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Thermal | Tas
N>>N-PKWL_94K_1 | 7.3333 | 31.25 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
Q_ROMA_8_ZERO_E | 7.3333 | 0 | Direction to zero for Roma #8 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
I_CTRL_ISSUE_ML | 7.25 | 4.5 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
Q_ROMA_7_ZERO_E | 7.25 | 0 | Direction to zero for Roma #7 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
V_MURRAWRWF_FLT_135 | 7.25 | 0 | Limit Murra Warra Wind Farm 1+2 upper limit to 135 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N_SUNRSF_FLT_60 | 7.1667 | 101.9167 | Limit Sunraysia solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_KENWF1_ZERO | 7.1667 | 0 | Kennedy Wind Farm upper limit of 0MW | Outage | Unit Zero | Qld
S-MWPS4-PV_0 | 7.0833 | 14 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW | Outage | Unit Zero | SA
V::N_X_SMSC_V | 7.0833 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage | Transient Stability | Vic
V>V_X_HWRO12_1 | 7 | 0 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, avoid O/L Yallourn to Rowville No. 6, 7 or 8 220 kV lines on trip of Yallourn to Rowville No. 5 220 kV line line, feedback, YWG1 on 220 kV, Radial mode | Outage | Thermal | Vic
I_CTRL_ISSUE_TE | 6.9167 | 2.3333 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
Q_STR_7C8C_HASF | 6.9167 | 31.1667 | Limit Haughton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
VSML_165 | 6.9167 | 0 | Vic to SA on ML upper transfer limit of 165 MW | Outage | Discretionary | Vic
NQ_700_TEST | 6.8333 | 0 | NSW to Qld on QNI upper transfer limit of 700 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
T_REECE1_100 | 6.8333 | 0 | Discretionary 100 MW upper limit on Reece unit 1 | Outage | Discretionary | Tas
V_CWWF_FLT_48 | 6.8333 | 0 | Limit Crowlands Wind Farm upper limit to 48 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S_DLBAT-G_ISL | 6.75 | 0 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network), Dalrymple Battery (Gen Mode) islanded | Outage | Islanding - Unit | SA
NC_V_JLA03 | 6.6667 | 0.083333 | Non Conformance Constraint for Jeeralang A - 03 Power Station | Other | Non-Conformance | Non-Conformance
N_BROKENHSF_FLT_30 | 6.6667 | 69.75 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>>CPWO1_CPWO2_WUGG | 6.6667 | 67.5 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Woolooga (814) on trip of Wurdong to Teebar Creek (819) line, Feedback | Outage | Thermal | Qld
Q_HAMISF1_ZERO | 6.6667 | 0.16667 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
V::S_2SE+PAVC_SETB | 6.6667 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S(Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
#MCKAY1_E | 6.5833 | 0 | VMKP1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
NC_N_NEVERSF1 | 6.5833 | 0 | Non Conformance Constraint for NEVERTIRE SOLAR FARM | Other | Non-Conformance | Non-Conformance
#DARTM1_E | 6.5 | 0 | VDPS.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
N>>N-DTSS_20 | 6.5 | 0 | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage | Thermal | NSW
TVBL_ROC | 6.4167 | 22.6667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
#GSTONE2_E | 6.3333 | 0 | QGLD2.ENERGY * 1 <= 230 (Wt = 35) | Other | DEFAULT | Quick
T^T_LIPM_1 | 6.3333 | 8.75 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Voltage Stability | Tas
V_MOORBWF_150_0SWT | 6.3333 | 0 | Moorabool Wind Farm upper limit of 150 MW. Limit Moorabool wind farm to 0 MW if any turbine online from the Moorabool wind farm - South (Cluster 2) | Outage | Discretionary | Vic
#SLDCBLK1_E | 6.25 | 0 | TSL3SL1S.ENERGY * 1 = 7 (Wt = 1160) | Other | DEFAULT | Quick
NC_S_QPS1 | 6.25 | 0 | Non Conformance Constraint for Quarantine QPS1 Power Station | Other | Non-Conformance | Non-Conformance
T>T_NIL_BL_IMP_6EE | 6.25 | 0.16667 | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
Q_YARANSF1_ZERO | 6.1667 | 1.3333 | Yarranlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
#VPGS5_E | 6.0833 | 0 | VLYP011.ENERGY * 1 >= 53 (Wt = 35) | Other | DEFAULT | Quick
Q>N-MUTE_758 | 6.0833 | 0 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
V_BANNERTSF_FLT_25 | 6.0833 | 101.8333 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>NIL_84_83_OPEN | 6 | 0 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | Thermal | NSW
NC_S_QPS3 | 6 | 0 | Non Conformance Constraint for Quarantine QPS3 Power Station | Other | Non-Conformance | Non-Conformance
S_HALWF2_0 | 6 | 2.6667 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
N_SUNRSF_FLT_120 | 5.9167 | 0 | Limit Sunraysia solar farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V::S_PWSE_MAXG | 5.9167 | 0 | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
#POR01_O_E | 5.8333 | 0 | SPLN1.ENERGY * 1 >= 22 (Wt = 65) | Other | DEFAULT | Direction
Q_STR_7C8C_RRSF | 5.8333 | 26.6667 | Limit Ross River SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_WHITSF1_ZERO | 5.8333 | 0.75 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_V_HYMO_1 | 5.8333 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line, Limit voltage unbalance at the APD 500 kV bus and Heywood 275 kV bus | Outage | Voltage Stability | Vic
#W/HOE#2_O_E | 5.75 | 0 | QWIV2.ENERGY * 1 >= 165 (Wt = 65) | Other | DEFAULT | Direction
Q_OKYTX4 | 5.75 | 0 | Out = Oakey 4T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 71MW | Outage | Thermal | Qld
S-DLBAT-L_0 | 5.75 | 0 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW | Outage | Unit Zero | SA
S>>CNRB+BRTW_04 | 5.75 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Morgan Whyalla 4 -Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
N_LIMOSF2_FLT_15 | 5.6667 | 94.5833 | Limit Limondale 2 solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S:V_550_HY_TEST | 5.6667 | 30 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
N^^Q-X_AR_LS_VC_B1, 2, 3, 4, 5, 6 | 5.5833 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
Q_STR_7C8C_KIDSF | 5.5833 | 26.1667 | Limit Kidston SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
#POR03_O_E | 5.5 | 0 | SPL31P.ENERGY * 1 >= 23 (Wt = 65) | Other | DEFAULT | Direction
#TAS1_E_20221122 | 5.4167 | 0 | Multiple TAS1 LHS <= 100 (Wt = 360) | Other | DEFAULT | Quick
N>N-WNMR_9R5_9R6 | 5.4167 | 0 | Out= Wagga North to Murrumburrah 132kV line (991), avoid O/L Wagga North to Wagga330 (9R5) on trip of Wagga North to Wagga 132 (9R6) line, Feedback | Outage | Thermal | NSW
N_BROKENHSF_FLT_32 | 5.4167 | 0 | Limit Broken Hill Solar Farm upper limit to 32 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_KIDSF_3 | 5.4167 | 6.9167 | No limit to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
#BARKIPS1_D_E | 5.3333 | 0.25 | SBPS1B.ENERGY * 1 = 70 (Wt = 755) | Other | DEFAULT | Direction
#LADBROK1_O_E | 5.3333 | 0 | SPEW1.ENERGY * 1 >= 42 (Wt = 65) | Other | DEFAULT | Direction
#STAN-3_O_E | 5.3333 | 0 | QSTN3.ENERGY * 1 >= 355 (Wt = 65) | Other | DEFAULT | Direction
N>>AVMA-17_39_11 | 5.3333 | 0 | Out = Avon - Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage | Thermal | NSW
N_COLEASF1_FLT_45 | 5.3333 | 137.1667 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q-X_STR_7C8C_CLRSF | 5.3333 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Clare Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
#SNUG1_O_E | 5.25 | 0 | SSGA1.ENERGY * 1 >= 65 (Wt = 65) | Other | DEFAULT | Direction
N>>LDTM_964_81_OPEN | 5.25 | 0 | Out= Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage | Thermal | NSW
N>N-X_MOON_WLTX_B | 5.25 | 0 | Out= 94T (Molong to Orange North) 132kV line and one of the Wellington 132/330kV Transformer, avoid O/L to Wellington to Orange North (947) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
N^^V_CNLT_1 | 5.25 | 0 | Out = Canberra - Lower Tumut (07) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
#MP2_E | 5.1667 | 0 | NMTP2.ENERGY * 1 <= 670 (Wt = 35) | Other | DEFAULT | Quick
#TARONG#3_O_E | 5.1667 | 0 | QTRN3.ENERGY * 1 >= 350 (Wt = 65) | Other | DEFAULT | Direction
Q-X_STR_7C8C_KIDSF | 5.1667 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Kidston Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_RRSF | 5.1667 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Ross River Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
T^V_NIL_8 | 5.1667 | 5.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
V::S_NIL_SETB_SECP_1 | 5.1667 | 0.33333 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | Transient Stability | SA
Q_STR_7C2K_RUGSF_3 | 5.0833 | 4.3333 | No limit to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
#BW02_E | 5.0833 | 0 | NBAY2.ENERGY * 1 <= 630 (Wt = 35) | Other | DEFAULT | Quick
N>NIL_947_94T | 5.0833 | 0 | Out= Nil, avoid O/L Wellington to Orange North (947) on trip of Molong to Orange North (94T), Feedback | NIL | Thermal | NSW
Q-X_STR_7C8C_COLSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Collinsville Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_DAYSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Daydream Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_HAMSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Hamilton Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_HAYSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Hayman Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_KEP | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Kennedy Energy park output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_RUGSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Rugby Run Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_SMSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Sun Metals Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_WHTSF | 5.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Whitsunday Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q_NIL_STRGTH_KBWF | 5.0833 | 0 | Out = Nil, limit Kaban Wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_STR_7C2K_CLRSF_3 | 5.0833 | 6.6667 | No limit to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KEP_3 | 5.0833 | 0 | No limit to Kennedy Energy Park if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
S-CRK_0 | 5.0833 | 0 | Discretionary upper limit for Cathedral Rocks windfarm generation of 0 MW | Outage | Unit Zero | SA
N>>V-LTYS_64_7_15M | 5 | 0 | Out= Lower Tumut to Yass(3), avoid O/L Lower Tumut to Upper Tumut (64), on trip of Lower Tumut to Canberra (7) ,Feedback | Outage | Thermal | NSW
Q_STR_7C2K_DAYSF_3 | 5 | 5.75 | No limit to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HAMSF_3 | 5 | 6.5 | No limit to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HAYSF_3 | 5 | 6.4167 | No limit to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_3 | 5 | 6.5833 | No limit to Whitsunday Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
V^^S_SETB_TBSE_2 | 5 | 2.0833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Voltage Stability | SA
#STAN-1_O_E | 4.9167 | 0 | QSTN1.ENERGY * 1 >= 350 (Wt = 65) | Other | DEFAULT | Direction
Q_STR_7C2K_COLSF_3 | 4.9167 | 5.5833 | No limit to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q^^CS_-360 | 4.8333 | 0 | Nominated Offset -360MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage | Voltage Stability | Qld
Q_STR_7C2K_RRSF_3 | 4.8333 | 5.9167 | No limit to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_SMSF_3 | 4.8333 | 0 | No limit to Sun Metals Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
V::S_SEVC_MAXG | 4.8333 | 0 | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V^^N_BADP_1 | 4.8333 | 7.8333 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
NC_V_ELAINWF1 | 4.75 | 0 | Non Conformance Constraint for ELAINE WIND FARM 1 | Other | Non-Conformance | Non-Conformance
N^^V_BADP_1 | 4.75 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>>NIL_TBTU_TBMO_1 | 4.75 | 2.8333 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
#STAN-2_O_E | 4.6667 | 0 | QSTN2.ENERGY * 1 >= 300 (Wt = 65) | Other | DEFAULT | Direction
#VPGS2_E | 4.6667 | 0 | VLYP08.ENERGY * 1 >= 48 (Wt = 35) | Other | DEFAULT | Quick
N_COLEASF1_FLT_50 | 4.6667 | 1.9167 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
VS_250_DYN | 4.6667 | 8.5833 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
#PUMP2_P_E | 4.5833 | 0 | QWIP2.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
N_CROOKWF2_ZERO | 4.5833 | 0 | Crookwell wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
T>T_NIL_BL_5C | 4.5833 | 1.3333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
V_KIAMSF_FLT_120 | 4.5833 | 0 | Limit Kiamal Solar Farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#WANDBG1_E | 4.5 | 83.1667 | QWSB1W.ENERGY * 1 <= 100 (Wt = 360) | Other | DEFAULT | Quick
S>>X_RBTU+HUWT_11 | 4.5 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV lineon trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
T>T_X_LIPM_WACB_A | 4.5 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, with associated 220kV CB at WA O/S, limit southern generators to <= southern load + 15 MW | Outage | Thermal | Tas
#MTGELWF1_E | 4.4167 | 3.25 | VGTW1M.ENERGY * 1 <= 66 (Wt = 360) | Other | DEFAULT | Quick
T_LIPM1_SLOAD_1_N-2 | 4.4167 | 0 | Out=Liapootah-Waddamana-Palmerston #1 220kV line and associated 220kV CBs at Waddamana I/S, loss of #2 parallel 220 kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Thermal | Tas
V^^S_SEVC1_SETB | 4.4167 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
N^^Q_TW_330_BUS1_B1 | 4.3333 | 35.9167 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
#SA1_E_20220803 | 4.25 | 0 | Multiple SA1 LHS <= 780 (Wt = 35) | Other | DEFAULT | Quick
S>>BRTX3_BWMP_WTTP | 4.25 | 3.25 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>MKRB_CNRB_WEMWP4 | 4.25 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Morgan Whyalla 4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | Thermal | SA
S>>X_RBPA+RBTX2_07 | 4.25 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), Feedback | Outage | Thermal | SA
S>>X_RBTU+RBTX_16 | 4.25 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage | Thermal | SA
V^^N_CNYS_1 | 4.25 | 0.33333 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
#STAN-4_O_E | 4.1667 | 0 | QSTN4.ENERGY * 1 >= 350 (Wt = 65) | Other | DEFAULT | Direction
N>>V_NIL_0X1_60 | 4.1667 | 0 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL | Thermal | NSW
S_TIPSB2+PV_180 | 4.1667 | 0 | Upper limit for TIPSB2 +SA rooftop PV trip <=180 MW for 70 MW metro gen option for SA Island - see TOA447 | Outage | Discretionary | SA
S>SETX_NIL_SETX | 4.0833 | 84.5833 | Out= One South East 275/132kV transformer O/S, avoid O/L of other South East 132/275kV TX on Nil trip, | NIL | Thermal | SA
V_WEMENSF_FLT_53 | 4.0833 | 0 | Limit Wemen Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#NSW1-QLD1_RAMP_I_F | 4 | 15.5 | NSW1-QLD1 >= MIN(-217, InitialFlow + 200) (Wt=35) | Other | Ramping | Quick
Q::N_BI_POT_-450 | 4 | 0 | Nominated Offset -450MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage | Transient Stability | Qld
Q>>CPPW_WOSP_WOGP_2 | 4 | 0 | Out= Calliope River to Palmwoods (813+810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
VS_250 | 4 | 7.8333 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
N>>N-NIL_998 | 3.9167 | 2.5833 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
N^^Q_AR_330_BS5_1_B1 | 3.9167 | 4.25 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
N_LIMOSF1_FLT_132 | 3.9167 | 0 | Limit Limondale 1 solar farm upper limit to 132 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S_PPT+SNPT_270 | 3.9167 | 0 | SA Pelican Point + Snapper Point generation <= 270 MW | Outage | Discretionary | SA
N::V_DDSM_MSDD | 3.8333 | 1.1667 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
Q_STR_32282_HASF | 3.8333 | 47.5 | Limit 50% to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
S>>CNRB_MKRB_BWMP | 3.8333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Blyth West-Blyth Munno Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
#TALWA1_E | 3.75 | 0 | NDT13T.ENERGY * 1 >= 190 (Wt = 35) | Other | DEFAULT | Quick
CA_SYDS_525B969A_1 | 3.75 | 0 | Constraint Automation, O/L NN_CR:LCRK:Z:110@N_NRFOLK@TAS for CTG LTBG on trip of CHAPEL ST_NEW NORFOLK 110KV LINE. Generated by STNET[BNECR3] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N_BROKENHSF_FLT_25 | 3.75 | 133.25 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_LIMOSF2_FLT_18 | 3.75 | 0 | Limit Limondale 2 solar farm upper limit to 18 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_32282_CLRSF | 3.75 | 6.3333 | Limit 50% to Clare SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_RGBSF | 3.75 | 6.3333 | Limit 50% to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
N_METZSF_85 | 3.6667 | 0 | Metz Solar farm upper limit of 85 MW | Outage | System Strength | NSW
Q_STR_32282_DAYSF | 3.6667 | 6.3333 | Limit 50% to Daydream SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_MEWF | 3.6667 | 9.0833 | Limit 50% to Mt Emerald WF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_WHTSF | 3.6667 | 6.3333 | Limit 50% to Whitsunday SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_RUGSF | 3.6667 | 12.8333 | Limit Rugby Run SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V::S_SEVC1+PWSE_SETB | 3.6667 | 0 | Out= Either one of the South East SVC+Penola West-South East 132kV (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
V_MURRAWRWF_FLT_15 | 3.6667 | 8.9167 | Limit Murra Warra Wind Farm 1+2 upper limit to 15 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
#DRYCGT1_D_E | 3.5833 | 0.66667 | SDCA1.ENERGY * 1 = 35 (Wt = 755) | Other | DEFAULT | Direction
NC_V_LNGS1 | 3.5833 | 0 | Non Conformance Constraint for Laverton North 1 | Other | Non-Conformance | Non-Conformance
NC_V_LNGS2 | 3.5833 | 0 | Non Conformance Constraint for Laverton North 2 | Other | Non-Conformance | Non-Conformance
Q_STR_32282_HAMSF | 3.5833 | 6.3333 | Limit 50% to Hamilton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_HAYSF | 3.5833 | 6.3333 | Limit 50% to Hayman SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_KIDSF | 3.5833 | 6.3333 | Limit 50% to Kidston SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
#GORDON_E | 3.5 | 0 | TGO11.ENERGY * 1 >= 208 (Wt = 360) | Other | DEFAULT | Quick
#METZSF1_E | 3.5 | 0 | NMTZ1M.ENERGY * 1 <= 115 (Wt = 360) | Other | DEFAULT | Quick
N>N-GITN_TE_C1 | 3.5 | 3.1667 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
NC_Q_GSTONE6 | 3.5 | 0.66667 | Non Conformance Constraint for Gladstone 6 Power Station | Other | Non-Conformance | Non-Conformance
Q>>CLWU_BCRG_BCCP | 3.5 | 0.66667 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
NRM_VIC1_NSW1 | 3.4167 | 0.75 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
Q_KEP-HYB_01MW | 3.4167 | 0 | Kennedy Energy Park upper limit of 1MW | Outage | Discretionary | Qld
Q_STR_32282_RRSF | 3.4167 | 6.3333 | Limit 50% to Ross River SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
V>>V_BABU_6 | 3.4167 | 0 | Out = Balranald to Buronga (X3) 220 kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V_GANWR_BAT_L_ISL_0 | 3.4167 | 4.4167 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
#SEBSF1_E | 3.3333 | 1 | NWGJ2S.ENERGY * 1 <= 90 (Wt = 360) | Other | DEFAULT | Quick
Q_WIVPUMP1_ZERO_E | 3.3333 | 0 | Direction to zero for Wivenhoe Pump #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_WIVPUMP2_ZERO_E | 3.3333 | 0 | Direction to zero for Wivenhoe Pump #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
T_LIPM_PMWA_2_N-3 | 3.3333 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to >= southern load - 15 MW | Outage | Other | Tas
V>NWB6022_TX1 | 3.3333 | 0 | Out= North West Bend CB 6022 O/S, avoid O/L North West Bend 275/132kV TX1 on trip of North West Bend 275/132kV TX3, Feedback | Outage | Thermal | SA
N>>81_964_82 | 3.25 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage | Thermal | NSW
Q_BRAEMAR5_ZERO_E | 3.25 | 0 | Direction to zero for Braemar #5 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
V_GANWR_SF_BAT_50 | 3.25 | 11.75 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
#HPRL1_E | 3.1667 | 0 | SMTL2H.ENERGY * 1 = 40 (Wt = 360) | Other | DEFAULT | Quick
#LD01_E | 3.1667 | 0 | NLDP1.ENERGY * 1 >= 350 (Wt = 35) | Other | DEFAULT | Quick
#LD02_E | 3.1667 | 0 | NLDP2.ENERGY * 1 >= 250 (Wt = 35) | Other | DEFAULT | Quick
QN_1200_DYN_TEST | 3.1667 | 0 | QLD to NSW on QNI upper transfer limit of 1200 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | Qld
TV_150 | 3.1667 | 0 | Tas to Vic on Basslink upper limit of 150 MW | Outage | Discretionary | Tas
V::S_NIL_TBSE_1 | 3.1667 | 0.58333 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | Transient Stability | SA
V_COHUNASF_FLT_17 | 3.1667 | 0 | Limit Cohuna Solar Farm upper limit to 17 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#WDGPH1_E | 3.0833 | 0.33333 | QWDR1W.ENERGY * 1 <= 300 (Wt = 360) | Other | DEFAULT | Quick
N>NIL_99U | 3.0833 | 0 | Out= Nil avoid O/L Sebastipol to Wagga North (99U) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
V::S_PAVC1_SETB | 3.0833 | 0.66667 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
V_KIATAWF_FLT_18 | 3.0833 | 2.6667 | Limit Kiata Wind Farm upper limit to 18 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_WEMENSF_FLT_25 | 3.0833 | 52.0833 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#LYA2_E | 3 | 0 | VLYP2.ENERGY * 1 <= 450 (Wt = 35) | Other | DEFAULT | Quick
N>N-9GL-999_998 | 3 | 0 | Out= Bango973 WF to Yass 132kV line(9GL), avoid O/L Cowra to Bango999 (999) on trip of line 998, Feedback | Outage | Thermal | NSW
N_FINLYSF1_0INV | 3 | 0.33333 | Constraint to violate if Finley solar farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q::N_8C8J_AR_2LG_N-2 | 3 | 0 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | Qld
Q>>NIL_STCP_RGLC | 3 | 1.5 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Stanwell to Calliope River (848+812) line, Feedback | NIL | Thermal | Qld
Q_STR_32282_COLSF | 3 | 6.3333 | Limit 50% to Collinsville SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
V>>V_DDTX_C | 3 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage | Thermal | Vic
CA_BRIS_511836F4_1 | 2.9167 | 0 | Constraint Automation, O/L 947:L947:I:132@WELLNGTN@NSW for CTG LNQR on trip of WELLNGTN-MT_PIPER 72 330KV LN. Generated by STNET[NORVM2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
Q::N_BI_POT_-500 | 2.9167 | 0 | Nominated Offset -500MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage | Transient Stability | Qld
Q_STR_32282_SMSF | 2.9167 | 8.25 | Limit 50% to Sun Metals SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
S>>X_RBTU+RX+HUSN_14 | 2.9167 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line + Hummocks??Snowtown 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
S_LB2WF_CONF | 2.9167 | 0.25 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
T_BLINK_TV_BID | 2.9167 | 0 | Out = Nil, limit Basslink to 0 MW if Basslink bid zero. Constraint to swamp otherwise. | NIL | Other | Tas
T>T_FASH_1_N-2 | 2.9167 | 3.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Thermal | Tas
V_KIAMSF_40INV | 2.9167 | 0 | Limit Kiamal Solar Farm upper limit to 0 MW if number of inverter available exceeds 40. Constraint swamps out otherwise. DS only | Outage | System Strength | Vic
NC_S_STARHLWF | 2.8333 | 0 | Non Conformance Constraint for Starfish Hill Wind Farm | Other | Non-Conformance | Non-Conformance
QNTE_OSCILLATE | 2.8333 | 3.3333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Discretionary | Qld
#YWPS2_E | 2.75 | 0 | VYP22.ENERGY * 1 <= 345 (Wt = 35) | Other | DEFAULT | Quick
#YWPS3_E | 2.75 | 0 | VYP23.ENERGY * 1 <= 325 (Wt = 35) | Other | DEFAULT | Quick
#YWPS4_E | 2.75 | 0 | VYP24.ENERGY * 1 <= 325 (Wt = 35) | Other | DEFAULT | Quick
N::Q_LDNC_TNT | 2.75 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage | Transient Stability | NSW
NC_Q_OAKEY2 | 2.75 | 0 | Non Conformance Constraint for Oakey 2 Power Station | Other | Non-Conformance | Non-Conformance
S>>CNRB+BRTW_01 | 2.75 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown- Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V::S_BLKRG_MAXG_3 | 2.75 | 0.083333 | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | Outage | Transient Stability | SA
V::S_SEVC1+PWSE_MAXG | 2.75 | 0 | Out= Either one of the South East SVC+Penola West-South East 132kV (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
#AGLSOM_E | 2.6667 | 0 | VTTS1.ENERGY * 1 >= 80 (Wt = 35) | Other | DEFAULT | Quick
Q_STR_7C8C_CLRSF | 2.6667 | 16.6667 | Limit Clare SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>V_460_DYN | 2.6667 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | SA
S_TIPSB4+PV_180 | 2.6667 | 0 | Upper limit for TIPSB4 +SA rooftop PV trip <=180 MW for 70 MW metro gen option for SA Island - see TOA447 | Outage | Discretionary | SA
#DARTM1_P_E | 2.5833 | 0 | VDPS.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#JUNEESF1_E | 2.5833 | 1.0833 | NWGJ1J.ENERGY * 1 <= 30 (Wt = 360) | Other | DEFAULT | Quick
#MCKAY1_P_E | 2.5833 | 0 | VMKP1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
Q>>WOPW_WOSP_WOGP_1 | 2.5833 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
Q_COLNVSF1_ZERO | 2.5833 | 0 | Collinsville solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_DDPS1_ZERO_E | 2.5833 | 0 | Direction to zero for Darling Downs GT for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_STR_7C2K_KIDSF_1 | 2.5833 | 0 | No limit to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
S>>BWMP_RBTU_WTTP | 2.5833 | 1.1667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_RBPA_RBTU | 2.5833 | 0 | Out= Nil, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | NIL | Thermal | SA
S>NIL_PL_GENMAX_YDMD | 2.5833 | 0 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | Thermal | SA
VSML_ZERO | 2.5833 | 21 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
N^^V_SMTXF2_1 | 2.5 | 0.83333 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_32282_KEP | 2.5 | 0 | Limit 50% to kennedy Energy Park if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
S^NIL_CRK+MTM+PLN110 | 2.5 | 0 | Out= Nil, upper limit for Cathedral Rocks WF + Mt Millar WF + Port Lincoln generation <= 110 MW to maintain voltage stability limits | NIL | Voltage Stability | SA
V::N_HYTR_O2 | 2.5 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
#HILLSTN1_E | 2.4167 | 2.6667 | NDNH1H.ENERGY * 1 <= 85 (Wt = 360) | Other | DEFAULT | Quick
#MIDDLSF1_E | 2.4167 | 59.6667 | QLIS2M.ENERGY * 1 <= 26 (Wt = 360) | Other | DEFAULT | Quick
NC_Q_SRSF1 | 2.4167 | 0 | Non Conformance Constraint for SUSANRIVERSOLARFARM | Other | Non-Conformance | Non-Conformance
NRM_NSW1_QLD1 | 2.4167 | 0.16667 | Negative Residue Management constraint for NSW to QLD flow. | NIL | Negative Residue | Negative Residue
NRM_VIC1_SA1 | 2.4167 | 1.3333 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue | Negative Residue
Q>>TRSP_BKSP_MESP | 2.4167 | 0 | Out= 832 (H18 Tarong to H2 South Pine) 275 kV feeder, avoid O/L 838 (H36 Blackwall to H2 South Pine) 275 kV feeder on trip of 825 (H12 Mt England to H2 South Pine) 275 kV feeder, Feedback | Outage | Thermal | Qld
Q^WOPW_CS_WOSP_O | 2.4167 | 0 | Out= Any of the 275kV lines between Woolooga to South Pine (807,808 or 810),avoid voltage instability on CQSQ on trip of the remaining 275kV Parallel line lines between Woolooga to South Pine (807,808 or 810) (132kV and 110kV parallel network open) | Outage | Voltage Stability | Qld
#TUMUT3_E | 2.3333 | 0 | NLTS8.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
N>N-WLWO_C | 2.3333 | 0 | Out = Wellington to Wollar line (79), avoid O/L on Cowra to Forbes North (998) on trip of Mt_Piper to Wellington line (72), Feedback | Outage | Thermal | NSW
N>N_96M_969_NIL | 2.3333 | 0 | Out= Any one 132kV feeder between Moree to Boggabri East (96M,9UH,9UJ),avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
N^^V_DPWG_X5_1 | 2.3333 | 4.0833 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q>>BCRG_BCCP_CLWU | 2.3333 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
Q_KEP-HYB_11MW | 2.3333 | 0 | Kennedy Energy Park upper limit of 11MW | Outage | Discretionary | Qld
Q_STR_7C2K_COLSF_1 | 2.3333 | 0 | No limit to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,((NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HASF_1 | 2.3333 | 0 | No limit to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_RUGSF_1 | 2.3333 | 0 | No limit to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
S-OUT_WTPT_SC+INV_1 | 2.3333 | 0 | Out=HUBG Or HUWT line Or one CB(HU 6135/6060,BG 6246,WT 7022/7021), limit output of Wattle Pt WF based on Wattle Pt statcom status & the number of Dalrymble battery inverters I/S (Note:swamped for No. of Dalrymple bat. inverters < 10 && 1or2 SC O/S) | Outage | Other | SA
S>>RBTU_RBPA_WTTP | 2.3333 | 2.5833 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
V>>N-LTUT_G | 2.3333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage | Thermal | Vic
V>>N_NIL_66_65 | 2.3333 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL | Thermal | Vic
N::N_CNSD_2 | 2.25 | 1.4167 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
N^^V_LTWG_1 | 2.25 | 3.75 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_NIL_STRGTH_HAUSF | 2.25 | 216.25 | Out = Nil, limit Haughton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_STR_7C2K_RRSF_1 | 2.25 | 0 | No limit to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG)or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_1 | 2.25 | 0 | No limit to Whitsunday Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG)or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
S>>TBTU_CGTB_MOTB | 2.25 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of Cherry Gardens-Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBTU+HUWT_10 | 2.25 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
V_GANWRSF_FLT_25 | 2.25 | 31.5833 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#BW04_E | 2.1667 | 0 | NBAY4.ENERGY * 1 <= 630 (Wt = 35) | Other | DEFAULT | Quick
#SA1_E_20220105 | 2.1667 | 0 | Multiple SA1 LHS <= 130 (Wt = 35) | Other | DEFAULT | Quick
#VBBL1_E | 2.1667 | 0 | VMLB2V.ENERGY * 1 = 100 (Wt = 360) | Other | DEFAULT | Quick
NC_Q_OAKEY1SF | 2.1667 | 2.1667 | Non Conformance Constraint for OAKEY 1 SOLAR FARM | Other | Non-Conformance | Non-Conformance
S_PELPT_GT1+2+PV_190 | 2.1667 | 0 | Discretionary upper limit for (Pelican PT GT1 +SA rooftop PV trip <=190 MW)&(Pelican PT GT2 +SA rooftop PV trip <=190 MW). NOTE: Refer to SO_OG_SA_12 section 4.4 | Outage | Discretionary | SA
T>T_NIL_BL_3C | 2.1667 | 1.9167 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
T_LIPM2_SLOAD_1_N-2 | 2.1667 | 0 | Out=Liapootah-Waddamana-Palmerston #2 220kV line and associated CBs at Waddamana I/S, loss of the #1 parallel 220kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Thermal | Tas
V_OWF_NRB_0 | 2.1667 | 4.9167 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Discretionary | Vic
#PUMP1_E | 2.0833 | 0 | QWIP1.ENERGY * 1 >= 240 (Wt = 35) | Other | DEFAULT | Quick
NC_V_STOCKYD1 | 2.0833 | 0.33333 | Non Conformance Constraint for STOCKYARD HILL | Other | Non-Conformance | Non-Conformance
Q_CS_1700 | 2.0833 | 0 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary) | Outage | Discretionary | Qld
SVML_FLT_150 | 2.0833 | 9.9167 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
V^^N_SDUT_1 | 2.0833 | 28.75 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_MTMERCER_ZERO | 2.0833 | 25.3333 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
#ADPPV1_E | 2 | 160.3333 | SMVE6D.ENERGY * 1 <= 9 (Wt = 360) | Other | DEFAULT | Quick
#GNNDHSF1_E | 2 | 144.9167 | NGNE1G.ENERGY * 1 <= 110 (Wt = 360) | Other | DEFAULT | Quick
N>N_968_969_NIL_1 | 2 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line and 96M(Narrabri to Moree), avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
NC_N_TALWA1 | 2 | 0.083333 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance | Non-Conformance
Q^^N_AR_SVC_1 | 2 | 22 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
S-LB2_0 | 2 | 0 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | Unit Zero | SA
S-MWPS3-PV_0 | 2 | 9.9167 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW | Outage | Unit Zero | SA
S>>BRDV_RBTU_WEWT | 2 | 2.6667 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>BRDV_BWPA_RHBR | 2 | 5.8333 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>V_460 | 2 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage | Thermal | SA
S_LB3_0 | 2 | 0.16667 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | Unit Zero | SA
T_BLINK_TV_NGZ | 2 | 4.25 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | Outage | Other | Tas
T_GO_300 | 2 | 0.66667 | Discretionary 300 MW upper limit on total Gordon generation | Outage | Discretionary | Tas
V::S_HYSE_MG_PPGT1_2 | 2 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors O/S). Co-optimised eq PPGT1 LHS | Outage | Transient Stability | SA
V^SML_HOMR_3 | 2 | 0 | Out = Horsham to Murra Warra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
V^^S_PAVC1_MAXG | 2 | 0.083333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
#BRAEMAR2_P_E | 1.9167 | 0 | QBRA2.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
NC_V_MUWAWF2 | 1.9167 | 0 | Non Conformance Constraint for MUWAWF2 | Other | Non-Conformance | Non-Conformance
N^^N_NIL_1 | 1.9167 | 0 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | Voltage Stability | NSW
N^^V_CNYS_1 | 1.9167 | 0 | Out = Canberra - Yass (9), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N^^V_MLNK_1 | 1.9167 | 0 | Out = Murraylink, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_LIMOSF1_FLT_50 | 1.9167 | 26 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_CLRSF_1 | 1.9167 | 0 | No limit to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Kar>=2+ Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
T^V_NIL_11 | 1.9167 | 30.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink harmonic filter, swamped if TVCC in service | NIL | Voltage Stability | Tas
V^^N_SMF2_1 | 1.9167 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^S_2SE+PAVC_MAXG | 1.9167 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V^^S_PAVC1_SETB | 1.9167 | 0 | Out= Para one SVC(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
#CG1_P_E | 1.8333 | 0 | NCLG1D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#CG2_P_E | 1.8333 | 0 | NCLG2D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#CG3_P_E | 1.8333 | 0 | NCLG3D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#CG4_P_E | 1.8333 | 0 | NCLG4D.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
NC_V_MUWAWF1 | 1.8333 | 0 | Non Conformance Constraint for MURRA WARRA WF 1 | Other | Non-Conformance | Non-Conformance
Q_OKYTX3 | 1.8333 | 11.0833 | Out = Oakey 3T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 67.3MW | Outage | Thermal | Qld
Q_STR_7C2K_SMSF_1 | 1.8333 | 0 | No limit to Sun Metals Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG)or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
S_DVCN_270 | 1.8333 | 0 | Out = Mt Lock 275 kV CB8020 or CB8018, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+ Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
V::N_LTWG_xxx | 1.8333 | 15.3333 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
VT_000 | 1.8333 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Discretionary | Vic
#BRAEMAR1_E | 1.75 | 0 | QBRA1.ENERGY * 1 <= 188 (Wt = 360) | Other | DEFAULT | Quick
#GSTONE5_E | 1.75 | 0 | QGLD5.ENERGY * 1 <= 245 (Wt = 35) | Other | DEFAULT | Quick
#OAKEY2_E | 1.75 | 0 | QOKY2.ENERGY * 1 <= 173 (Wt = 360) | Other | DEFAULT | Quick
S>>X_RBTU+RX+HUSN_13 | 1.75 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
#BOWWPV1_E | 1.6667 | 19.5833 | SPGW2B.ENERGY * 1 <= 6.1 (Wt = 360) | Other | DEFAULT | Quick
#PUMP2_E | 1.6667 | 0 | QWIP2.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Quick
N>>X-WG5012+TX2_02_L | 1.6667 | 0 | Out = Wagga 330kV CB 5012 (Option 1) + Wagga 330/132kV TX2 O/S, avoid O/L one Yass 132/330kV TX on trip of other Yass 132/330kV TX , Feedback | Outage | Thermal | NSW
N^^V_X_SMF2_SMSC_1 | 1.6667 | 0 | Out = South Morang F2 500/330kV txfmr and both South Morang Series Capacitors, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_YARANSF1_ZERO_N-1 | 1.6667 | 0 | Limit Yarrenlea Solar Farm to 0 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip,Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
S-SA_DVRB_GEN_0300 | 1.6667 | 0 | Discretionary upper limit for SA generation connected at Davenport and between Davenport-Robertstown 275kV lines of 300MW. | Outage | Discretionary | SA
S>>BWMP_RBTU_RBPA | 1.6667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Robertstown-Para 275kV line on trip of Robertstown -Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T>T_LIPM_110_2B | 1.6667 | 0 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
V::N_HYTR_O1 | 1.6667 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::S_HYSE_MAXG_2 | 1.6667 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | Transient Stability | SA
VSML_110 | 1.6667 | 0 | Vic to SA on ML upper transfer limit of 110 MW | Outage | Discretionary | Vic
S-DLBAT-G_0 | 1.5833 | 0 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW | Outage | Unit Zero | SA
CA_BRIS_5233A5C6_1 | 1.5833 | 0 | Constraint Automation, O/L XFMR 3H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
N>N-X_MOON_WLTX_A | 1.5833 | 0 | Out= 94T (Molong to Orange North) 132kV line and one of the Wellington 132/330kV Transformers, avoid O/L Molong to Wellington (945) on trip of Wellington Suntop Tee to Wellington 94K/1 132kV line, Feedback. 94K/1Metering at Wellington end | Outage | Thermal | NSW
NC_Q_OAKEY1 | 1.5833 | 0 | Non Conformance Constraint for Oakey 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_BARKIPS1 | 1.5833 | 0.083333 | Non Conformance Constraint for BARKER INLET PS | Other | Non-Conformance | Non-Conformance
N_WELLSF1_ZERO | 1.5833 | 1.6667 | Wellington solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>>BRDV_RBTU_RBPA | 1.5833 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Robertstown-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>MKRB_BRTW_WTTP | 1.5833 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_RBTU_RBPA | 1.5833 | 0 | Out= Nil, avoid O/L Robertstown-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S>NIL_NWMH1_NWMH2 | 1.5833 | 0.083333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on trip of North West Bend-Monash #1 132kV line, Feedback | NIL | Thermal | SA
V::N_JNWG_xxx | 1.5833 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_ROSM_O2 | 1.5833 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
V>>V_ROTS_TX_2A_R | 1.5833 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Thermal | Vic
V_KIAMSF_40INV_DYN | 1.5833 | 0 | Limit Kiamal Solar Farm upper limit to 0 MW if number of inverter available exceeds 40 and Murra Warra 2 WF Syncon O/S. Constraint swamps out otherwise. DS only | Outage | System Strength | Vic
#STAN-4_P_E | 1.5 | 0 | QSTN4.ENERGY * 1 <= 220 (Wt = 29) | Other | DEFAULT | Direction
#URANQ11_P_E | 1.5 | 0 | NURQ1U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#URANQ12_P_E | 1.5 | 0 | NURQ2U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#URANQ13_P_E | 1.5 | 0 | NURQ3U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
#URANQ14_P_E | 1.5 | 0 | NURQ4U.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
CA_BRIS_52460E76_1 | 1.5 | 0 | Constraint Automation, O/L XFMR T_1@R_TOWN@SA for CTG LS6W on trip of W_LOO - WATE_E 132KV 1 LINE. Generated by STNET[BNECR1] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
N_FINLEYSF_49_INV | 1.5 | 0 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 49. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
N_GOONSF1_0INV | 1.5 | 0 | Constraint to violate if Goonumbla Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_V_HV1100 | 1.5 | 0 | Discretionary constraint on transfer from NSW to VIC of 1100 MW on DDTS-NSW cutset | Outage | Discretionary | NSW
S>>SETB_TBSE_TBKH2_1 | 1.5 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend-Keith #2 132kV Line on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
S>>X_RBTU+RX+HUSN_15 | 1.5 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
T_LIPM_PMWA_1_N-3 | 1.5 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to <= southern load + 15 MW | Outage | Other | Tas
V>>N_051_66_65_R | 1.5 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line,(Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
V_KIATA_ISL_0 | 1.5 | 29.5833 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
#OAKEY1_P_E | 1.4167 | 0 | QOKY1.ENERGY * 1 <= 0 (Wt = 29) | Other | DEFAULT | Direction
N::Q_LDNC_KC | 1.4167 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>>N-DTMN_39_16 | 1.4167 | 0 | Out = Dapto-Marulan(8), avoid O/L Bannaby to Sydney West (39) on trip of Marulan to Avon (16) line, Feedback | Outage | Thermal | NSW
N>>V_SMDD6 | 1.4167 | 5.6667 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
NC_S_LADBROK1 | 1.4167 | 0 | Non Conformance Constraint for Ladbroke Grove 1 Power Station | Other | Non-Conformance | Non-Conformance
N^N_KKLS_1 | 1.4167 | 14.5 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
S>>MKRB_BWMP_WTTP | 1.4167 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V>>S_MOTB_TBCG_TBTU | 1.4167 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
V^^S_NIL_MAXG_xxx | 1.4167 | 0 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Voltage Stability | SA
N>>NIL_7_3 | 1.3333 | 2.5 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | Thermal | NSW
NC_N_CG1 | 1.3333 | 0 | Non Conformance Constraint for Colongra 1 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_MLNK_ARWBBA | 1.3333 | 0 | Out = Murraylink, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | Outage | Voltage Stability | NSW
N_DARLSF_FLT_193 | 1.3333 | 0 | Limit Darlington Pt Solar Farm upper limit to 193 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>>BRTW_BWPA_WTTP | 1.3333 | 2 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>BWMP_HUWT_RHBG-T | 1.3333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill-Brinkworth 132kV T line on trip of Hummocks-Waterloo 132kV line, Feedback | Outage | Thermal | SA
S>>CNRB_BWPA_BGTX | 1.3333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Bungama 275/132kV (TX2) on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>RBTX_BWPA_WTTP | 1.3333 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V::S_HYSE_MG_TPSB2 | 1.3333 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (TIPSB2+ DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors I/S). Co-optimised eq TIPSB2 LHS. | Outage | Transient Stability | SA
N>>N-DTKV_CTMN | 1.25 | 0 | Out= Dapto- Kangaroo Valley (18), avoid O/L Crookwell to Bannaby (61) on trip Collector WF to Marulan (4) line, Feedback | Outage | Thermal | NSW
NSA_T_GO2_10 | 1.25 | 0 | Gordon unit 2 >= 10 MW for Network Support Agreement | Outage | Network Support | Tas
N_SILVERTWF_FLT_100 | 1.25 | 66.6667 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
S>>PARB_RBTU_RBMWP4 | 1.25 | 0.083333 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>NIL_NWRB1_MWP3RB | 1.25 | 0 | Out= NIL, avoid O/L Morgan Pipeline 3-Robertstown 132kV line on trip of North West Bend-Roberstown 132kV line, Feedback | NIL | Thermal | SA
T_FASH_MAXGEN_1 | 1.25 | 22.75 | Upper limit on Mackintosh + Bastyan + John Butters with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Other | Tas
V::N_HYTR_xxx | 1.25 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::N_ROSM_O1 | 1.25 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::S_SEVC1_SETB | 1.25 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
#OAKEY1_O_E | 1.1667 | 0 | QOKY1.ENERGY * 1 >= 160 (Wt = 65) | Other | DEFAULT | Direction
CA_SYDS_5283EFAB_1 | 1.1667 | 0 | Constraint Automation, O/L NN_CS:LNNF:I:110@CHAPEL@TAS for CTG MTD9 on trip of N_NRFOLK - CREEK RD + NYRSTAR LD. Generated by STNET[BNECR2] Host NORREGEEMP4(EMPSYD) | Outage | Thermal | Constraint Automation
N::N_GRYS_2 | 1.1667 | 0 | Out = Gullen Range to Yass (3J), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
NC_Q_KEPWF1 | 1.1667 | 0 | Non Conformance Constraint for KEP WIND | Other | Non-Conformance | Non-Conformance
NC_Q_SWAN_E | 1.1667 | 1.5833 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance | Non-Conformance
NC_S_BOWWPV1 | 1.1667 | 0 | Non Conformance Constraint for BOLIVAR WWTP PV1 | Other | Non-Conformance | Non-Conformance
NC_V_YWPS1 | 1.1667 | 0.66667 | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Other | Non-Conformance | Non-Conformance
N^^Q_LS_SVC_KPP_1 | 1.1667 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage | Voltage Stability | NSW
N^^V_DPWG_X5_RVYS_1 | 1.1667 | 0 | Out = Darlington Point to Wagga with line X5 open and Ravine to Yass (2+63) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_SUNRSF_FLT_50 | 1.1667 | 38 | Limit Sunraysia solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C8C_COLSF | 1.1667 | 14.5 | Limit Collinsville SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>BWMP_DVBR_BGTX2 | 1.1667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Bungama 275/132kV (TX2) on trip of Davenport-Brinkworth 275 kV line, Feedback | Outage | Thermal | SA
T>T_FASH_2_N-2 | 1.1667 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.1 transformer | Outage | Thermal | Tas
#SHPUMP_E | 1.0833 | 0 | NSHP1.ENERGY * 1 >= 120 (Wt = 65) | Other | DEFAULT | Direction
N>NIL_9GL | 1.0833 | 0 | Out= Nil, avoid O/L Bango973 to Yass (9GL) on trip of Nil, (Note: Swamped when 999 is O/S) | NIL | Thermal | NSW
NC_N_MP2 | 1.0833 | 0.25 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_MTMILLAR | 1.0833 | 0 | Non Conformance Constraint for Mount Millar Wind Farm | Other | Non-Conformance | Non-Conformance
N_COLEASF1_FLT_105 | 1.0833 | 0 | Limit Coleambally solar farm upper limit to 105 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
QNI_SOUTH_1150_DYN | 1.0833 | 1.6667 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Transient Stability | Qld
Q_CHILDSF1_ZERO | 1.0833 | 0 | Childers Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
Q_NIL_STRGTH_CLRSF | 1.0833 | 25.75 | Out = Nil, limit Clare solar farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Kareeya generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_COLSF | 1.0833 | 27.5 | Out = Nil, limit Collinsville solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_DAYSF | 1.0833 | 25.0833 | Out = Nil, limit Daydream solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_KEP | 1.0833 | 0 | Out = Nil, limit Kennedy energy park output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_KIDSF | 1.0833 | 32.1667 | Out = Nil, limit Kidston solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_MEWF | 1.0833 | 43.1667 | Out = Nil, limit Mt Emerald wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_RRSF | 1.0833 | 29.0833 | Out = Nil, limit Ross River solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_RUGSF | 1.0833 | 0 | Out = Nil, limit Rugby run solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_SMSF | 1.0833 | 47.9167 | Out = Nil, limit Sun metals solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_WHTSF | 1.0833 | 26.0833 | Out = Nil, limit Whitsunday solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_RRSF1_ZERO | 1.0833 | 0.41667 | Ross River solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C2K_KEP_1 | 1.0833 | 0 | No limit to Kennedy Energy Park if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_DAYSF | 1.0833 | 13.1667 | Limit Daydream SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_HAYSF | 1.0833 | 15.6667 | Limit Hayman SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S::V_TBSE_TBSE_2 | 1.0833 | 12.3333 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
T>T_X_LIPM_TWO_E | 1.0833 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L Tungatinah to Meadowbank Tee 2 on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
VSML_195 | 1.0833 | 0 | Vic to SA on ML upper transfer limit of 195 MW | Outage | Discretionary | Vic
V_BULGANAWF_FLT_111 | 1.0833 | 0 | Limit Bulgana Wind Farm upper limit to 111 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_COHUNASF_0INV | 1.0833 | 5.9167 | Constraint to violate if Cohuna Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
V_MOORBWF_FLT_150 | 1.0833 | 0 | Limit Moorabool Wind Farm upper limit to 150 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#BANGOWF2_E | 1 | 0 | NBB21B.ENERGY * 1 <= 69 (Wt = 360) | Other | DEFAULT | Quick
#CATHROCK_E | 1 | 0 | SCRK.ENERGY * 1 <= 35 (Wt = 35) | Other | DEFAULT | Quick
#DALNTHL1_E | 1 | 0 | SDAN2D.ENERGY * 1 >= 3 (Wt = 360) | Other | DEFAULT | Quick
#SWAN_E_E | 1 | 0 | QSWE.ENERGY * 1 <= 360 (Wt = 360) | Other | DEFAULT | Quick
N>999_9GL_NIL | 1 | 0 | Out= Bango999 WF to Cowra 132kV line(999), avoid O/L Bango973 to Yass (9GL) on trip of Nil, Feedback | NIL | Thermal | NSW
N>>N-NIL_68 | 1 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) on trip of Collector to Marulan (4) line, Feedback | NIL | Thermal | NSW
N>>NIL_7_1 | 1 | 0.25 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Stockdill (1) line, Feedback | NIL | Thermal | NSW
NC_N_VP5 | 1 | 2 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_VP6 | 1 | 6.5833 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance | Non-Conformance
Q^FNQ_MEWF_-60_-100 | 1 | 0 | Nominated Offset= -60MW (Fdr7139 and Fdr7301 closed),-100 (Fdr7139 and Fdr7301 opened) Far North Qld Voltage Stability limit for loss of Mt Emerald Windfarm during system normal configuration (Fdr857+877 IS) | Outage | Voltage Stability | Qld
Q^FNQ_MEWF_-70_-120 | 1 | 0 | Nominated Offset= -70MW (Fdr7139 and Fdr7301 closed),-120 (Fdr7139 and Fdr7301 opened) Far North Qld Voltage Stability limit for loss of Mt Emerald Windfarm during system normal configuration (Fdr857+877 IS) | Outage | Voltage Stability | Qld
Q_CHCR | 1 | 0 | Out = Charters Towers to Cape River 66kV line, limit Kennedy Energy Park to 11MW | Outage | Unit Zero | Qld
Q_KEP-HYB_27MW | 1 | 0 | Kennedy Energy Park upper limit of 27MW | Outage | Discretionary | Qld
Q_NIL_STRGTH_HAMSF | 1 | 29.1667 | Out = Nil, limit Hamilton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_HAYSF | 1 | 27.9167 | Out = Nil, limit Hayman solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_STR_7C2K_COLSF_5 | 1 | 0 | No limit to Collinsville Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_WHTSF | 1 | 8.25 | Limit Whitsunday SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>X_RBTU+RX+HUSN_10 | 1 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Templers-Roseworthy 132 kV on trip of Templers West-Para 275 kV line, Feedback | Outage | Thermal | SA
V::S_SETB_MAXG | 1 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with one Black Range series capacitors I/S). | Outage | Transient Stability | SA
V::S_SEVC1_MAXG | 1 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V>>N-LTMS_1 | 1 | 2.0833 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage | Thermal | Vic
N>>X-17+76_39_11 | 0.91667 | 0 | Out= Avon to Macarthur (17) and Sydney South to Wallerawang (76), avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage | Thermal | NSW
Q>>BCST_BCST_STBS | 0.91667 | 0 | Out = 848 or 849 (H29 Stanwell to H10 Bouldercombe 275 kV line), avoid O/L the remaining 848 or 849(H29 Stanwell to H10 Bouldercombe 275 kV line) on trip of Stanwell to Broadsound (8331) line with 7114/1 open post contingent or pre contingent. Feedback | Outage | Thermal | Qld
Q_STR_7C2K_HAMSF_1 | 0.91667 | 0 | No limit to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HAYSF_1 | 0.91667 | 0 | No limit to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_MEWF_1 | 0.91667 | 0 | No limit to Mt Emerald if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad)>=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haugh Syncon ON.(80% if Kar>=2+ NQLD>270(AVG),Ross_FN>120(AVG)).If Haugh Syncon OFF, limit 80% D/100% N with Kar>=2, 80% N Kar=0),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_MEWF_7 | 0.91667 | 0 | No limit to Mt Emerald WF if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(Kar=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG) or Glad.=1 +Haughton syncon ON or Kar=0,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon ON),Zero otherwise. | Outage | System Strength | Qld
Q_WOOLGSF1_ZERO | 0.91667 | 0 | Woolooga Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>CGTB1_TUTB_MOTB | 0.91667 | 2.8333 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_RBTX_RBTX_2 | 0.91667 | 0.33333 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL | Thermal | SA
S>>TBTU_TBCG_TBMO | 0.91667 | 3 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
S^NIL_MTM_VCS_STATUS | 0.91667 | 0 | Out= Nil, upper limit for Mt Millar WF based on Mt Millar Voltage Control System (VCS) availability, (Note: MTM <=16 MW when VCS OFF; MTM<= 70 MW when VCS ON) | NIL | Voltage Stability | SA
S_SNOW_N+S_210 | 0.91667 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 210 MW | Outage | Discretionary | SA
T_CTHLWF_020 | 0.91667 | 0 | Wild Cattle Hill Wind Farm upper limit of 20 MW | Outage | Discretionary | Tas
V::N_SMF2_O1 | 0.91667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::S_HYSE_MAXG | 0.91667 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | Transient Stability | SA
S>VMLMHNW2 | 0.91667 | 0.25 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage | Thermal | SA
N_BROKENH1_0INV | 0.83333 | 5.25 | Constraint to violate if Broken Hill Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
#WALGRVG1_E | 0.83333 | 0.083333 | NSWB1W.ENERGY * 1 <= 50 (Wt = 360) | Other | DEFAULT | Quick
N>>N-DTMN_08 | 0.83333 | 0 | Out = Dapto-Marulan(8), avoid O/L Marulan to Avon (16) on trip of Dapto to Kangaroo Valley (18) line, Feedback | Outage | Thermal | NSW
N>>NIL_998 | 0.83333 | 0 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
NC_N_ER01 | 0.83333 | 0 | Non Conformance Constraint for Eraring ER01 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_QPS5 | 0.83333 | 0 | Non Conformance Constraint for Quarantine QPS5 Power Station | Other | Non-Conformance | Non-Conformance
Q>>CPST_LCCP_CLWU | 0.83333 | 2.3333 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage | Thermal | Qld
Q>NIL_MRTA_B | 0.83333 | 0.16667 | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
QN_1200_TEST | 0.83333 | 0 | Qld to NSW on QNI upper transfer limit of 1200 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | Qld
Q_KSP1_ZERO | 0.83333 | 16.25 | Kidston solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C2K_DAYSF_1 | 0.83333 | 0 | No limit to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
S>NIL_NIL_SETX12 | 0.83333 | 14.5 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | Thermal | SA
V>>V_NIL_26 | 0.83333 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
V>V_NIL_RADIAL_10 | 0.83333 | 0 | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Thermal | Vic
#COLUMSF1_E | 0.75 | 0 | QCBR1C.ENERGY * 1 <= 162 (Wt = 360) | Other | DEFAULT | Quick
#LIMOSF11_E | 0.75 | 1.75 | NBSF1L.ENERGY * 1 <= 220 (Wt = 360) | Other | DEFAULT | Quick
#NSW1-QLD1_RAMP_E_F | 0.75 | 0 | NSW1-QLD1 <= MAX(4, InitialFlow - 200) (Wt=35) | Other | Ramping | Quick
#WKIEWA1_E | 0.75 | 0 | VWKP1.ENERGY * 1 >= 17 (Wt = 35) | Other | DEFAULT | Quick
N^^V_JNWG_63_X5_1 | 0.75 | 0 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_COLMBSF_60_INV | 0.75 | 0 | Limit Coleambally Solar Farm upper limit to 0 MW if number of inverter available exceed 60. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
N_MOLNGSF1_ZERO | 0.75 | 0 | Molong solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q>>NIL_BCCP_LCCP | 0.75 | 0 | Out= Nil, avoid O/L Larcom Creek to Calliope River (8859) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
Q>NIL_MRTA_A | 0.75 | 0.083333 | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
Q>NIL_SRMB_M020/1 | 0.75 | 10.25 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
S-HDWF2_0 | 0.75 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
S_HALWF_0 | 0.75 | 6.8333 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW | Outage | Unit Zero | SA
S_HDWF1_0 | 0.75 | 0 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
S_HDWF3_0 | 0.75 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
T>T_NIL_BL_IMP_6E | 0.75 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
V^^S_SEVC1_MAXG | 0.75 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V_GANWRSF_0INV | 0.75 | 1.5833 | Constraint to violate if Gannawarra Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
N::Q_NIL_KC | 0.66667 | 2.5833 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | Transient Stability | NSW
N:V_DDSM_BWRG | 0.66667 | 0.083333 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage | Transient Stability | NSW
N>N-WLWO_B | 0.66667 | 0 | Out = Wellington to Wollar line (79), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Mt_Piper line (72), Feedback | Outage | Thermal | NSW
NC_N_BW01 | 0.66667 | 0.5 | Non Conformance Constraint for Bayswater 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-4 | 0.66667 | 0.83333 | Non Conformance Constraint for Stanwell STAN-4 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_LYA2 | 0.66667 | 0.083333 | Non Conformance Constraint for Loy Yang A2 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YWPS4 | 0.66667 | 0.75 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance | Non-Conformance
N_COLEASF1_ZERO | 0.66667 | 66.6667 | Coleambally solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_FINLYSF_FLT_30 | 0.66667 | 34.4167 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_GOONSF_11_INV | 0.66667 | 0.16667 | Limit Goonumbla Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
N_MBTE1_A | 0.66667 | 6 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
Q_CRCRE_6383 | 0.66667 | 0 | Out = Cape River to Cape River East 66kV line, limit Kennedy Energy Park to 0MW | Outage | Unit Zero | Qld
Q_RGBYRSF1_ZERO | 0.66667 | 2.6667 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
SV_240_DYN | 0.66667 | 0 | SA to Victoria on Heywood upper transfer limit of 240 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
T>T_NIL_BL_IMP_1B | 0.66667 | 0 | Out = Nil, avoid O/L either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line with no SPS action, feedback | NIL | Thermal | Tas
T>T_NWSD_110_1 | 0.66667 | 0 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Thermal | Tas
T>T_X_LIPM_WACB_C | 0.66667 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, with associated 220kV CB at WA O/S, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Thermal | Tas
V::N_SMF2_O2 | 0.66667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
VT_050 | 0.66667 | 0 | Vic to Tas on Basslink upper limit of 50 MW | Outage | Discretionary | Vic
V_DDWF_SHWF_600 | 0.66667 | 0 | Limit Dundonnell and Stockyard Hill Wind Farms combined upper limit to 600 MW | Outage | Discretionary | Vic
V_STOCKYH_ZERO | 0.66667 | 105.75 | Stockyard Hill wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
CA_BRIS_51934522_1 | 0.58333 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG LVK1 on trip of KMTS - RCTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N::V_DTKV_MSDD | 0.58333 | 0 | Out=Dapto - Kangaroo Valley (18), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
N>>V_SMDD3 | 0.58333 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the Eildon to Thomastown 220 kV line (flow to South) on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
NC_N_DARLSF1 | 0.58333 | 2 | Non Conformance Constraint for DARLINGTON POINT SF | Other | Non-Conformance | Non-Conformance
NC_N_GOONSF1 | 0.58333 | 0 | Non Conformance Constraint for GOONUMBLA SF | Other | Non-Conformance | Non-Conformance
NC_S_SNAPPER1 | 0.58333 | 0 | Non Conformance Constraint for SNAPPER POINT POWER | Other | Non-Conformance | Non-Conformance
N_MOREESF1_23INV | 0.58333 | 0 | Limit Moree Solar Farm upper limit to 0 MW if number of inverter available exceed 23. Constraint swamp out otherwise. | Outage | System Strength | NSW
Q>>X_CLWU+BCST_2 | 0.58333 | 0 | Out= 871 (H24 Calvale to H40 Wurdong) 275kV line and 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line, avoid O/L remaining 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line on trip of 8811 (Calvale to Halys) line, Feedback | Outage | Thermal | Qld
Q>COLTX | 0.58333 | 0.33333 | Out = Collinsville North T1 or T2 132/33 kV transformer, limit Collinsville Solar Farm to 33.9MW to prevent overload on RMU of the remaining transformer | Outage | Thermal | Qld
Q_STR_7C2K_RUGSF_5 | 0.58333 | 0 | No limit to Rugby Run Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
S>>BRDV_RBTU_WTTP | 0.58333 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_TBCG_TBTU_1 | 0.58333 | 0 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | Thermal | SA
S>>V_MOTB_TUTB_CGTB | 0.58333 | 0 | Out=Mobilong - Tailem Bend 132kV line; avoid O/L Cherry Gardens -Tailem Bend 275kV on trip Tungkillo -Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
S>BRTW_BWMP_STHU | 0.58333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Snowtown T - Hummocks 132kV line on trip of Blyth West- Munno Para 275kV line, Feedback | Outage | Thermal | SA
S^CNRB_SA_NORTH | 0.58333 | 0 | Out = Canowie-Robertstown 275kV line, Manage voltage collapse in northern SA for the trip of one 275kV line between Davenport-Para or Davenport-Tungkillo. | Outage | Voltage Stability | SA
S_CRK_20 | 0.58333 | 0 | Discretionary upper limit for Cathedral Rocks windfarm generation of 20 MW | Outage | Discretionary | SA
#GULLRWF2_E | 0.5 | 103.4167 | NGUR3G.ENERGY * 1 <= 22 (Wt = 360) | Other | DEFAULT | Quick
#NSW1_E_20220630 | 0.5 | 0 | Multiple NSW1 LHS <= 850 (Wt = 35) | Other | DEFAULT | Quick
N>>964_88_84_S | 0.5 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage | Thermal | NSW
N>>NIL_4 | 0.5 | 2.0833 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL | Thermal | NSW
NC_N_LD01 | 0.5 | 0.41667 | Non Conformance Constraint for Liddell LD01 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_CPP_3 | 0.5 | 0.41667 | Non Conformance Constraint for Callide C CPP_3 | Other | Non-Conformance | Non-Conformance
NC_S_AGLHAL | 0.5 | 0.083333 | Non Conformance Constraint for AGL Hallet Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YWPS2 | 0.5 | 0.66667 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance | Non-Conformance
N_X_MBTE2_A & N_X_MBTE2_B | 0.5 | 11.1667 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
Q>>NIL_LCCP_BCCP | 0.5 | 0 | Out= Nil, avoid O/L Bouldercombe to Calliope River (812) on trip of Larcom Creek to Calliope River (8859) line, Feedback | NIL | Thermal | Qld
Q^FNQ_WRVC_-90_-150 | 0.5 | 0 | Nominated Offset= -90MW (Fdr7139 and Fdr7301 closed),-150 (Fdr7139 and Fdr7301 opened) Far North Qld Voltage Stability limit for loss of Woree SVC during system normal configuration (Fdr857+877 IS) | Outage | Voltage Stability | Qld
Q_BLUEGSF1_ZERO | 0.5 | 0 | Bluegrass Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C2K_SMSF_5 | 0.5 | 0 | No limit to Sun Metals Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_HAMSF | 0.5 | 17.75 | Limit Hamilton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C_7C2K_CMSF | 0.5 | 3.3333 | No limit to Clermont SF if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8 OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_EMSF | 0.5 | 3.3333 | No limit to Emerald SF if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8 OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_LVSF | 0.5 | 0 | No limit to Lilyvale SF if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8 OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_MIDSF | 0.5 | 0 | No limit to Middlemount SF to if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8 OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
S-BUPV1_0 | 0.5 | 8.5 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
S>>BRTX3_RBTU_WTTP | 0.5 | 0 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>RBTU_TWPA_TPRS | 0.5 | 1.3333 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>>V_NIL_NIL_RBMW3 | 0.5 | 1.4167 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
S>>X_RBTU+RX+HUSN_22 | 0.5 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Robertstown 132 kV line, Feedback | Outage | Thermal | SA
SV_240 | 0.5 | 0 | SA to Victoria on VicSA upper transfer limit of 240 MW | Outage | Discretionary | SA
S_DV-RB2_050 | 0.5 | 0 | Discretionary upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 50 MW | Outage | Discretionary | SA
S_DV-RB2_DYNAMIC | 0.5 | 0 | Discretionary DYNAMIC upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= MAXG SA(i.e.function X_SA_MAXG_ST_DS) | Outage | Discretionary | SA
S_SNOW_N+S_130 | 0.5 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 130 MW | Outage | Discretionary | SA
T:T_LIPM_1 | 0.5 | 5 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South). Swamp if no Gordon units online. | Outage | Transient Stability | Tas
T>T_LIPM_110_2A | 0.5 | 0.75 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
T_T_MC_ZERO | 0.5 | 0.25 | Discretionary 0 MW upper limit on Macintosh generation | Outage | Discretionary | Tas
T_V_NIL_FCSPS | 0.5 | 1 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Other | Tas
VT_100 | 0.5 | 0 | Vic to Tas on Basslink upper limit of 100 MW | Outage | Discretionary | Vic
V_BRYBWF_ZERO | 0.5 | 0.33333 | Berrybank Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
#NEWENSF2_E | 0.41667 | 0 | NURR2N.ENERGY * 1 <= 6 (Wt = 360) | Other | DEFAULT | Quick
#POR01_E | 0.41667 | 0 | SPLN1.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
CA_BRIS_52155A1A_2 | 0.41667 | 0 | Constraint Automation, O/L ELTS_MLTS_220:LMLT:Z:220@ELTS@VIC for CTG LVAI on trip of BATS-MLTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
CA_SYDS_51A7040E_1 | 0.41667 | 0 | Constraint Automation, O/L 61:LN61:Z:330@CROOKWF@NSW for CTG LNQT on trip of COLLECWF-MARULAN 4 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP4(EMPSYD) | Outage | Thermal | Constraint Automation
N::V_DDSM_UTMS | 0.41667 | 0 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit for trip of Upper Tumut - Murray (65) line | Outage | Transient Stability | NSW
NC_N_LD02 | 0.41667 | 0.25 | Non Conformance Constraint for Liddell LD02 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_SNOWYP | 0.41667 | 0 | Non Conformance Constraint for Lower Tumut Pump | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE5 | 0.41667 | 0.5 | Non Conformance Constraint for Gladstone 5 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_KAREEYA2 | 0.41667 | 0 | Non Conformance Constraint for Kareeya 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_ROMA_7 | 0.41667 | 0 | Non Conformance Constraint for Roma 7 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_ROMA_8 | 0.41667 | 0 | Non Conformance Constraint for Roma 8 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_YABULU2 | 0.41667 | 0.25 | Non Conformance Constraint for Yabulu 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_LKBONNY1 | 0.41667 | 0 | Non Conformance Constraint for Lake Bonney 1 Wind Farm | Other | Non-Conformance | Non-Conformance
NC_S_TORRB4 | 0.41667 | 0.33333 | Non Conformance Constraint for Torrens B4 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_LTYS_1 | 0.41667 | 9.3333 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_SAPHWF1_56WT | 0.41667 | 0 | Constraint to violate if Sapphire WF turbines On greater than 56. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q>CPWO1_CPWU_CPWO2 | 0.41667 | 0 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (814) line, Feedback | Outage | Thermal | Qld
Q_MEWF1_ZERO | 0.41667 | 1.0833 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S_IBR_LB_600 | 0.41667 | 0 | Discretionary upper limit of 600 MW for SA non-synchronous generation excluding Lake Bonney 1,2,3 and Canunda | Outage | Discretionary | SA
S_NBH_0 | 0.41667 | 9.5833 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | Unit Zero | SA
S_SNOW_N+S_190 | 0.41667 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 190 MW | Outage | Discretionary | SA
T_V_BL_GT_300_E | 0.41667 | 0 | Direction to greater than 300 MW for Basslink (Tas to Vic), for Predispatch | Outage | Other | Tas
V::S_HYSE_MG_PPGT1 | 0.41667 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors I/S). Co-optimised eq PPGT1 LHS | Outage | Transient Stability | SA
V::S_SETB_MG_PPGT2 | 0.41667 | 0 | Out= one South East -Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT2 + DPV trip) in SA (SE Cap Available). (NOTE: with one Black Range series capacitors I/S. Co-optimised eq PPGT2 LHS | Outage | Transient Stability | SA
V_BULGANAWF_FLT_40 | 0.41667 | 40.9167 | Limit Bulgana Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KM_TX | 0.41667 | 0 | Out =One Kiamal 220/33 kV Transformer, manage continuous rating on remaining transformer | Outage | Thermal | Vic
N_WR_57_WT-INV | 0.41667 | 0 | Constraint to violate if White Rock wind/solar farm wind turbine + inverter availability greater than 57. Dispatch only. swamped out otherwise. DS only. | Outage | System Strength | NSW
NSA_V_BDL0xxx | 0.33333 | 2.1667 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Network Support | Vic
#BARKIPS1_E | 0.33333 | 0 | SBPS1B.ENERGY * 1 >= 70 (Wt = 360) | Other | DEFAULT | Quick
#BDL01_E | 0.33333 | 0 | VMWT2.ENERGY * 1 >= 43 (Wt = 35) | Other | DEFAULT | Quick
N>>NIL_DPTX_LV | 0.33333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
N>>V_NIL_66_65 | 0.33333 | 0 | Out = Nil, avoid Lower Tumut to Murray(66) using 15 mins rating O/L on Upper Tumut to Murray(65) trip; (Note: Swamped when TL 64 is O/S) | NIL | Thermal | NSW
NC_N_BW03 | 0.33333 | 0 | Non Conformance Constraint for Bayswater 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE3 | 0.33333 | 0.33333 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE4 | 0.33333 | 0.91667 | Non Conformance Constraint for Gladstone 4 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_MWPS3PV1 | 0.33333 | 0 | Non Conformance Constraint for MORGAN-WHYALLAPS3 | Other | Non-Conformance | Non-Conformance
NC_V_LYA1 | 0.33333 | 0 | Non Conformance Constraint for Loy Yang A1 Power Station | Other | Non-Conformance | Non-Conformance
N_METZSF_0INV | 0.33333 | 0 | Constraint to violate if Metz Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_MOREESF1_0INV | 0.33333 | 0.33333 | Constraint to violate if Moree Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_MOREESF1_40INV | 0.33333 | 0 | Constraint to violate if Moree Solar Farm inverter availability greater than 40. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_V_HV1500 | 0.33333 | 0 | Discretionary constraint on transfer from NSW to VIC of 1500 MW on DDTS-NSW cutset | Outage | Discretionary | NSW
N_WR_30_WT-INV | 0.33333 | 0.25 | Constraint to violate if White Rock wind/solar farm wind turbine + inverter availability greater than 30. Dispatch only. swamped out otherwise. DS only. | Outage | System Strength | NSW
Q::N_ARSVC_AR_2L-G | 0.33333 | 3.5 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
Q>ISTX | 0.33333 | 0 | Out = Isis T2 132/66 kV transformer, limit Childers Solar Farm to 46MW to prevent overload on remaining transformer | Outage | Thermal | Qld
S-MAPS2-PV_0 | 0.33333 | 0 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 2 PV (Palmer) generation of 0 MW | Outage | Unit Zero | SA
S>>PARB_TWPA_TPRS | 0.33333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>>TPRS_RBPA_RBTU | 0.33333 | 0 | Out= Templers-Roseworthy 132kV line, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
S>V_RBNW_RBMWP3 | 0.33333 | 2.8333 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage | Thermal | SA
S_DCBUS_DC2 | 0.33333 | 0 | Outage of Dry Creek 66kV bus section, DRYCGT2<=0 | Outage | Unit Zero | SA
S_DC_CBG3 | 0.33333 | 0 | Outage of Dry Creek 66kV CB G3, DRYCGT3<=0 | Outage | Unit Zero | SA
S_ISLE_LKB1+2+3_40 | 0.33333 | 0 | Discretionary upper limit on Lake Bonney (1+2+3) windfarms<=40 MW & No. in-service wind turbines for LKB at 14 Turbines.(Note otherwise, LKB 2+3 +1 will be constrained to 0 MW) | Outage | Discretionary | SA
T>T_NIL_BL_110_8_1 | 0.33333 | 0.083333 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Thermal | Tas
VS_050 | 0.33333 | 0.5 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Discretionary | Vic
V_KIAMSF_DYN | 0.33333 | 0 | Out = Kiamal Syncon, Limit Kiamal solar farm to 100 MW when Murra Warra 2 WF syncon I/S. Limit Kiamal solar farm to 50 MW when Murra Warra 2 WF syncon O/S | Outage | Discretionary | Vic
#MOREESF1_E | 0.25 | 0 | NMR41M.ENERGY * 1 <= 40 (Wt = 35) | Other | DEFAULT | Quick
#MTMILLAR_E | 0.25 | 0 | SMTM1.ENERGY * 1 <= 6 (Wt = 35) | Other | DEFAULT | Quick
#SAPHWF1_E | 0.25 | 0 | NSAP1S.ENERGY * 1 <= 187 (Wt = 35) | Other | DEFAULT | Quick
#T-V-MNSP1_RAMP_E_F | 0.25 | 0.75 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other | Ramping | Quick
#TARONG#1_E | 0.25 | 0 | QTRN1.ENERGY * 1 <= 330 (Wt = 35) | Other | DEFAULT | Quick
#TORRB2_E | 0.25 | 0 | STSB2.ENERGY * 1 >= 70 (Wt = 360) | Other | DEFAULT | Quick
CA_SYDS_5233E05E_1 | 0.25 | 0 | Constraint Automation, O/L XFMR T_2@R_TOWN@SA for CTG LSIR on trip of R_TOWN - TUNKIL 275KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N>>N-NIL_64 | 0.25 | 0.58333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | Thermal | NSW
N>N-WLMP_A | 0.25 | 0 | Out = Wellington to Mt_Piper line (72), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Wollar (79), Feedback | Outage | Thermal | NSW
N>WLTX_94T_WLTX | 0.25 | 0 | Out= one of the Wellington 132/330kV Transformers, avoid O/L on Molong to Orange North (94T) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
NC_N_BW02 | 0.25 | 0.41667 | Non Conformance Constraint for Bayswater 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_BW04 | 0.25 | 0 | Non Conformance Constraint for Bayswater 4 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_CRWASF1 | 0.25 | 3.5833 | Non Conformance Constraint for COROWA SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_N_WELLSF1 | 0.25 | 0.66667 | Non Conformance Constraint for WELLINGTON SF | Other | Non-Conformance | Non-Conformance
NC_S_BOLIVPS1 | 0.25 | 0 | Non Conformance Constraint for BOLIVARPOWERSTATION1 | Other | Non-Conformance | Non-Conformance
N_BANGOWF2_ZERO | 0.25 | 0 | Bango 999 wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_COLEASF1_FLT_30 | 0.25 | 40.6667 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_WAGGNSF1_ZERO | 0.25 | 0 | Wagga North solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_WALGR_BAT_L_ZERO | 0.25 | 0 | Wallgrove Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | NSW
Q_NQ_SEMI_ZERO | 0.25 | 0 | Limit all North Qld semi-scheduled generators to zero | Outage | Unit Zero | Qld
Q_STR_7C2K_CLRSF_5 | 0.25 | 0 | No limit to Clare Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_5 | 0.25 | 0 | No limit to Daydream Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HAMSF_5 | 0.25 | 0 | No limit to Hamilton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HAYSF_5 | 0.25 | 0 | No limit to Hayman Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KEP_5 | 0.25 | 0 | No limit to Kennedy Energy Park if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KIDSF_5 | 0.25 | 0 | No limit to Kidston Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_RRSF_5 | 0.25 | 0 | No limit to Ross River Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_5 | 0.25 | 0 | No limit to Whitsunday Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
S>>CNRB_RBTU_WTTP | 0.25 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_BWMP_WTTP | 0.25 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
S^NIL_SA_NORTH | 0.25 | 0 | Out = NIL, Manage voltage collapse in northern SA for the trip of one 275kV line between Davenport-Para or Davenport-Tungkillo.(Note:for both DV + RB Syn Cons are I/S, OR one DV Syn Con O/S, OR one RB Syn Con O/S, OR one DV +RB Syn Con O/S) | NIL | Voltage Stability | SA
S_PPT_0 | 0.25 | 0 | Pelican Pt Power Station out of service | Outage | Unit Zero | SA
T>>T_NIL_BL_EXP_5F | 0.25 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
T_CTHLWF_080 | 0.25 | 0 | Wild Cattle Hill Wind Farm upper limit of 80 MW | Outage | Discretionary | Tas
V::V_1900 | 0.25 | 0.33333 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
V>>V_BUDP_6 | 0.25 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V>>V_NIL1A_R | 0.25 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL | Thermal | Vic
V>>V_NIL_14 | 0.25 | 39.75 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V_GANWR_BAT_G_FLT_0 | 0.25 | 0 | Limit Gannawarra Battery (Generation Component) upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#BANGOWF1_E | 0.16667 | 4.1667 | NBA21B.ENERGY * 1 <= 155 (Wt = 360) | Other | DEFAULT | Quick
#BBTHREE3_E | 0.16667 | 0.083333 | TBB13.ENERGY * 1 <= 25 (Wt = 360) | Other | DEFAULT | Quick
#DARLSF1_E | 0.16667 | 45.0833 | NDNS1D.ENERGY * 1 <= 275 (Wt = 360) | Other | DEFAULT | Quick
#OAKEY1SF_E | 0.16667 | 0 | QTKS1O.ENERGY * 1 <= 24 (Wt = 35) | Other | DEFAULT | Quick
#TARONG#2_E | 0.16667 | 0 | QTRN2.ENERGY * 1 <= 330 (Wt = 35) | Other | DEFAULT | Quick
CA_BRIS_5120191F_1 | 0.16667 | 0 | Constraint Automation, O/L 0X1:L0X1:I:220@BURONGA@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORVM1] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
CA_BRIS_51201D29_1 | 0.16667 | 0 | Constraint Automation, O/L 0X1:L0X1:I:220@BURONGA@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORVM1] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
N::Q_RGSW_KC | 0.16667 | 0 | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N>>N-NIL_996_IN | 0.16667 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL | Thermal | NSW
N>>V-NIL_0X1 | 0.16667 | 0.58333 | Out= NIL, avoid O/L Buronga to Red cliffs (OX1) on Nil trip, Feedback | NIL | Thermal | NSW
N>>V_NIL_65_66 | 0.16667 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL | Thermal | NSW
NC_N_MP1 | 0.16667 | 1.8333 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE2 | 0.16667 | 0.33333 | Non Conformance Constraint for Gladstone 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#2 | 0.16667 | 0 | Non Conformance Constraint for Tarong 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_PPCCGT | 0.16667 | 0.41667 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance | Non-Conformance
NC_T_DEVILS_G | 0.16667 | 0 | Non Conformance Constraint for Devils Gate Power Station | Other | Non-Conformance | Non-Conformance
NC_T_LI_WY_CA | 0.16667 | 0.083333 | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations | Other | Non-Conformance | Non-Conformance
NC_V_GANNSF1 | 0.16667 | 1.6667 | Non Conformance Constraint for GANNAWARRA SOLAR | Other | Non-Conformance | Non-Conformance
NC_V_YWPS3 | 0.16667 | 1.4167 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance | Non-Conformance
N_BKHSF_44INV | 0.16667 | 1.3333 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 44. Constraint swamp out if number of inverter available not exceed 44. This is to manage voltage oscillation. DS only | Outage | System Strength | NSW
N_GNNDHSF1_ZERO | 0.16667 | 0.16667 | Gunnedah solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_SEBSF1_0INV | 0.16667 | 0 | Constraint to violate if Sebastopol Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q:NIL_CS | 0.16667 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Transient Stability | Qld
Q>>NIL_CLWU_RGLC | 0.16667 | 3.4167 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL | Thermal | Qld
Q_HASMME_RAMP_ZERO | 0.16667 | 0 | Ramp Haughton, Sun Metals, Kaban and Mt Emerald generators to zero and hold at zero. | Outage | Unit Zero | Qld
Q_KMBG_7184 | 0.16667 | 0 | Out= 7184 Kamerunga Barron Gorge PS 132kV line | Outage | Unit Zero | Qld
Q_MIDDLSF1_ZERO | 0.16667 | 0 | Middlemount Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_NIL_STRGTH_SSNRV | 0.16667 | 0 | Limit Susan River SF to 25 inverters on trip of Maryborough 66kV CB E352. (managed by Ergon Fast Tripping scheme by tripping inverter strings in less than 200ms when CB E352 trips) | NIL | System Strength | Qld
Q_STR_7C2K_DAYSF_2 | 0.16667 | 1.0833 | Limit 80% to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_KIDSF_2 | 0.16667 | 5.9167 | Limit 80% to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S>>BWMP_BGBR_HUWT | 0.16667 | 0.83333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | Thermal | SA
S>>CGTB1_TBTU_TBMO | 0.16667 | 22.75 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>DVBL_TWPA_TPRS | 0.16667 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>>MKRB_BWPA_BRTW | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBTX1_WTHU_02 | 0.16667 | 0 | Out= Robertstown 132/275kV TX1 + Waterloo-Hummocks 132kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
S>NIL_NIL_NWMH2 | 0.16667 | 0.5 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
SA_IBR_1800 | 0.16667 | 0 | Discretionary upper limit of 1800 MW for SA non-synchronous generation | Outage | Discretionary | SA
SVML_FLT_125 | 0.16667 | 35 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
S_TIPSB4+PV_190 | 0.16667 | 0 | Discretionary upper limit for TIPSB4 +SA rooftop PV trip <=190 MW. NOTE: Refer to SO_OG_SA_12 section 4.4 | Outage | Discretionary | SA
T>>T_NIL_BL_EXP_6E | 0.16667 | 0 | Out = Nil, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
T_T_TI_GH_RC12_250 | 0.16667 | 29.3333 | Discretionary 250 MW upper limit on Tribute, Granville Harbour, Reece 1 and 2 generation | Outage | Discretionary | Tas
V::N_DDMB_xxx | 0.16667 | 3.75 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_HWCB_xxx | 0.16667 | 0.41667 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_ROSM_xxx | 0.16667 | 3 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V>>N-LTMS_4 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L(15m rating) on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Thermal | Vic
V>>SML_NIL_7B | 0.16667 | 0 | Out = Nil, avoid O/L Buangor to Ararat 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL | Thermal | Vic
V>SML_NSWRB_10 | 0.16667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Thermal | Vic
V^^N_LTYS_MNYS_1 | 0.16667 | 0 | Out = 3 (Lower Tumut to Yass) 330kV line and 5 (Marulan to Yass) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_MOORBWF_50WT | 0.16667 | 0 | Limit Moorabool Wind Farm upper limit to 0 MW if number of turbine ON exceed 50. Constraint swamp out if number of turbine ON not exceed 50. DS only | Outage | System Strength | Vic
N_FINLYSF1_ZERO | 0.16667 | 4.1667 | Finley solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_HILLSTSF1_0INV | 0.16667 | 0 | Constraint to violate if Hillston solar farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
#LBBL1_E | 0.083333 | 0 | SLBB2L.ENERGY * 1 = 15 (Wt = 360) | Other | DEFAULT | Quick
#LILYSF1_E | 0.083333 | 0 | QBDR1L.ENERGY * 1 <= 100 (Wt = 360) | Other | DEFAULT | Quick
#SA1_E_20221109 | 0.083333 | 0 | Multiple SA1 LHS <= 220 (Wt = 35) | Other | DEFAULT | Quick
#SNUG1_E | 0.083333 | 0 | SSGA1.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
#V-S-MNSP1_RAMP_E_F | 0.083333 | 0 | V-S-MNSP1 <= MAX(0, InitialFlow - 25) (Wt=35) | Other | Ramping | Quick
CA_SYDS_5125A47F_1 | 0.083333 | 0 | Constraint Automation, O/L X3:LX3:I:220@BALRANLD@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP4(EMPSYD) | Outage | Thermal | Constraint Automation
N::V_NIL_MSDD | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | NIL | Transient Stability | NSW
N:V_NIL_BWRG | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | NIL | Transient Stability | NSW
N>>N-NIL_2XN | 0.083333 | 0 | Out=Nil, avoid O/L Collector to Marulan (4) on trip of Yass to Marulan (5) line, Feedback | NIL | Thermal | NSW
N>>UTRV-6X_64_1 | 0.083333 | 0 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, avoid O/L Lower Tumut to Upper Tumut (64) on trip of Upper Tumut to Stockdill (1) line, Feedback | Outage | Thermal | NSW
N>>V_DBUSS_4 | 0.083333 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage | Thermal | NSW
N>N-9GM_9GL_NIL | 0.083333 | 0 | Out= Bango999 WF to Yass 132kV line(9GM), avoid O/L Bango973 to Yass (9GL) on trip of Nil, Feedback | NIL | Thermal | NSW
NC_N_GUTHEGA | 0.083333 | 0 | Non Conformance Constraint for Guthega Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_BARRON-1 | 0.083333 | 0.083333 | Non Conformance Constraint for Barron Gorge 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_CALL_B_1 | 0.083333 | 0 | Non Conformance Constraint for Callide B_1 | Other | Non-Conformance | Non-Conformance
NC_Q_CALL_B_2 | 0.083333 | 0.083333 | Non Conformance Constraint for Callide B_2 | Other | Non-Conformance | Non-Conformance
NC_Q_COOPGWF1 | 0.083333 | 0.083333 | Non Conformance Constraint for COOPERS GAP WF | Other | Non-Conformance | Non-Conformance
NC_Q_DDPS1 | 0.083333 | 0.33333 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_KPP_1 | 0.083333 | 0.5 | Non Conformance Constraint for Kogan Creek Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-1 | 0.083333 | 0 | Non Conformance Constraint for Stanwell STAN-1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-2 | 0.083333 | 0.083333 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#3 | 0.083333 | 0.083333 | Non Conformance Constraint for Tarong 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_YARANSF1 | 0.083333 | 0 | Non Conformance Constraint for YARRANLEA SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_S_OSB-AG | 0.083333 | 0.75 | Non Conformance Constraint for Osborne Power Station | Other | Non-Conformance | Non-Conformance
NC_S_SNOWTWN1 | 0.083333 | 0 | Non Conformance Constraint for Snowtown Wind Farm | Other | Non-Conformance | Non-Conformance
NC_S_TORRB2 | 0.083333 | 0 | Non Conformance Constraint for Torrens B2 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_BALBG1 | 0.083333 | 0.66667 | Non Conformance Constraint for BALLARAT BATT (GEN) | Other | Non-Conformance | Non-Conformance
NC_V_BDL01 | 0.083333 | 0 | Non Conformance Constraint for Bairnsdale 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_CHYTWF1 | 0.083333 | 0 | Non Conformance Constraint for CHERRY TREE WF | Other | Non-Conformance | Non-Conformance
N_LIMOSF11_ZERO | 0.083333 | 42.1667 | Limondale 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_METZSF_40INV | 0.083333 | 0 | Constraint to violate if Metz Solar Farm inverter availability greater than 40. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_METZSF_ZERO | 0.083333 | 0 | Metz Solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_MOREESF1_040 | 0.083333 | 0 | Moree Solar Farm upper limit of 40 MW | Outage | System Strength | NSW
N_V_HV1150 | 0.083333 | 0 | Discretionary constraint on transfer from NSW to VIC of 1150 MW on DDTS-NSW cutset | Outage | Discretionary | NSW
N_WRSF1_ZERO | 0.083333 | 0 | White Rock solar farm upper limit of 0 MW and all inverters disconnected | Outage | Unit Zero | NSW
N_WR_0WT-0INV | 0.083333 | 0 | Constraint to violate if White Rock WF turbines On or White Rock SF Inverters available greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q>>CLWU_BCCP_LCCP | 0.083333 | 0 | Out= Calvale to Wurdong (871), avoid O/L Larcom Creek to Calliope River (8859) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
Q>>CPST_BCRG_CLWU | 0.083333 | 6.0833 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
Q>COL_CBEB05Q00 | 0.083333 | 0 | Out = Collinsville North 33kV bus coupler CB EB05Q00, limit Collinsville Solar Farm to 33.9 MW to prevent overload on RMU of no 1 transformer | Outage | Thermal | Qld
Q_CLERMSF1_ZERO | 0.083333 | 0.33333 | Clermont Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_KA_1TX | 0.083333 | 0 | Out= Kareeya Power Station 1 132/11/11kV transformer | Outage | Unit Zero | Qld
Q_STR_7C2K_CLRSF_2 | 0.083333 | 3.25 | Limit 80% to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_WARWSF2_16 | 0.083333 | 0 | Warwick Solar Farm 2 upper limit of 16 MW | Outage | Discretionary | Qld
S-SNPT_0 | 0.083333 | 0 | Snapper Pt Power Station out of service | Outage | Unit Zero | SA
S-WP_0 | 0.083333 | 0 | Discretionary upper limit for Wattle Point windfarm generation of 0 MW | Outage | Unit Zero | SA
S>>CNRB_BRTW_WTTP | 0.083333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
S>>CNRB_MKRB_DVBR | 0.083333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Davenport-Brinkworth 275kV line on trip of Mokota-Robertstown 27kV line(this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S>>MOTB_TBTU_TBCG | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>RBTX1_NIL_RBTX2 | 0.083333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Robertstown 275/132kV TX2 on Nil trip, Feedback | NIL | Thermal | SA
S>>SETB_TBSE_KHKN_1 | 0.083333 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith-Kincraig 132kV Line on trip of other Tailem Bend-South East 275kV line, (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
S>>V_NIL_NIL_RBNW1 | 0.083333 | 5.3333 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | Thermal | SA
S>>X_RBPA+RBTX2_05 | 0.083333 | 0 | Out= Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown-Morgan Whyalla 4 (1) on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
S>>X_RBPA+RBTX2_13 | 0.083333 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Templers-Roseworthy 132 kV on trip of Templers West-Para 275 kV line, Feedback | Outage | Thermal | SA
S>>X_RBTU+HUWT_23 | 0.083333 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Redhill T-Brinkworth 132kV line on trip of Bungama 132/275 kV TX, Feedback | Outage | Thermal | SA
S>LFTI_PPPW_LFTX4 | 0.083333 | 0.83333 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX4 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Thermal | SA
S>LFTI_PPPW_NOTI4 | 0.083333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L New Osborne-TIPS #4 66kV line, on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Thermal | Constraint Automation - RT
S>NIL_HUWT_STBG2 | 0.083333 | 217.0833 | Out = Nil; avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=60 MW && when Dalymple Battery (i.e. both Gen and Load component) is I/S].[Note:Swamped when WTTPT<80 && DALR OFF OR DalrB OFF] | NIL | Thermal | SA
S>NIL_PL_GENMAX | 0.083333 | 0 | Out = Nil, Maximum generation at Port Lincoln Due to Port Lincoln-Yadnarie line rating. | NIL | Thermal | SA
SVML_-020 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of -20 MW | Outage | Discretionary | SA
S_BF_0 | 0.083333 | 0 | Discretionary upper limit for Bluff Windfarm generation of 0 MW | Outage | Unit Zero | SA
S_PLN_CB6210 | 0.083333 | 0 | Out=Port Lincoln CB6210 ( Generator transformer CB) | Outage | Unit Zero | SA
S_PPT+SNPT_225 | 0.083333 | 0 | SA Pelican Point + Snapper Point generation <= 225 MW | Outage | Discretionary | SA
S_TIPSB2+PV_110_180 | 0.083333 | 0 | Discretionary upper limit for TIPSB2 +SA rooftop PV trip <=180 MW. NOTE: Refer to SO_OG_SA_12 section 4.4 | Outage | Discretionary | SA
T>T_NIL_BL_5A | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Hadspen to Georgetown No. 1 220kV line (flow to North), feedback | NIL | Thermal | Tas
TV_000 | 0.083333 | 0 | Tas to Vic on Basslink upper limit of 0 MW | Outage | Discretionary | Tas
T_FARC1 | 0.083333 | 0 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
V::N_HWRO3_O1 | 0.083333 | 0 | Out = Hazelwood to Rowville No.3 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::N_HYMO_O1 | 0.083333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::S_TBCP1_MAXG | 0.083333 | 0 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage | Transient Stability | SA
V:S_570_OSC_AUTO | 0.083333 | 0 | Out = NIL (Note: with both Black Range series capacitors I/S), Upper transfer limit of 570 MW on VIC to SA on Heywood, Active only when I25 mode cannot be monitored. | NIL | Oscillatory Stability | Vic
V>>N-LTYS_CH | 0.083333 | 0.16667 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
V>>SML_NSWRB_11 | 0.083333 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Thermal | Vic
V>>SML_NSWRB_11_1 | 0.083333 | 0.16667 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Balranald to Buronga (X3) 220 kV line, feedback | NIL | Thermal | Vic
V>>V_NIL_21 | 0.083333 | 0 | Out= Nil, avoid O/L Kerang to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V>>V_NIL_22 | 0.083333 | 0 | Out= Nil, avoid O/L Wemen to Red Cliffs 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V>>V_NIL_3_SIPS | 0.083333 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, 5 min line rating, feedback. Swamp if SIPS not available | NIL | Thermal | Vic
V>>V_ROTS_TX_3A_R | 0.083333 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Thermal | Vic
V>SML_NSWRB_10_1 | 0.083333 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Buronga (X3) 220 kV line, feedback | NIL | Thermal | Vic
VSML_VFRB_OFF | 0.083333 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Other | Vic
V^^SML_NIL_3 | 0.083333 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Voltage Stability | Vic
V_T_BL_ZERO_E | 0.083333 | 0 | Direction to zero for Basslink (Vic to Tas) for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic

## Binding FCAS
Constraint Equation ID | 2022 Hours | 2021 Hours | Description | Type
F_I+LREG_0210 | 6886.4167 | 7901.25 | NEM Lower Regulation Requirement greater than 210 MW | NIL
F_I+RREG_0220 | 6654.25 | 7689.75 | NEM Raise Regulation Requirement greater than 200 MW | NIL
F_I+NIL_APD_TL_L5 | 5726.75 | 7127.9167 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_APD_TL_L60 | 5574.5 | 6785.6667 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R6 | 5453.1667 | 7559.25 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL
F_I+NIL_MG_R5 | 5231.6667 | 6579 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL
F_I+NIL_MG_R60 | 4710.6667 | 7075.9167 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL
F_T+NIL_ML_L6 | 4546.0833 | 2616.5 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T_AUFLS2_R6 | 4340.4167 | 4265.25 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL
F_T+NIL_ML_L60 | 4258.5 | 2558.4167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_I+NIL_APD_TL_L6 | 3593.5833 | 751.0833 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_T+NIL_ML_L5 | 2206.8333 | 1344.0833 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R60 | 1958.5 | 1585.25 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R60 | 1848.6667 | 522.1667 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L5 | 1846.9167 | 2029.4167 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_T+NIL_MG_R6 | 1827.25 | 445 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 1779.6667 | 1607.75 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 1727.75 | 2394.4167 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_T+NIL_MG_R5 | 1719.6667 | 404.8333 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 1628.25 | 1401.3333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_I+ML_L6_0400 | 1594 | 5952.5 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN++NIL_MG_R6 | 1515.0833 | 2389.25 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_T+NIL_MG_RECL_R5 | 1237 | 1486.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_TASCAP_LREG_0210 | 1167.9167 | 1483.3333 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T+LREG_0050 | 1158.4167 | 259.1667 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 1143.8333 | 1421.1667 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_TASCAP_RREG_0220 | 1139.1667 | 955.8333 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T+RREG_0050 | 1129 | 251.8333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 1118.0833 | 254.8333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 1115 | 258.5 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+RREG_0220 | 1089.9167 | 242.9167 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+LREG_0210 | 1061.0833 | 234.5833 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R6 | 1043.5833 | 1386.9167 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L6 | 1042.4167 | 328.25 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 1020.3333 | 247.5833 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 1015.6667 | 234.6667 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_T+NIL_WF_TG_R5 | 1010.25 | 1430.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 959.9167 | 255.5833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 947.9167 | 1525.0833 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_T+STH_NYR_ML_L60 | 881.3333 | 0 | Lower 60 sec requirement for South Tasmania for loss of Nyrstart load | Outage
F_MAIN++NIL_BL_L60 | 876.4167 | 1172.0833 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_MAIN++ML_L6_0400 | 816.9167 | 1166.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_MAIN+APD_TL_L6 | 812.1667 | 14.9167 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T+STH_NYR_ML_L6 | 767.0833 | 0 | Lower 6 sec requirement for South Tasmania for loss of Nyrstar load | Outage
F_I+TTS_TG_R5 | 720.5 | 89.1667 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_I+TTS_TG_R60 | 696.3333 | 91.75 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_T+STH_NYR_ML_L5 | 659.4167 | 0 | Lower 5 min requirement for South Tasmania for loss of Nyrstar load | Outage
F_T_NIL_MINP_R6 | 650.5 | 834.0833 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL
F_MAIN++LREG_0210 | 642.5 | 681.8333 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
F_T+MINS_LREG | 641.5 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS LREG FCAS procurement from south of Palmerston | Outage
F_T+MAXS_R6 | 622 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS R6 FCAS procurement from south of Palmerston | Outage
F_MAIN+NIL_DYN_RREG | 598.25 | 749.5833 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL
F_I+GFT_TG_R5 | 558.8333 | 265.0833 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_T++RREG_0050 | 529.25 | 473.25 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_I+GFT_TG_R60 | 478.8333 | 262.75 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_T+MINS_RREG | 452.25 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS RREG FCAS procurement from south of Palmerston | Outage
F_T+MAXS_R60 | 447.6667 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS R60 FCAS procurement from south of Palmerston | Outage
F_MAIN++RREG_0220 | 416 | 964 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
F_I+TTS_TG_R6 | 413.4167 | 19.25 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_T+MAXS_RREG | 342.6667 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS RREG FCAS procurement from south of Palmerston | Outage
F_T+MAXS_R5 | 332.5833 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS R5 FCAS procurement from south of Palmerston | Outage
F_T+MINS_L5 | 328.4167 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS L5 FCAS procurement from south of Palmerston | Outage
F_T++LREG_0050 | 295.3333 | 432.4167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_T+MINS_R5 | 291.5833 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS R5 FCAS procurement from south of Palmerston | Outage
F_MAIN+NIL_DYN_LREG | 263.1667 | 543.6667 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL
F_I+GFT_TG_R6 | 247.8333 | 40.3333 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_S++HYSE_L60 | 230.8333 | 122.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
F_Q++ARTW_L6 | 198 | 272.5 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
F_Q++ARTW_L60 | 195.75 | 267.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_S++HYSE_L6_1 | 191 | 31.5833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_T+MAXS_LREG | 169.1667 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS LREG FCAS procurement from south of Palmerston | Outage
F_MAIN++GFT_TG_R60 | 166.25 | 81.4167 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_ESTN+LREG_0210 | 162.75 | 0 | Eastern Lower Regulation Requirement greater than 210 MW | Outage
F_MAIN+ML_L6_0400 | 154.5833 | 237.0833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_S+LREG_0035 | 151.9167 | 0 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage
F_ESTN+ML_L6_0400 | 142 | 0 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_T+MINS_L60 | 137 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS L60 FCAS procurement from south of Palmerston | Outage
F_S+RREG_0035 | 131.5 | 0 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage
F_QNV+DYN_RREG | 113.5833 | 0 | Qld, NSW and Vic Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | Outage
F_MAIN+GFT_TG_R60 | 113.0833 | 8.8333 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+GFT_TG_R5 | 112.8333 | 8.3333 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_ESTN+MG_R6 | 110 | 0 | Raise 6 sec Service Requirement for Eastern Generation Event | Outage
F_ESTN+MG_R5 | 102.5 | 0 | Raise 5 min Service Requirement for Eastern Generation Event | Outage
F_MAIN++GFT_TG_R5 | 96.5 | 39.6667 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_T++NIL_MG_RECL_R60 | 94.4167 | 70.6667 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T+GTTE_TL_L6 | 90.5833 | 0.5 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_ESTN+MG_R60 | 88.9167 | 0 | Raise 60 sec Service Requirement for Eastern Generation Event | Outage
F_T+GTTE_TL_L60 | 88 | 0.5 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_S+SA_ISLE_R6_1 | 85 | 0 | Raise 6 sec Service Requirement for SA island | Outage
F_T++NIL_MG_RECL_R6 | 84.6667 | 77.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S+SA_ISLE_L6_1 | 84.4167 | 0 | Lower 6 sec Service Requirement for SA island | Outage
F_T++NIL_MG_RECL_R5 | 79.5833 | 120.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T+CSGO_TG_R5 | 75.3333 | 18.1667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_MAIN++TTS_TG_R60 | 71.8333 | 7.4167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_T+MINS_R60 | 69.75 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS R60 FCAS procurement from south of Palmerston | Outage
F_S+SNS_TG_R60 | 64 | 0 | Raise 60 sec Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line | Outage
F_S+OD_TL_L60 | 62.4167 | 0 | Lower 60 sec Service Requirement for SA island for loss of Olympic Dam | Outage
F_S+SA_ISLE_LB_L6_1 | 60.75 | 0 | Lower 6 sec Service Requirement for SA island | Outage
F_T++NIL_MG_R5 | 59.5 | 41.5 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S+SNS_TG_R5 | 58.6667 | 0 | Raise 5 min Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line | Outage
F_MAIN++GFT_TG_R6 | 55.8333 | 5.9167 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_ESTN+RREG_0220 | 54.9167 | 0 | Eastern Raise Regulation Requirement greater than 220 MW | Outage
F_T+CSGO_TG_R6_2 | 53.5 | 5.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage
F_Q++ARTW_L5 | 53.0833 | 122.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
F_QNV++MG_R60 | 53.0833 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_T++NIL_ML_L6 | 51 | 135.75 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_S+ML_L5 | 49.9167 | 0 | Lower 5 min Service Requirement for SA island for loss of Murraylink | Outage
F_S_HPRL_LREG-5MW | 48.9167 | 0 | Out= NIL, Hornsdale Battery (Load Component) LREG Requirement <= 5MW | Outage
F_S+PPT_R5 | 48 | 0 | Raise 5 min Service Requirement for SA island for loss of Pelican Point | Outage
F_S+SA_ISLE_LB_R6_1 | 47.9167 | 0 | Raise 6 sec Service Requirement for SA island | Outage
F_S+OD_TL_L5 | 46.5 | 0 | Lower 5 min Service Requirement for SA island for loss of Olympic Dam | Outage
F_S+PPT_R60 | 46.5 | 0 | Raise 60 sec Service Requirement for SA island for loss of Pelican Point | Outage
F_T++NIL_WF_TG_R5 | 41.8333 | 84.1667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+GFT_TG_R6 | 40.4167 | 0.33333 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_S+ML_L60 | 38.4167 | 0 | Lower 60 sec Service Requirement for SA island for loss of Murraylink | Outage
F_Q++ARTW_R60 | 37.0833 | 28.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_S+ML_R5 | 35.5833 | 0 | Raise 5 min Service Requirement for SA island for loss of Murraylink | Outage
F_QNV++MG_R6 | 34.5 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_I+BIP_ML_L6 | 34.3333 | 0 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL
F_T++NIL_ML_L60 | 33.6667 | 344.3333 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_Q++ARTW_R6 | 33.5833 | 25.4167 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
F_S+ML_R60 | 33.4167 | 0 | Raise 60 sec Service Requirement for SA island for loss of Murraylink | Outage
F_MAIN++ML_L6_APD_LD | 32.1667 | 32.0833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_S_HPRG_RREG-5MW | 32 | 0 | Out= NIL, Hornsdale Battery (Generation Component) RREG Requirement <= 5MW | Outage
F_MAIN++NIL_BL_L6 | 31.8333 | 149.75 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_T++NIL_WF_TG_R60 | 30.5 | 56.5833 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S++HYSE_L5 | 30.1667 | 0.83333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
F_T++NIL_MG_R60 | 29.6667 | 34.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN++TTS_TG_R5 | 29.0833 | 1.9167 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_QNV++ML_L6_0400 | 28.8333 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_I+ML_L6_APD | 28.0833 | 102.8333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_T+CSGO_TG_R60 | 27.25 | 18.25 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_MAIN+TTS_TG_R5 | 26.75 | 2.75 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_MAIN+TTS_TG_R60 | 26.5 | 3.4167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_ESTN+GFT_TG_R5 | 26 | 0 | Raise 5 min requirement for a Eastern Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | Outage
F_T+MAXS_L6 | 25.5833 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS L6 FCAS procurement from south of Palmerston | Outage
F_S_LBBL1_LREG | 24.9167 | 0 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 0MW | Outage
F_I+BIP_ML_L60 | 24.9167 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL
F_Q++8C_L6 | 24.8333 | 56.4167 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
F_Q++8E_L6 | 24.75 | 18.3333 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
F_Q++8C_L60 | 24.5833 | 56 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
F_Q++8E_L60 | 24.4167 | 18.75 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage
F_Q++BCDM_L6 | 24.4167 | 122.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
F_MAIN+ML_L6_APD | 24.3333 | 1.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_QNV++GFT_TG_R60 | 23.6667 | 0 | Raise 60 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage
F_Q++BCDM_L60 | 22.5833 | 126.25 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
F_I+94_96_TL_L60 | 22.5833 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load | Outage
F_I+94_96_TL_L6 | 22.5833 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load | Outage
F_S_DLBAT-L_L60 | 22.25 | 3.3333 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage
F_I+94_96_TL_L5 | 22.25 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load | Outage
F_S_DLBAT-G_R60 | 22.1667 | 3.4167 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage
F_S_LBBG1_RREG | 22.1667 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) RREG Requirement <= 0MW | Outage
F_S_DLBAT-G_R6 | 22.0833 | 3.4167 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage
F_S_DLBAT-G_R5 | 21.9167 | 2.9167 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage
F_Q++ARTW_R5 | 21.1667 | 5.5 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
F_ESTN+TTS_TG_R60 | 20.5833 | 0 | Raise 60 sec requirement for a Eastern Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | Outage
F_MAIN++ML_L6_APD | 20.1667 | 10.4167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_S+ML_L6_2_LB_0 | 19.6667 | 0 | Lower 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage
F_S_LBBG1_R60 | 19.1667 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) R60 Requirement <= 0MW | Outage
F_ESTN+TTS_TG_R5 | 19 | 0 | Raise 5 min requirement for a Eastern Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | Outage
F_ESTN+TTS_TG_R6 | 18.9167 | 0 | Raise 6 sec requirement for a Eastern Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | Outage
F_MAIN++TTS_TG_R6 | 18.8333 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_S_LBBG1_R5 | 18.6667 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) R5 Requirement <= 0MW | Outage
F_S_DLBAT-L_L6 | 18.5 | 3.3333 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage
F_S_DLBAT-L_L5 | 18.3333 | 3.3333 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage
F_T+MINS_R6 | 17.8333 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS R6 FCAS procurement from south of Palmerston | Outage
F_QNV++MG_R5 | 16.5 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_S_LBBL1_L6 | 15.6667 | 0 | Out= NIL, Lake Bonney Battery (Load Component) L6 Requirement <= 0MW | Outage
F_S_LBBL1_L5 | 15.6667 | 0 | Out= NIL, Lake Bonney Battery (Load Component) L5 Requirement <= 0MW | Outage
F_S_LBBG1_R6 | 15.4167 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) R6 Requirement <= 0MW | Outage
F_MAIN++94_96_TL_L60 | 15.0833 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink able transfer FCAS | Outage
F_ESTN+GFT_TG_R60 | 14.9167 | 0 | Raise 60 sec requirement for a Eastern Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | Outage
F_S_LBBL1_L60 | 14.6667 | 0 | Out= NIL, Lake Bonney Battery (Load Component) L60 Requirement <= 0MW | Outage
F_T++NIL_MG_R6 | 13.4167 | 18.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_WF_TG_R6 | 13.25 | 50.25 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_ESTN+GFT_TG_R6 | 12.8333 | 0 | Raise 6 sec requirement for a Eastern Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | Outage
F_S+PAREP_R5 | 11.75 | 0 | Raise 5 min Service Requirement for SA island for loss of Davenport - Pt Patterson 275kV line | Outage
F_T++NIL_ML_L5 | 11.5 | 1.9167 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_I+ML_L6_APD_LD | 11.5 | 97.0833 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_T+MINS_L6 | 11.1667 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS L6 FCAS procurement from south of Palmerston | Outage
F_T++CSGO_TG_R5 | 11 | 0.5 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_Q++8C_L5 | 10.5833 | 13.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
F_S+PAREP_R60 | 10.5 | 0 | Raise 60 sec Service Requirement for SA island for loss of Davenport - Pt Patterson 275kV line | Outage
F_T+FASH_N-2_RREG | 10.3333 | 16.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_MAIN++94_96_TL_L6 | 10.25 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink able transfer FCAS | Outage
F_S+TB2_R60_70M | 10 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B2 for 70 MW metro gen trip option | Outage
F_S+SNS_TG_R6_2_LB_0 | 10 | 0 | Raise 6 sec Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line (FFR ZERO) | Outage
F_ESTN++HYMO_L6 | 9.75 | 8.8333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
F_T+FARE_N-2_TG_R5 | 9.6667 | 6.75 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_ESTN++HYMO_L60 | 9.5 | 14 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_T+STH_MG_R5 | 9.1667 | 0 | Raise 5 min requirement for a South Tasmania Generation Event | Outage
F_T+STH_LREG | 9.1667 | 0 | Lower Regulation requirement for Southern Tasmania | Outage
F_T+STH_MG_R60 | 9.1667 | 0 | Raise 60 sec requirement for a South Tasmania Generation Event | Outage
F_ESTN++HYTR_L6 | 9.1667 | 0.41667 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_T+STH_MG_R6 | 9.0833 | 0 | Raise 6 sec requirement for a South Tasmania Generation Event | Outage
F_ESTN+ML_L5_0400 | 8.9167 | 0 | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage
F_I+ML_ST2_L60 | 8.6667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_T+STH_RREG | 8.6667 | 0 | Raise Regulation requirement for Southern Tasmania | Outage
F_S+TB2_R5_70M | 8.6667 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B2 for 70 MW metro gen trip option | Outage
F_I+ML_ST2_L6 | 8.6667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_MAIN+BIP_ML_L6 | 8.5833 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL
F_ESTN++HYTR_L60 | 8.5833 | 0.5 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_ESTN+ML_L60_0400 | 8.3333 | 0 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_T+STH_ML_L60 | 8.25 | 0 | Lower 60 sec requirement for a South Tasmania Load Event | Outage
F_T+FARE_N-2_RREG | 8.1667 | 1.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_T++CSGO_TG_R6 | 8 | 0.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_I+ML_ST2_L5 | 8 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_V+NIL_APD01_R60 | 7.8333 | 1.3333 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_T+NTH_ML_L6 | 7.8333 | 0 | Lower 6 sec requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_V+NIL_APD01_R6 | 7.8333 | 1.3333 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_V+NIL_APD01_R5 | 7.8333 | 1.3333 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_I+ML_L60_0400 | 7.75 | 57.5 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN++94_96_TL_L5 | 7.6667 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load, Basslink able to transfer FCAS | Outage
F_S_LBBG1_LREG | 7.6667 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) LREG Requirement <= 0MW | Outage
F_T+STH_ML_L6 | 7.6667 | 0 | Lower 6 sec requirement for a South Tasmania Load Event | Outage
F_S+TORRB4_R5 | 7.5 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B4 | Outage
F_S_LBBL1_RREG | 7.4167 | 0 | Out= NIL, Lake Bonney Battery (Load Component) RREG Requirement <= 0MW | Outage
F_T+NTH_MG_R6 | 7.3333 | 0 | Raise 6 sec requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS | Outage
F_T+NTH_MG_R60 | 7.3333 | 0 | Raise 60 sec requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS | Outage
F_T+NTH_MG_R5 | 7.3333 | 0 | Raise 5 min requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS | Outage
F_S+TB4_R60_70M | 7.1667 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B4 for 70 MW metro gen trip option | Outage
F_MAIN+ST2_ML_L6 | 6.9167 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_MAIN+ST2_ML_L60 | 6.9167 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_MAIN+ST2_ML_L5 | 6.9167 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_I+TL_L6_0700 | 6.75 | 0 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 700 | Outage
F_I+TL_L60_0700 | 6.75 | 0 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 700 | Outage
F_QNV++GFT_TG_R5 | 6.75 | 0 | Raise 5 min requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage
F_T++CSGO_TG_R60 | 6.75 | 0.16667 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_S+TORRB4_R60 | 6.5833 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B4 | Outage
F_S+TB2_R6_2_LB0_70M | 6.5 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B2 (FFR ZERO) for 70 MW metro gen trip option | Outage
F_S+TB4_R5_70M | 6.4167 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B4 for 70 MW metro gen trip option | Outage
F_MAIN+TTS_TG_R6 | 6.1667 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_I+TL_L5_0700 | 6.1667 | 0 | Lower 5 min Service Requirement for a NEM Network Event, TL = 700 | Outage
F_QNV++LREG_0210 | 5.8333 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage
F_S+SNS_TG_R6_3_LB_0 | 5.5 | 0 | Raise 6 sec Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line (FFR ZERO) | Outage
F_T+FARE_N-2_TG_R6_2 | 5.5 | 3.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_T+NTH_ML_L60 | 5.3333 | 0 | Lower 60 sec requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_MAIN+BIP_ML_L60 | 5.25 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL
F_T+NIL_BB_TG_R60 | 5.25 | 0 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T+NIL_BB_TG_R6 | 5.25 | 0 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T+CSGO_TG_R6_1 | 5.25 | 4.5 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage
F_I+ML_ST3_L6 | 5.1667 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_I+ML_L5_APD | 5.0833 | 4.3333 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_QNV++TTS_TG_R60 | 5 | 0 | Raise 60 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage
F_QNV++GFT_TG_R6 | 4.8333 | 0 | Raise 6 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage
F_ESTN+MCSH_TG_R5 | 4.75 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line | Outage
F_I+ML_L60_APD | 4.6667 | 4.6667 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage
F_I+ML_ST1_L6 | 4.4167 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_I+ML_ST3_L60 | 4.3333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_MAIN+ML_L5_APD | 4.25 | 0.083333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_T+MAXS_L5 | 4.25 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS L5 FCAS procurement from south of Palmerston | Outage
F_MAIN+ML_L60_APD | 4.1667 | 0.083333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_QNV+LREG_0210 | 4.0833 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | Outage
F_I+ML_L5_0400 | 4.0833 | 53.5833 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL
F_QNV+ML_L6_0400 | 4.0833 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_QNV+MG_R6 | 3.8333 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_QNV++MCSH_TG_R60 | 3.8333 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage
F_T+FARE_N-2_TG_R60 | 3.8333 | 0.58333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_QNV+MCSH_TG_R5 | 3.6667 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink unable to transfer FCAS | Outage
F_QNV+MG_R60 | 3.5 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_QNV+MG_R5 | 3.5 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_T+NIL_BB_TG_R5 | 3.5 | 0 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T+FARE_N-2_TG_R6_1 | 3.3333 | 2.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_S+QPS5_R60 | 3.3333 | 0 | Raise 60 sec Service Requirement for SA island for loss of Quarantine 5 | Outage
F_S+QPS5_R5 | 3.3333 | 0 | Raise 5 min Service Requirement for SA island for loss of Quarantine 5 | Outage
F_T+NTH_ML_L5 | 3.25 | 0 | Lower 5 min requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_T+GTTE_TL_L5 | 3.0833 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_QNV++RREG_0220 | 3.0833 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink able transfer FCAS | Outage
F_S_LG2_L60 | 3 | 0 | Out= NIL, Ladbroke Grove Unit2 L60 Requirement <= 0MW | Outage
F_T+NTH_LREG | 2.9167 | 0 | Lower Regulation requirement for Northern Tasmania, Basslink unable to transfer FCAS | Outage
F_S+ML_R6_2_LB_0 | 2.9167 | 0 | Raise 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage
F_I+ML_ST3_L5 | 2.9167 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage
F_QNV+MCSH_TG_R60 | 2.9167 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink unable to transfer FCAS | Outage
F_QNV++MCSH_TG_R5 | 2.8333 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage
F_S+TB4_R6_2_LB0_70M | 2.6667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B4 (FFR ZERO) for 70 MW metro gen trip option | Outage
F_S_LG1_R6 | 2.5833 | 0 | Out= NIL, Ladbroke Grove Unit1 R6 Requirement <= 0MW | Outage
F_S_LG1_L60 | 2.5 | 0 | Out= NIL, Ladbroke Grove Unit1 L60 Requirement <= 0MW | Outage
F_T+MAXS_L60 | 2.5 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS L60 FCAS procurement from south of Palmerston | Outage
F_QNV++ML_L60_0400 | 2.4167 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_Q++LDTW_R60 | 2.3333 | 102.5 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_MAIN++TL_L60_0700 | 2.25 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage
F_S+RREG_0070 | 2.25 | 0 | SA Raise Regulation Requirement greater than 70 MW | Other
F_I+BIP_ML_L5 | 2.1667 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL
F_S+PAREP_R6_2_LB_0 | 2.0833 | 0 | Raise 6 sec Service Requirement for SA island for loss of Davenport - Pt Patterson 275kV line (FFR ZERO) | Outage
F_T+NTH_WF_TG_R6 | 1.9167 | 0 | Raise 6 sec requirement for North Tasmania for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | Outage
F_T+NTH_WF_TG_R60 | 1.8333 | 0 | Raise 60 sec requirement for North Tasmania for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | Outage
F_T+NTH_WF_TG_R5 | 1.8333 | 0 | Raise 5 min requirement for North Tasmania for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | Outage
F_T+NTH_RREG | 1.75 | 0 | Raise Regulation requirement for Northern Tasmania, Basslink unable to transfer FCAS | Outage
F_MAIN++MG_R6_0850 | 1.6667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
F_MAIN++MG_R5_0850 | 1.6667 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
F_MAIN++MG_R60_0850 | 1.6667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
F_QNV+DYN_LREG | 1.5833 | 0 | Qld, NSW and Vic Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | Outage
F_S_LG1_R60 | 1.5833 | 0 | Out= NIL, Ladbroke Grove Unit1 R60 Requirement <= 0MW | Outage
F_Q++LDTW_R6 | 1.5833 | 96.8333 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
F_Q++8E_L5 | 1.5833 | 9.9167 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
F_MAIN++BIP_ML_L6 | 1.5833 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
F_QNV+HYMO_L6 | 1.5 | 0.91667 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_ESTN+MCSH_TG_R60 | 1.5 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line | Outage
F_MAIN+ST3_ML_L60 | 1.5 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L6_APD_LD | 1.5 | 3.25 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage
F_QNV+HYMO_L60 | 1.5 | 1.25 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+ST3_ML_L6 | 1.5 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_MAIN+ST3_ML_L5 | 1.5 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_S_LG1_L5 | 1.5 | 0 | Out= NIL, Ladbroke Grove Unit1 L5 Requirement <= 0MW | Outage
F_S_LG1_L6 | 1.5 | 0 | Out= NIL, Ladbroke Grove Unit1 L6 Requirement <= 0MW | Outage
F_Q++BCDM_R60 | 1.5 | 7.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
F_MAIN+MG_R5_0850 | 1.4167 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 850, Basslink unable to transfer FCAS | Outage
F_MAIN+MG_R6_0850 | 1.4167 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink unable to transfer FCAS | Outage
F_S+TORRB2_R60 | 1.4167 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B2 | Outage
F_S_LG2_L6 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 L6 Requirement <= 0MW | Outage
F_T++NTH_LREG | 1.4167 | 0 | Lower Regulation requirement for Northern Tasmania, Basslink able to transfer FCAS | Outage
F_MAIN+MG_R60_0850 | 1.4167 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink unable to transfer FCAS | Outage
F_S_LG2_R6 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 R6 Requirement <= 0MW | Outage
F_S_LG2_L5 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 L5 Requirement <= 0MW | Outage
F_S_LG2_R60 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 R60 Requirement <= 0MW | Outage
F_Q++BCDM_L5 | 1.3333 | 34.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
F_QNV++HYMO_L60 | 1.3333 | 0.91667 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+BB_N-2_TG_R5 | 1.3333 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_S+TORRB2_R5 | 1.25 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B2 | Outage
F_QNV++MCSH_TG_R6 | 1.25 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage
F_S+TB2_R6_3_LB0_70M | 1.25 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B2 (FFR ZERO) for 70 MW metro gen trip option | Outage
F_QNV+RREG_0220 | 1.25 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink unable to transfer FCAS | Outage
F_Q++8E_R60 | 1.1667 | 0.16667 | Out = Sapphire to Armidale (8E) line, Qld Raise 60 sec Requirement | Outage
F_S+TB4_R6_3_LB0_70M | 1.1667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B4 (FFR ZERO) for 70 MW metro gen trip option | Outage
F_MAIN++BIP_ML_L60 | 1.1667 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
F_MAIN++ML_L5_0400 | 1.1667 | 3.75 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_Q++8E_R6 | 1.1667 | 0.25 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage
F_S_LG1_R5 | 1.0833 | 0 | Out= NIL, Ladbroke Grove Unit1 R5 Requirement <= 0MW | Outage
F_I+NIL_BB_TG_R6 | 1.0833 | 0 | Out= Nil, Global Raise 6 sec requirement for loss of a Bell Bay to George Town line | NIL
F_I+NIL_WF_TG_R60 | 1.0833 | 0 | Out= Nil, Global Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line | NIL
F_I+NIL_BB_TG_R60 | 1.0833 | 0 | Out= Nil, Global Raise 60 sec requirement for loss of a Bell Bay to George Town line | NIL
F_I+NIL_WF_TG_R6 | 1.0833 | 0 | Out= Nil, Global Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line | NIL
F_S_LG2_R5 | 1.0833 | 0 | Out= NIL, Ladbroke Grove Unit2 R5 Requirement <= 0MW | Outage
F_Q++BCDM_R6 | 1 | 8.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
F_QNV++TTS_TG_R5 | 1 | 0 | Raise 5 min requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage
F_MAIN++ML_L5_APD | 0.91667 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_QNV+ML_L5_0400 | 0.91667 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_MAIN++TL_L5_0700 | 0.83333 | 0 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage
F_QNV++HYTR_L6 | 0.83333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++NIL_R60 | 0.83333 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL
F_ESTN++HYMO_L5 | 0.83333 | 1.6667 | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
F_T+GO_C752_TG_R5 | 0.83333 | 0 | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_Q++8C_R6 | 0.75 | 7.1667 | Out = Armidale to Dumaresq (8C), Qld Raise 6 sec Requirement | Outage
F_Q++8C_R60 | 0.75 | 7.0833 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage
F_QNV++ML_L5_0400 | 0.75 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_MAIN++ST2_ML_L6 | 0.66667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_MAIN++ST1_ML_L6 | 0.66667 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_MAIN++ST2_ML_L60 | 0.66667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_STHN++ARTW_L60 | 0.66667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage
F_ESTN+MO_TG_R5 | 0.66667 | 2.6667 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line | Outage
F_T+FASH_N-2_TG_R5 | 0.66667 | 9.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_N_ER02_RREG | 0.58333 | 0 | Out= NIL, Eraring 2 RREG Requirement <= 0MW | Outage
F_N_ER04_RREG | 0.58333 | 0 | Out= NIL, Eraring 4 RREG Requirement <= 0MW | Outage
F_S+HL_TG_R60 | 0.58333 | 0 | Raise 60 sec Service Requirement for SA island for loss of Canowie to Hallett 275 kV line | Outage
F_QNV+TTS_TG_R60 | 0.58333 | 0 | Raise 60 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | Outage
F_N_ER03_RREG | 0.58333 | 0 | Out= NIL, Eraring 3 RREG Requirement <= 0MW | Outage
F_MAIN+94_96_TL_L5 | 0.58333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load , Basslink unable transfer FCAS | Outage
F_MAIN+94_96_TL_L60 | 0.58333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink unable transfer FCAS | Outage
F_QNV+TTS_TG_R5 | 0.58333 | 0 | Raise 5 min requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | Outage
F_QNV+ML_L60_0400 | 0.58333 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_T+FASH_N-2_TG_R6_2 | 0.58333 | 8.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage
F_N_BW04_RREG | 0.58333 | 0 | Out= NIL, Bayswater 4 RREG Requirement <= 0MW | Outage
F_MAIN+ML_L60_0400 | 0.58333 | 3.5 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN+94_96_TL_L6 | 0.58333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink unable transfer FCAS | Outage
F_N_BW01_RREG | 0.58333 | 0 | Out= NIL, Bayswater 1 RREG Requirement <= 0MW | Outage
F_N_ER03_LREG | 0.58333 | 0 | Out= NIL, Eraring 3 LREG Requirement <= 0MW | Outage
F_MAIN++TL_L6_0700 | 0.58333 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage
F_N_ER04_LREG | 0.58333 | 0 | Out= NIL, Eraring 4 LREG Requirement <= 0MW | Outage
F_QNV+MCSH_TG_R6 | 0.58333 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink unable to transfer FCAS | Outage
F_QNV+MO_TG_R5 | 0.5 | 0.083333 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage
F_S+HL_TG_R5 | 0.5 | 0 | Raise 5 min Service Requirement for SA island for loss of Canowie to Hallett 275 kV line | Outage
F_MAIN++NIL_BL_L5 | 0.5 | 0 | Mainland Lower 5 min Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_S+PPT_R6_2_LB_0 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Pelican Point (FFR ZERO) | Outage
F_S++HYSE_L6_2 | 0.41667 | 4.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
F_S+NBH_TG_R5 | 0.41667 | 0 | Raise 5 min Service Requirement for SA island for loss of North Brown Hill windfarm to Belalie 275 kV line | Outage
F_N_LD01_LREG | 0.41667 | 0 | Out= NIL, Liddell 1 LREG Requirement <= 0MW | Outage
F_N_LD01_RREG | 0.41667 | 0 | Out= NIL, Liddell 1 RREG Requirement <= 0MW | Outage
F_MAIN+TL_L5_0700 | 0.41667 | 0 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 700, Basslink unable to transfer FCAS | Outage
F_MAIN++BIP_ML_L5 | 0.41667 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
F_QNV++MO_TG_R5 | 0.41667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line, Basslink able to transfer FCAS | Outage
F_N_LD04_LREG | 0.41667 | 0 | Out= NIL, Liddell 4 LREG Requirement <= 0MW | Outage
F_S+NBH_TG_R60 | 0.41667 | 0 | Raise 60 sec Service Requirement for SA island for loss of North Brown Hill windfarm to Belalie 275 kV line | Outage
F_MAIN+TL_L6_0700 | 0.41667 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink unable to transfer FCAS | Outage
F_N_LD04_RREG | 0.41667 | 0 | Out= NIL, Liddell 4 RREG Requirement <= 0MW | Outage
F_ESTN+MCSH_TG_R6 | 0.41667 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line | Outage
F_MAIN+TL_L60_0700 | 0.41667 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink unable to transfer FCAS | Outage
F_QNV++MO_TG_R60 | 0.33333 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line, Basslink able to transfer FCAS | Outage
F_N_LD02_RREG | 0.33333 | 0 | Out= NIL, Liddell 2 RREG Requirement <= 0MW | Outage
F_S+TORRB4_R6_2_LB_0 | 0.33333 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B4 (FFR ZERO) | Outage
F_MAIN++ML_L60_0400 | 0.33333 | 1.1667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_QNV++HYTR_L60 | 0.33333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_N_LD02_LREG | 0.33333 | 0 | Out= NIL, Liddell 2 LREG Requirement <= 0MW | Outage
F_S_HPRL_RREG-5MW | 0.33333 | 0 | Out= NIL, Hornsdale Battery (Load Component) RREG Requirement <= 5MW | Outage
F_QNV++TTS_TG_R6 | 0.33333 | 0 | Raise 6 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage
F_MAIN+ST1_ML_L6 | 0.33333 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage
F_T+CSGO_TG_R6_3 | 0.25 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment3 | Outage
F_T_FARC2_R6 | 0.25 | 0 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW | Outage
F_N_WALGR_BAT_G_R6 | 0.25 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise 6 sec Requirement <= 0MW | Outage
F_QNV++HYMO_L6 | 0.25 | 0.58333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_QNV+TTS_TG_R6 | 0.25 | 0 | Raise 6 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | Outage
F_T++FARE_N-2_TG_R6 | 0.25 | 10.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_N_WALGR_BAT_G_R5 | 0.25 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise 5 min Requirement <= 0MW | Outage
F_N_WALGR_BAT_G_R60 | 0.25 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise 60 sec Requirement <= 0MW | Outage
F_QNV+MO_TG_R60 | 0.16667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage
F_MAIN+BIP_ML_L5 | 0.16667 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL
F_T++FASH_N-2_TG_R60 | 0.16667 | 9.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_N_BW04_LREG | 0.16667 | 0 | Out= NIL, Bayswater 4 LREG Requirement <= 0MW | Outage
F_T++FASH_N-2_TG_R5 | 0.16667 | 8.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN++ST2_ML_L5 | 0.16667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_QNV++HYMO_L5 | 0.083333 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_N_MP2_RREG | 0.083333 | 0 | Out= NIL, MT Piper 2 RREG Requirement <= 0MW | Outage
F_MAIN+ML_L5_0400 | 0.083333 | 3.3333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T+NIL_TL_L5_DS | 0.083333 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_ESTN++HYTR_R60 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Raise 60 sec Requirement | Outage
F_MAIN++ST3_ML_L60 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_N_BW01_LREG | 0.083333 | 0 | Out= NIL, Bayswater 1 LREG Requirement <= 0MW | Outage
F_S+ML_L6_3_LB_0 | 0.083333 | 0 | Lower 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage
F_T++GTTE_TL_L6 | 0.083333 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T+GO_C752_TG_R60 | 0.083333 | 0 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_S+TORRB2_R6_3_LB_0 | 0.083333 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B2 (FFR ZERO) | Outage
F_MAIN+BLFCTRL_L60 | 0.083333 | 0 | Out = Nil, Lower 60 sec requirement for up to 100 MW fast response on Basslink for a Tasmanian event. | NIL
F_MAIN++ST3_ML_L5 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_MAIN++ST3_ML_L6 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
F_S+OD_TL_L6_2_LB_0 | 0.083333 | 0 | Lower 6 sec Service Requirement for SA island for loss of Olympic Dam (FFR ZERO) | Outage
F_T+FASH_N-2_TG_R6_1 | 0.083333 | 0.83333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage

## Binding Impact
Constraint Equation ID | 2022 Marginal Values | 2021 Marginal Values | 2022 Hours | 2021 Hours | Description | Type | Limit Type | Region
NSA_S_PORxxx | 36153196.4277 | 0 | 210.25 | 0 | Port Lincoln >= 15 MW for Network Support Agreement | Outage | Network Support | SA
N>NIL_94T | 27360028.1108 | 11942468.2359 | 1596.1667 | 844.0833 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | NIL | Thermal | NSW
N>NIL_969 | 15722420.9595 | 2412928.344 | 1256.4167 | 183.5 | Out= Nil, avoid O/L Gunnedah to Tamworth (969) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
N^^N_NIL_3 | 14868142.3154 | 6739547.4244 | 1485.8333 | 1245.25 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL | Voltage Stability | NSW
S>NIL_MHNW1_MHNW2 | 12209619.288 | 8487751.4099 | 1489.9167 | 1722.5833 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
N^N-LS_SVC | 9612752.5502 | 18564.6516 | 4465.4167 | 69.5 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; Swamp out when three directlink cables are O/S; TG formulation only | Outage | Voltage Stability | NSW
N>NIL_94K_1 | 9199302.2294 | 0 | 865.3333 | 0 | Out= Nil, avoid O/L Suntop Tee to Wellington (94K/1) on trip of Nil, Feedback | NIL | Thermal | NSW
Q^^N_NIL_SRAR | 9063740.7583 | 58348.4641 | 318.25 | 134 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
S_TORRB3_ZERO_E | 8790090.7643 | 0 | 86.6667 | 0 | Direction to zero for Torrens Island B #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
N>NIL_997_99A | 8401523.6931 | 2368768.4717 | 666.1667 | 235 | Out= Nil, avoid O/L Corowa to Albury 132kV line (997/1) on trip of Finley to Uranquinty 132kV line (99A), Feedback | NIL | Thermal | NSW
V^^N_NIL_1 | 8289426.8499 | 1639245.0945 | 389.6667 | 875 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
Q>NIL_EMCM_6056 | 7981726.0815 | 5497767.8756 | 952.25 | 475.5833 | Out= NIL, avoid thermal overload on Emerald to Comet (6056) 66 kV Feeder | NIL | Thermal | Qld
N_SITHE01_ZERO_E | 7935494.121 | 0 | 84.5833 | 0 | Direction to zero for Sithe for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
S^NIL_CRK+MTM_95 | 7572134.7857 | 0 | 351.8333 | 0 | Out= Nil, upper limit for Cathedral Rocks WF + Mt Millar WF <= 95 MW to maintain voltage stability limits | NIL | Voltage Stability | SA
S_TORRB2_ZERO_E | 7085534.152 | 0 | 77 | 0 | Direction to zero for Torrens Island B #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_PPCCGT_ZERO_E | 7038417.0674 | 0 | 76.9167 | 0 | Direction to zero for Pelican Point for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
N_URANQ11_ZERO_E | 6188872.8125 | 0 | 46.8333 | 0 | Direction to zero for Uranquinty #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_URANQ14_ZERO_E | 6177816.1073 | 0 | 46.5 | 0 | Direction to zero for Uranquinty #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_URANQ13_ZERO_E | 6177816.0947 | 0 | 46.5 | 0 | Direction to zero for Uranquinty #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_URANQ12_ZERO_E | 6177816.0878 | 0 | 46.5 | 0 | Direction to zero for Uranquinty #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
T_V_BL_ZERO_E | 5837308.1987 | 0 | 36.3333 | 0 | Direction to zero for Basslink (Tas to Vic) for Dispatch and Predispatch and NOT PASA | Outage | Other | Tas
V^^V_NIL_KGTS V^^V_NIL_KGTS_2 | 5625095.8078 | 2366922.9098 | 843.4167 | 349.5 | Out= Nil, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | NIL | Voltage Stability | Vic
V>>V_NIL_18 | 5493534.9084 | 1410266.0201 | 466 | 228.1667 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
V_MCKAY1_ZERO_E | 5351603.8407 | 0 | 64 | 0 | Direction to zero for McKay Creek for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
S>NIL_HUWT_STBG3 | 5214486.6843 | 168272.3386 | 375.0833 | 16 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Constraint Swamped when Wattle PT when generating >=60 MW) | NIL | Thermal | SA
V_NPS_ZERO_E | 5191865.7506 | 0 | 45.4167 | 0 | Direction to zero for Newport for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_DARTM1_ZERO_E | 5147604.314 | 0 | 64 | 0 | Direction to zero for Dartmouth for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
Q>NIL_YLMR | 4616408.0759 | 571931.6936 | 593.75 | 563.25 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
F_MAIN+NIL_DYN_RREG | 4510954.3132 | 384174.2696 | 525.25 | 749 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL | FCAS | FCAS
N_TUMUT3_ZERO_E | 4466985.8828 | 0 | 49.25 | 0 | Direction to zero for Tumut 3 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
S_OSB-AG_ZERO_E | 4110055.684 | 0 | 28.75 | 0 | Direction to zero for Osborne for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
F_S+LREG_0035 | 3915973.1277 | 0 | 160.0833 | 0 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage | FCAS | FCAS
Q>>WOPW_WOSP_WOGP_2 | 3654609.6338 | 217564.9101 | 65 | 28.5 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
Q_WIV1_ZERO_E | 3424066.0208 | 0 | 22.1667 | 0 | Direction to zero for Wivenhoe #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
N_CG3_ZERO_E | 3400976.9179 | 0 | 27.75 | 0 | Direction to zero for Colongra #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
Q_STR_7C2K_MEWF_5 | 3202796.832 | 0 | 55.9167 | 0 | No limit to Mt Emerald Windfarm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
N_TARALGAWF_ZERO | 3110147.3548 | 312585.6938 | 966.5833 | 23.9167 | Taralga WF upper limit of 0 MW | Outage | Unit Zero | NSW
N_CG4_ZERO_E | 3041131.7405 | 0 | 23.3333 | 0 | Direction to zero for Colongra #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N>NIL_PKTX_LV | 2979321.5419 | 2657984.6431 | 613.0833 | 394 | Out= Nil, avoid O/L either Parkes 132kV/66kV Transformer on NIL trip, Feedback. | NIL | Thermal | NSW
N_CG1_ZERO_E | 2969553.2007 | 0 | 26.25 | 0 | Direction to zero for Colongra #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_CG2_ZERO_E | 2852796.7945 | 0 | 21.6667 | 0 | Direction to zero for Colongra #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N>NIL_9R6_9R5 | 2816062.7955 | 0 | 277.5833 | 0 | Out= Nil, avoid O/L Wagga North to Wagga132 (9R6) on trip of Wagga North to Wagga330 (9R5) line, Feedback | NIL | Thermal | NSW
F_S+RREG_0035 | 2758587.3773 | 0 | 159.0833 | 0 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage | FCAS | FCAS
N^^Q_LS_VC_B1, 2, 3, 4, 5, 6 | 2664972.4845 | 2754.5239 | 381.4167 | 9.4167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
S_BARKIPS1_ZERO_E | 2631836.1713 | 0 | 27.25 | 0 | Direction to zero for Barker Inlet for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
N_NIL_TE_B | 2588225.9413 | 9231.6398 | 91.75 | 26.8333 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
S_ISLE_CRK_10 | 2559038.126 | 0 | 282.6667 | 0 | Discretionary upper limit on Cathedral Rocks windfarm<=10 MW when 2-4 syn cons I/S for SA is at risk of islanding or in islanded mode(Note: this equation is swamped when 0-1 sync cons are I/S) | Outage | Discretionary | SA
Q_WIV2_ZERO_E | 2529617.0653 | 0 | 18.75 | 0 | Direction to zero for Wivenhoe #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
F_S+OD_TL_L60 | 2394363.9735 | 0 | 63.1667 | 0 | Lower 60 sec Service Requirement for SA island for loss of Olympic Dam | Outage | FCAS | FCAS
F_MAIN+NIL_MG_R6 | 2277439.1884 | 57056.712 | 1163.0833 | 258.4167 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
V_JLB01_ZERO_E | 2257386.151 | 0 | 20.0833 | 0 | Direction to zero for Jeeralang B1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_BANSF_BBD_60 | 2255269.3344 | 1327289.4762 | 369.1667 | 199.9167 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
V_JLB02_ZERO_E | 2244520.6267 | 0 | 19.9167 | 0 | Direction to zero for Jeeralang B2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_SHWF_FLT_286 | 2201145.5776 | 4590.962 | 102.4167 | 2.6667 | Limit Stockyard Hill wind farm to 286 MW if Heywood flow is above 450 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
SA_TBSE1 | 2160081.0767 | 0 | 168.6667 | 0 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS) Vic-SA Flow = South East Area Load - Local Generation | Outage | Region Separation | SA
V_JLB03_ZERO_E | 2094271.9961 | 0 | 19.0833 | 0 | Direction to zero for Jeeralang B3 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
T_WIND_NTH_100 | 2053986.0266 | 0 | 243 | 0 | 100 MW upper limit on TAS North Wind Generation | Outage | Transient Stability | Tas
F_T_AUFLS2_R6 | 2039751.8852 | 1649224.7148 | 4335.6667 | 4264.9167 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL | FCAS | FCAS
F_S_HPRL_LREG-5MW | 2010071.3646 | 0 | 51.0833 | 0 | Out= NIL, Hornsdale Battery (Load Component) LREG Requirement <= 5MW | Outage | FCAS | FCAS
F_MAIN+RREG_0220 | 1986972.3019 | 51795.8175 | 1131.4167 | 242.75 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_JLA01_ZERO_E | 1963949.2399 | 0 | 18.4167 | 0 | Direction to zero for Jeeralang A1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLA04_ZERO_E | 1933897.6204 | 0 | 18.1667 | 0 | Direction to zero for Jeeralang A4 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_JLA02_ZERO_E | 1926762.6597 | 0 | 18.25 | 0 | Direction to zero for Jeeralang A2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
S^NIL_PL_MAX | 1902712.4965 | 20710.697 | 43.9167 | 1.5833 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
Q_KEP-HYB_25MW | 1832720.2198 | 0 | 621.9167 | 0 | Kennedy Energy Park upper limit of 25MW | Outage | Discretionary | Qld
T>T_X_NTH_STH_B | 1780149.7045 | 0 | 601.9167 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit southern generators to >= southern load - 15 MW | Outage | Thermal | Tas
V>>V_NIL_7 | 1719136.1139 | 568018.3596 | 116.5833 | 81.5 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
N_SNOWYP_ZERO_E | 1711794.2596 | 0 | 15.25 | 0 | Direction to zero for Snowy Pumps for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
N_TARALGAWF_005 | 1676590.5329 | 0 | 359.9167 | 0 | Taralga WF upper limit of 5 MW | Outage | Discretionary | NSW
F_I+RREG_0220 | 1650475.9018 | 1234031.1304 | 6511.8333 | 7689.25 | NEM Raise Regulation Requirement greater than 200 MW | NIL | FCAS | FCAS
NRM_QLD1_NSW1 | 1635408.6589 | 5761967.614 | 26.0833 | 94.5 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
Q_KEP-HYB_20MW | 1621001.7216 | 0 | 260.75 | 0 | Kennedy Energy Park upper limit of 20MW | Outage | Discretionary | Qld
T_CTHLWF_100 | 1619907.7257 | 0 | 168.4167 | 0 | Wild Cattle Hill Wind Farm upper limit of 100 MW | Outage | Discretionary | Tas
S:V_PA_SVC_420 | 1585322.7456 | 141724.0026 | 99.5 | 180.5 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
S>NIL_NWRB2_NWRB1 | 1536619.4835 | 0 | 214 | 0 | Out= NIL, avoid O/L North West Bend-Roberstown #1 132kV line on trip of North West Bend-Robertstown #2 132kV line (this trips MWP1-3 SFs), Feedback | NIL | Thermal | SA
N_SHGEN_ZERO_E | 1526785.7921 | 0 | 12.6667 | 0 | Direction to zero for Shoalhaven for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
V^^V_MLNK_KGTS | 1524031.7314 | 2955395.9265 | 128.0833 | 221.9167 | Out= Murraylink, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | Outage | Voltage Stability | Vic
Q_YARANSF1_RB | 1503723.7998 | 28774.3849 | 196.9167 | 30.25 | Yarrranlea Run Back limit | NIL | Discretionary | Qld
V_MORTLK12_ZERO_E | 1481974.2936 | 0 | 15.3333 | 0 | Direction to zero for Mortlake #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
S>>BWMP_TWPA_TPRS | 1471044.5518 | 18533.9896 | 79.1667 | 2.8333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S_DRYCGT3_ZERO_E | 1444842.151 | 0 | 12 | 0 | Direction to zero for Dry Creek #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
SVML^NIL_MH-CAP_ON | 1404487.602 | 213298.4733 | 447.0833 | 283.25 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL | Voltage Stability | SA
S_DRYCGT1_ZERO_E | 1400270.701 | 0 | 11.75 | 0 | Direction to zero for Dry Creek #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
V>>V_NIL_9 | 1390363.8586 | 569730.4007 | 127.1667 | 75.75 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
F_S_HPRG_RREG-5MW | 1362902.1202 | 0 | 41.5 | 0 | Out= NIL, Hornsdale Battery (Generation Component) RREG Requirement <= 5MW | Outage | FCAS | FCAS
V_LNGS1_ZERO_E | 1352010.8946 | 0 | 11.75 | 0 | Direction to zero for Laverton North #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_LNGS2_ZERO_E | 1349415.2591 | 0 | 11.6667 | 0 | Direction to zero for Laverton North #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_MORTLK11_ZERO_E | 1340862.8139 | 0 | 12.6667 | 0 | Direction to zero for Mortlake #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V>V_NIL_17 | 1316077.8431 | 1848399.7813 | 212.9167 | 283.8333 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
S_QPS3_ZERO_E | 1277381.7592 | 0 | 9.25 | 0 | Direction to zero for Quarantine #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_QPS1_ZERO_E | 1262281.759 | 0 | 9.1667 | 0 | Direction to zero for Quarantine #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
T_GRANVH_100 | 1227531.5303 | 0 | 100.75 | 0 | Discretionary 100 MW upper limit on Granville Harbour Wind Farm | Outage | Discretionary | Tas
N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 1205783.4109 | 0 | 157.1667 | 0 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_7C2K_MEWF_3 | 1179083.3953 | 0 | 83.6667 | 0 | No limit to Mt Emerald Windfarm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_TASCAP_RREG_0220 | 1153572.1656 | 100587.2358 | 1122.6667 | 954.75 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
F_S+OD_TL_L5 | 1126832.8348 | 0 | 58 | 0 | Lower 5 min Service Requirement for SA island for loss of Olympic Dam | Outage | FCAS | FCAS
S_ISLE_CANUNDA_35 | 1106894.8706 | 0 | 81.6667 | 0 | Discretionary upper limit on Canunda windfarm<=35MW & No. in-service wind turbines for canunda at 23 Turbines.(Note otherwise,Canunda will be constrained to 0 MW) | Outage | Discretionary | SA
NRM_NSW1_VIC1 | 1090771.9197 | 107581.3591 | 78.4167 | 23.75 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
SA_ISLE_HPR_HIGH_SOC | 1080354.5863 | 0 | 9.4167 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is above 70% | Outage | Other | SA
Q>NIL_757_758_ECS | 1070285.7186 | 0 | 40.8333 | 0 | Out= Nil, ECS for managing Mudgeeraba to Terranora (757 or 758) 110kV lines, Summer and Winter ECS ratings selected by SCADA status | NIL | Thermal | Qld
V::N_X_SMSC_xxx | 1046896.5737 | 0 | 190.8333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
S_DRYCGT2_ZERO_E | 1001704.9526 | 0 | 9.0833 | 0 | Direction to zero for Dry Creek #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
F_S+TB4_R60_70M | 1000249.5071 | 0 | 7.5833 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B4 for 70 MW metro gen trip option | Outage | FCAS | FCAS
V>>N_NIL_66_65 | 997995.2853 | 0 | 6.5833 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL | Thermal | Vic
S_QPS4_ZERO_E | 996951.6287 | 0 | 6.9167 | 0 | Direction to zero for Quarantine #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_QPS2_ZERO_E | 996951.6284 | 0 | 6.9167 | 0 | Direction to zero for Quarantine #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
Q_KEP-HYB_ZERO | 996766.4159 | 0 | 234.1667 | 0 | Kennedy Energy Park upper limit of 0MW | Outage | Unit Zero | Qld
Q_BRAEMAR3_ZERO_E | 984906.7608 | 0 | 6.5 | 0 | Direction to zero for Braemar #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
N_BROKENH1_ZERO | 937261.5907 | 1817725.9293 | 90.75 | 136.0833 | Broken Hill Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_BRAEMAR2_ZERO_E | 926925.9452 | 0 | 6.5833 | 0 | Direction to zero for Braemar #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
S_QPS5_ZERO_E | 919563.7849 | 0 | 5.6667 | 0 | Direction to zero for Quarantine #5 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
V_NUMURKAH_ZERO | 907571.6617 | 1082993.5352 | 70.6667 | 88 | Numurkah Solar Farm upper limit of 0 MW | NIL | Unit Zero | Vic
F_S_LBBL1_LREG | 875430.0946 | 0 | 24.8333 | 0 | Out= NIL, Lake Bonney Battery (Load Component) LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S+SA_ISLE_L6_1 | 853873.8111 | 0 | 84.4167 | 0 | Lower 6 sec Service Requirement for SA island | Outage | FCAS | FCAS
F_MAIN+NIL_MG_R60 | 851549.8614 | 36309.7318 | 1068.5 | 247.75 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
S_SNUG1_ZERO_E | 850506.2172 | 0 | 5.3333 | 0 | Direction to zero for Snuggery for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_DVRB_270 | 842314.2141 | 0 | 99 | 0 | Out = DV-BL 275kV line Or MK-RB 275kV line O/S, discretionary upper limit for North Brown Hill WF + Bluff WF + Willogolechie WF + Hallet Hill WF (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
F_T+NIL_MG_RECL_R6 | 835220.5772 | 465507.6487 | 1747.75 | 1607.5833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_S+PPT_R5 | 832353.0397 | 0 | 47.6667 | 0 | Raise 5 min Service Requirement for SA island for loss of Pelican Point | Outage | FCAS | FCAS
N::N_NIL_63 | 807834.8038 | 557120.9356 | 71.75 | 52.25 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
F_I+LREG_0210 | 777786.7088 | 908349.202 | 6698 | 7901 | NEM Lower Regulation Requirement greater than 210 MW | NIL | FCAS | FCAS
F_S_LBBG1_RREG | 752917.6854 | 0 | 19.25 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q:N_1078 | 751732.3616 | 2954.6116 | 12.5833 | 3.3333 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
Q_NQ_SEMI_RAMP_ZERO | 740005.2962 | 0 | 41.6667 | 0 | Ramp North Qld semi-scheduled generators to zero and hold at zero | Outage | Unit Zero | Qld
N^^Q_NIL_A | 735152.7246 | 292635.0741 | 177.1667 | 39.25 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | Voltage Stability | NSW
Q>>WOPW_WOSP_WOGP_1 | 728281.9475 | 0 | 8.25 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
S_ISLE_LKB1+2+3_60 | 718580.3644 | 0 | 165.4167 | 0 | Discretionary upper limit on Lake Bonney (1+2+3) windfarms<=60 MW & No. in-service wind turbines for LKB at 41 Turbines.(Note otherwise, LKB 2+3 +1 will be constrained to 0 MW) | Outage | Discretionary | SA
S>>NIL_TWPA_TPRS | 700728.5406 | 58123.4744 | 51.4167 | 7.8333 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
Q_YABULU_ZERO_E | 699551.4041 | 0 | 4.75 | 0 | Direction to zero for Yabulu for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
V::N_X_SMSC_O1 | 686026.482 | 0 | 95.1667 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
N>NIL_94T_947 | 673406.9934 | 2119871.8128 | 89.9167 | 407 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947) line, Feedback | NIL | Thermal | NSW
V^^N_DTKV_1 | 665598.5992 | 0 | 135.9167 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_MURRAWRWF_FLT_90 | 654586.5781 | 2041076.5381 | 72 | 164.75 | Limit Murra Warra Wind Farm 1+2 upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
Q_BRAEMAR7_ZERO_E | 650455.7446 | 0 | 4.5833 | 0 | Direction to zero for Braemar #7 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
N>NIL_9ML | 647527.932 | 197668.7787 | 68.8333 | 26.75 | Out= Nil, avoid O/L Crudine Ridge to Ilford Tee (9ML) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
F_Q++ARTW_L6 | 636365.5551 | 1078462.8081 | 197.1667 | 272.5833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
S>>MKRB_TWPA_TPRS | 630991.3255 | 0 | 49.5 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
Q_BRAEMAR6_ZERO_E | 610706.9616 | 0 | 4.4167 | 0 | Direction to zero for Braemar #6 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q>NIL_EMBW_EMLV_DS | 604255.185 | 128977.9057 | 141.0833 | 11.5833 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
F_T+RREG_0050 | 598060.19 | 115671.0325 | 1169.5 | 251.5833 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T+STH_NYR_ML_L6 | 597971.6485 | 0 | 677.5 | 0 | Lower 6 sec requirement for South Tasmania for loss of Nyrstar load | Outage | FCAS | FCAS
F_Q++ARTW_L60 | 583749.7762 | 1216909.3858 | 194.5 | 267 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
F_T+NIL_MG_R6 | 576088.6998 | 280157.6468 | 1835.6667 | 444.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::N_ESTN_TBSE_xxx | 575102.8965 | 0 | 36 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
N::N_UTRV_2 | 571030.585 | 1115.946 | 235.4167 | 4.25 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
Q_CS_1100 | 570416.9445 | 0 | 70.6667 | 0 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary) | Outage | Discretionary | Qld
F_Q++ARTW_R6 | 564248.7384 | 265089.6367 | 33.5833 | 25.3333 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
T>T_X_NTH_STH_A | 558657.955 | 0 | 154.0833 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit southern generators to <= southern load + 15 MW | Outage | Thermal | Tas
Q_MARYRSF1_RB | 554659.3097 | 32267.1885 | 156.0833 | 26.5833 | Maryrorough Run Back limit | NIL | Discretionary | Qld
N::N_RVYS_2 | 554571.643 | 0 | 56.1667 | 0 | Out = Ravine -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
F_S_LBBG1_LREG | 553900.887 | 0 | 7.1667 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>RBTX_WEWT_RBTX | 547578.0521 | 496420.9904 | 90.6667 | 66.75 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
F_S+PPT_R60 | 544708.3571 | 0 | 46.4167 | 0 | Raise 60 sec Service Requirement for SA island for loss of Pelican Point | Outage | FCAS | FCAS
V_VPGS2_ZERO_E | 543583.3131 | 0 | 6.75 | 0 | Direction to zero for Valley Power GT #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
F_Q++ARTW_R60 | 529306.4465 | 126477.0806 | 37.0833 | 28.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
V::N_X_SMSC_O2 | 526368.1525 | 0 | 96.5 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
T>T_X_LIPM_TWO_F | 518628.0616 | 0 | 77.1667 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L Chapel St to New Norfolk 110kV for loss of Creek Road to New Norfolk 110kV line and Nyrstar load declared credible, Feedback | Outage | Thermal | Tas
V_BULGANAWF_FLT_0 | 515768.6342 | 49357.9125 | 37.6667 | 3.75 | Limit Bulgana Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_KARADSF_FLT_25 | 512506.7375 | 2503761.7239 | 49.5833 | 209.25 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
VTBL_ROC | 511991.7303 | 14278.5298 | 11.5833 | 16.75 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
S>>X_RBTU+RBTX_15 | 508923.2001 | 0 | 61.25 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
S>DVTX_NIL_DVTX | 508467.5122 | 490992.8649 | 44.75 | 40.6667 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | NIL | Thermal | SA
V>>V_NIL_27 | 500358.2834 | 0 | 82.5 | 0 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
Q_MSTUART1_ZERO_E | 499089.6164 | 0 | 3 | 0 | Direction to zero for Mt Stuart #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q>NIL_TV66 | 491394.0796 | 412897.7854 | 10.5833 | 24.4167 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Thermal | Qld
N>N-MOON_945_94K | 477589.1848 | 0 | 40.0833 | 0 | Out= Molong to Orange North (94T) 132kV line, avoid O/L Molong to Wellington (945/1) on trip of Parkes to Wellington (94K) line, Feedback | Outage | Thermal | NSW
N^^Q_TW_330_BUS3_B1 | 474753.0049 | 934251.0969 | 33.25 | 30 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
N>N-NIL_JUTX_LV | 473976.5258 | 0 | 76.1667 | 0 | Out= Nil, avoid O/L Junee#3 132/66kV transformer on trip of Nil, Feedback. 90% of Rating is used as operating margin. | NIL | Thermal | NSW
T_MRWF_100 | 468373.9407 | 0 | 119.25 | 0 | Discretionary 100 MW upper limit on Musselroe Wind Farm | Outage | Discretionary | Tas
T_CTHLWF_ZERO | 468164.4284 | 205093.877 | 40.25 | 16.6667 | Wild Cattle Hill Wind Farm upper limit of 0 MW | Outage | Unit Zero | Tas
V_VS_LB_CAN_50 | 463480.9702 | 108519.5843 | 69.0833 | 128.0833 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. Constraint swamp out when 2-4 syncons I/S | Outage | System Strength | SA
F_T+MINS_LREG | 460711.7598 | 0 | 574.5 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS LREG FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
Q_ROMA_7_ZERO_E | 460436.7657 | 0 | 2.5833 | 0 | Direction to zero for Roma #7 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q_ROMA_8_ZERO_E | 460436.7656 | 0 | 2.5833 | 0 | Direction to zero for Roma #8 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 455853.4176 | 17465.4017 | 8.5833 | 31.5833 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Transient Stability | Qld
S>>X_RBPA+RBTX2_06 | 455105.7321 | 0 | 50.4167 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
N>NIL_MBDU | 454246.7309 | 18476.6807 | 50.1667 | 56.8333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
F_I+NIL_MG_R6 | 453569.1162 | 720714.2397 | 5305.25 | 7559 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
F_S_LBBL1_RREG | 449602.6778 | 0 | 4.5833 | 0 | Out= NIL, Lake Bonney Battery (Load Component) RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V_VPGS3_ZERO_E | 444456.9798 | 0 | 5.25 | 0 | Direction to zero for Valley Power GT #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_VPGS4_ZERO_E | 440731.844 | 0 | 4.75 | 0 | Direction to zero for Valley Power GT #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
V_VPGS6_ZERO_E | 437002.6658 | 0 | 4.5833 | 0 | Direction to zero for Valley Power GT #6 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
F_S_LBBG1_R60 | 428225.7202 | 0 | 16.9167 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++RREG_0220 | 405930.6114 | 207875.3072 | 406.1667 | 964.1667 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
S>>X_RBPA+RBTX2_22 | 405904.2864 | 0 | 38.0833 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo-Templers 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
F_T+NIL_WF_TG_R6 | 400449.6559 | 790984.3783 | 1040.0833 | 1386.6667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_S+TB4_R5_70M | 397797.3395 | 0 | 4.9167 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B4 for 70 MW metro gen trip option | Outage | FCAS | FCAS
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 393657.4617 | 25687.8543 | 21.0833 | 34.25 | Out= Nil, avoid overloading Mudgeeraba to Terranora (757) 110kV line, swamped out when ECS is in service | NIL | Thermal | Qld
N_WRWSF_055 | 392056.079 | 59326.3046 | 27 | 43.3333 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | System Strength | NSW
Q_STR_KBWF_N-2 | 385586.331 | 0 | 29.6667 | 0 | Out = Nil, Loss of 858 and 857 declared credible. Limit Kaban WF to 1% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7, Kar>= 2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S-DLBAT-L_0 | 382623.4145 | 0 | 5 | 0 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW | Outage | Unit Zero | SA
V_BANNERTSF_FLT_45 | 381248.3978 | 1196811.2802 | 30.75 | 97.9167 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_T+NIL_ML_L6 | 376912.6562 | 385971.7815 | 4559.6667 | 2616.3333 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
SA_ISLE_HPR_LOW_SOC | 376527.2354 | 0 | 11.75 | 0 | Out = SA / ESTN separation between Moorabool and Mortlake/Haunted Gully, upper limit on Hornsdale battery of 2 MW, except when state of charge is below 30% | Outage | Other | SA
T_WIND_100 | 372104.1207 | 0 | 84.0833 | 0 | Limit output of TAS wind generation to less than 100 MW. Note, due to 144 MW rating of Non-Scheduled Woolnorth Wind Farm, directions may be required to reduce Woolnorth MW output if this constraint violates | Outage | Transient Stability | Tas
F_T+LREG_0050 | 368465.2597 | 71334.4247 | 1204.5833 | 258.9167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::N_DDSM_xxx | 364981.265 | 58992.3862 | 312.75 | 131.4167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
SVML_ZERO | 364456.9757 | 77164.7913 | 121.9167 | 131 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
VS_050_DYN | 364028.3878 | 48983.5235 | 27.5 | 12.25 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
S>>X_RBTU+RBTX_14 | 360285.1559 | 0 | 32.75 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
V>>N_NIL_65_66 | 360188.253 | 338671.9914 | 133.1667 | 103.3333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
F_S++HYSE_L60 | 354213.8866 | 143882.4195 | 230.1667 | 122.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage | FCAS | FCAS
N>N_968_969_NIL | 352820.9987 | 0 | 27.5 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
T::T_NIL_1 | 348623.3174 | 474322.7926 | 280.75 | 1427.4167 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
S-DLBAT-G_0 | 346890.8265 | 0 | 2.5833 | 0 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW | Outage | Unit Zero | SA
N_BANGOWF1_ZERO | 345809.3443 | 0 | 26.0833 | 0 | Bango 973 wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
S_TORRB4_ZERO_E | 343108.2836 | 0 | 4 | 0 | Direction to zero for Torrens Island B #4 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S_DV-RB2_070 | 342123.6519 | 0 | 10.5833 | 0 | Discretionary upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 70 MW | Outage | Discretionary | SA
S>>X_RBTU+RBTX_10 | 338640.7343 | 0 | 20.6667 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Templers- Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N>N-WLTX_A | 338389.6639 | 0 | 37.0833 | 0 | Out= one of the Wellington 123/330kV Transformers, avoid O/L on Molong to Orange North (94T) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
V_VPGS5_ZERO_E | 338009.3843 | 0 | 4.1667 | 0 | Direction to zero for Valley Power GT #5 for Dispatch and Predispatch and NOT PASA | Outage | Other | Vic
F_T+MINS_RREG | 336415.2878 | 0 | 404.8333 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS RREG FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
V^^N_DDSM_1 | 335262.6486 | 0 | 52.8333 | 0 | Out = Dederang to South Morang 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_KIAMSF_FLT_50 | 329150.7822 | 2580762.7758 | 27.25 | 211.9167 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_X_MBTE_3A & N_X_MBTE_3B | 327353.8674 | 83314.6976 | 310.5833 | 319.9167 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
V::S_HYSE_MAXG_2 | 310000 | 0 | 1.6667 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | Transient Stability | SA
V_GANWRSF_FLT_30 | 307964.0673 | 966486.6059 | 28.3333 | 80.25 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_7C2K_HASF_4 | 306808.8374 | 0 | 10.4167 | 0 | No limit to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N::N_LTYS_2 | 302253.8726 | 73041.5791 | 98.8333 | 41 | Out = Lower Tumut-Yass (03), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
S>>PATW_BWPA_TPRS | 296943.129 | 40830.4686 | 13.5 | 5.4167 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_S++HYSE_L6_1 | 296686.8448 | 12245.3283 | 189.6667 | 31.5833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS | FCAS
F_T+NIL_ML_L60 | 291850.7129 | 138745.3081 | 4275 | 2558.1667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_MAIN+GFT_TG_R60 | 289459.4202 | 2748.7984 | 112.4167 | 8.5833 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V>>V_NIL_25 | 288421.5731 | 0 | 133.5 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
S>>X_RBPA+RBTX2_16 | 283936.7156 | 0 | 27.9167 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
S>>CNRB_TWPA_TPRS | 280978.073 | 0 | 26 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
V>>V_NIL_24 | 280706.4896 | 68813.7038 | 24.8333 | 6.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
V_MACWF_FLT_0 | 275767.7525 | 939999.678 | 24.1667 | 72.1667 | Limit Macarthur Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
T^V_NIL_8 | 271549.5851 | 1598.9351 | 9 | 5.0833 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
N_STWF1_ZERO | 269416.4575 | 316250.7432 | 21 | 25.1667 | Silverton wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_YATPSF_FLT_25 | 269303.2174 | 2014657.9587 | 43 | 217 | Limit Yatpool solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>N-DP_TIETX_D | 265305.7389 | 0 | 39.6667 | 0 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (220 KV to 330 kV) on Kerang-Bendigo trip; Feedback | Outage | Thermal | NSW
VSML_ROC_80 | 264648.5611 | 126190.4882 | 71.5 | 84.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
S_SNAPPER1_ZERO_E | 263128.365 | 0 | 3.75 | 0 | Direction to zero for Snapper Point for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
F_T+MAXS_R6 | 263051.5164 | 0 | 555.8333 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS R6 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
V>>V_DDSM_1 | 261004.5461 | 168226.0013 | 136.8333 | 91.4167 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Thermal | Vic
F_T+NIL_MG_R60 | 253629.5374 | 50352.4631 | 1856.5833 | 522.0833 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
NSA_Q_GSTONE34_xxx | 251406.1617 | 1055282.2777 | 98.4167 | 18.9167 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
S>>CNRB_BWPA_RHBR-T | 250822.5765 | 0 | 25.4167 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_MAIN++NIL_MG_R6 | 248125.8164 | 488377.2922 | 1478.9167 | 2389.6667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
V>V_X_HWRO12_3 | 246691.4414 | 0 | 40.0833 | 0 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, avoid O/L Yallourn to Rowville No. 5 220 kV line on trip of Yallourn to Rowville No. 6,7 or 8 220 kV lines, feedback, YWG1 on 220 kV, Radial mode | Outage | Thermal | Vic
Q_STR_7C2K_HAYSF_7 | 244951.3737 | 0 | 20.1667 | 0 | Limit to Hayman Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V::S_NIL_MAXG_xxx | 243635.7525 | 66097.5122 | 57.1667 | 18.3333 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
N>N-MOON_947_72 | 243603.6075 | 0 | 19.1667 | 0 | Out= Molong to Orange North (94T) 132kV line, avoid O/L Wellington to Orange North (947) 132kV line on trip of Wellington to Mt Piper (72) 330kV line, Feedback | Outage | Thermal | NSW
F_T+STH_NYR_ML_L60 | 241313.4695 | 0 | 773.0833 | 0 | Lower 60 sec requirement for South Tasmania for loss of Nyrstart load | Outage | FCAS | FCAS
F_S+SA_ISLE_LB_L6_1 | 240816.9866 | 0 | 60.9167 | 0 | Lower 6 sec Service Requirement for SA island | Outage | FCAS | FCAS
NSA_Q_BARCALDN | 240726.0924 | 254881.7366 | 21.8333 | 20.3333 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
F_MAIN++APD_TL_L60 | 237626.398 | 39272.5744 | 1584 | 1401.0833 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
S>>PARB_RBTU_WEWT | 236242.3323 | 125974.1424 | 31.5 | 56.25 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
SVML_FLT_130 | 234854.6082 | 4275.188 | 26.1667 | 19.1667 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
T>T_X_LIPM_WACB_B | 233592.7252 | 0 | 106.5 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, with associated 220kV CB at WA O/S, limit southern generators to >= southern load - 15 MW | Outage | Thermal | Tas
Q_KWF1_ZERO | 232881.5781 | 0 | 14.9167 | 0 | Kaban Wind Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N_WRWSF_ZERO | 231363.6753 | 358.455 | 12.5 | 1.0833 | White Rock wind farm and White Rock solar farm upper limit of zero MW | Outage | Discretionary | NSW
Q_STR_7C2K_RUGSF_7 | 224759.1211 | 0 | 17.8333 | 0 | Limit to Rugby Run Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
NRM_SA1_VIC1 | 223970.3135 | 0 | 11 | 0 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue | Negative Residue
SV_420_DYN | 220181.6105 | 327039.929 | 160.5833 | 330.8333 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
F_S_LBBG1_R5 | 218922.6993 | 0 | 16.25 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 218068.4689 | 798340.2205 | 250.25 | 411.6667 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | Voltage Stability | NSW
S>>CNRB_BWPA_HUWT | 217688.1862 | 2559.1469 | 29.25 | 0.41667 | Out= Canowie-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
Q_STR_7C2K_KBWF_4 | 215163.6764 | 0 | 15.5 | 0 | Limit Kaban Solar Farm to 60% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG) with Haughton syncon ON, (1% if Haughton syncon OFF) Zero otherwise. | Outage | System Strength | Qld
Q>>BCST_BCST_CLWU | 210832.8625 | 238801.3915 | 140.25 | 89.3333 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line, avoid O/L the remaining Stanwell to Bouldercombe 848 or 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
F_S+ML_L5 | 207949.6695 | 0 | 49 | 0 | Lower 5 min Service Requirement for SA island for loss of Murraylink | Outage | FCAS | FCAS
Q_STR_7C2K_DAYSF_7 | 204316.4096 | 0 | 16.3333 | 0 | Limit to Daydream Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N_WRWSF_125 | 204158.2089 | 0 | 13.4167 | 0 | White Rock wind farm and White Rock solar farm upper limit of 125 MW | Outage | System Strength | NSW
T>T_NIL_BL_IMP_6EE | 204153.7047 | 6954.1281 | 6.25 | 0.33333 | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
S:VS_PA_SVC_570 | 200622.1463 | 11362.3785 | 4.5 | 12.3333 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | Oscillatory Stability | SA
F_MAIN+LREG_0210 | 199359.4328 | 49428.7344 | 1090.0833 | 234.4167 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N>>N-MPWW_ONE_8 | 197897.6091 | 1105397.0428 | 8.9167 | 53.9167 | Out= Mt. Piper to Wallerawang(70 or 71), avoid O/L Molong to Orange North (94T) on trip of the remaining Mt Piper to Wallerawang (71 or 70) , Feedback | Outage | Thermal | NSW
Q-X_STR_7C8C_MEWF | 195384.1704 | 0 | 14.4167 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Mt Emerald windfarm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
N_CRWF1_ZERO | 194715.4452 | 4129.7099 | 37 | 0.33333 | Crudine Ridge wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V^^SML_NSWRB_2 | 194297.2169 | 503101.1041 | 81.75 | 59.3333 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
S>>X_RBTU+RBTX_13 | 189750.9758 | 0 | 25 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
F_T+NTH_MG_R6 | 188625.2431 | 0 | 7.25 | 0 | Raise 6 sec requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T_MRWF_GCS | 188324.3442 | 2809.8406 | 113.8333 | 4.1667 | Musselroe wind farm Generator Control Scheme (GCS) constraint to maintain TAS FOS for a Tasmania generator event. Limit Musselroe wind farm based on load available/armed by Musselroe GCS | NIL | Other | Tas
N_FINLEYSF_49_INV | 186498.2644 | 0 | 1.3333 | 0 | Limit Finley Solar Farm upper limit to 0 MW if number of inverter available exceed 49. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
S_WATERLWF_RB | 185661.6408 | 8985.5333 | 16.9167 | 1 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
Q_STR_7C2K_COLSF_7 | 185588.2153 | 0 | 15.0833 | 0 | Limit to Collinsville Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N_SUNRSF1_ZERO | 184413.8491 | 1084503.1338 | 22.25 | 81.75 | Sunraysia 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_STR_7C2K_HAMSF_7 | 183540.6707 | 0 | 15.0833 | 0 | Limit to Hamilton Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
T::T_NIL_3 | 183237.7548 | 3516.1605 | 120.75 | 16.25 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
S>MKRB_BWMP_HUWT | 182158.6319 | 0 | 18.25 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S_ISLE_CANUNDA_10 | 181138.4966 | 0 | 12.0833 | 0 | Discretionary upper limit on Canunda windfarm<=10 MW & No. in-service wind turbines for canunda at 5 Turbines.(Note otherwise,Canunda will be constrained to 0 MW) | Outage | Discretionary | SA
TVBL_ROC | 181035.4268 | 40516.2664 | 6.3333 | 22.8333 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
S>>CNRB+BRTW_03 | 180765.1367 | 0 | 23.25 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Blyth West-Munno Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
N>>NIL_7_1 | 177647.6326 | 6162.5197 | 1.25 | 0.25 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Stockdill (1) line, Feedback | NIL | Thermal | NSW
S>>CNRB_BWPA_WTTP | 177470.1687 | 0 | 20.1667 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V_WEMENSF_FLT_45 | 177370.8955 | 261726.2431 | 19.5833 | 26.8333 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
T_V_NIL_BL1 | 176759.3858 | 2017.5908 | 13 | 6.9167 | Out=Nil, Basslink no go zone limits Tas to Vic. Limit Basslink upper limit to 125 MW on 1st DI out of no go zone. i.e. BL <= 125 MW | NIL | Other | Tas
S>>NIL_RBTU_WTTP | 174159.7171 | 1924.7128 | 31.75 | 0.5 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | NIL | Thermal | SA
F_T+STH_MG_R6 | 173125.1957 | 0 | 9 | 0 | Raise 6 sec requirement for a South Tasmania Generation Event | Outage | FCAS | FCAS
F_T+MINS_R5 | 171778.401 | 0 | 214.75 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS R5 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
Q_MARYRSF1_10 | 170670.737 | 5161.2396 | 28.4167 | 4.6667 | Maryrorough Solar Farm upper limit of 10 MW | Outage | Discretionary | Qld
Q_HASMME_RAMP_ZERO | 169627.4075 | 0 | 12.5 | 0 | Ramp Haughton, Sun Metals, Kaban and Mt Emerald generators to zero and hold at zero. | Outage | Unit Zero | Qld
N>N-WLWO_C | 165560.4381 | 0 | 2.3333 | 0 | Out = Wellington to Wollar line (79), avoid O/L on Cowra to Forbes North (998) on trip of Mt_Piper to Wellington line (72), Feedback | Outage | Thermal | NSW
F_S+ML_R60 | 164643.6627 | 0 | 37.4167 | 0 | Raise 60 sec Service Requirement for SA island for loss of Murraylink | Outage | FCAS | FCAS
F_I+NIL_MG_R60 | 162913.6919 | 439024.9746 | 4579.4167 | 7075.4167 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
F_T+NIL_MG_RECL_R60 | 161553.9295 | 116228.0696 | 1934.25 | 1585.0833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_OWF_TGTSNRBHTN_30 | 161232.8951 | 80172.2907 | 11.3333 | 9.75 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
S:V_PA_SVC_470 | 161189.5833 | 0 | 218.4167 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 470 MW | Outage | Oscillatory Stability | SA
Q_STR_7C2K_SMSF_7 | 158895.056 | 0 | 12.9167 | 0 | Limit to Sun Metals Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
T_GO3_100 | 154919.1567 | 0 | 22.5 | 0 | Discretionary 100 MW upper limit on Gordon unit 3. DS only. | Outage | Discretionary | Tas
F_QNV+DYN_RREG | 154010.5837 | 0 | 113.5833 | 0 | Qld, NSW and Vic Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | Outage | FCAS | FCAS
F_S_LG1_R5 | 153131.6937 | 0 | 1.0833 | 0 | Out= NIL, Ladbroke Grove Unit1 R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LG2_R5 | 153131.6936 | 0 | 1.0833 | 0 | Out= NIL, Ladbroke Grove Unit2 R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S^CNRB+BRTW_SA_NORTH | 152266.2726 | 0 | 12.5 | 0 | Out = Canowie-Robertstown 275kV line+Brinkworth-Templers West + RB SVC, Manage voltage collapse in northern SA for the trip of one 275kV line between Davenport-Para or Davenport-Tungkillo. | Outage | Voltage Stability | SA
V::S_2SE+PAVC_MAXG | 151853.6692 | 2.9578 | 22.1667 | 0.16667 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
F_S+TORRB4_R5 | 151330.2475 | 0 | 8.4167 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B4 | Outage | FCAS | FCAS
Q>>BCRG_CLWU_BCCP | 149239.8659 | 0 | 35 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q_STR_7C2K_MEWF_80 | 148514.3366 | 0 | 9.8333 | 0 | Limit to Mt Emerald Wind Farm to 80% if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,Kar=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
V:S_600_HY_TEST | 147813.2456 | 60228.3116 | 65.6667 | 49.0833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
S>>CNRB+BRTW_02 | 147475.0032 | 0 | 33 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Claire North 132 to Brinkworth 132 kV line on trip of Mokota-Robertstown 275kV line(this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S^NIL_CRK_VCS_STATUS | 147003.3528 | 0 | 34.8333 | 0 | Out= Nil, upper limit for Cathedral Rocks WF based on Mt Millar Voltage Control System (VCS) availability, (Note: CRK <=55 MW when VCS OFF; CRK<= 60 MW when VCS ON) | NIL | Voltage Stability | SA
F_S+SA_ISLE_R6_1 | 146530.156 | 0 | 85 | 0 | Raise 6 sec Service Requirement for SA island | Outage | FCAS | FCAS
F_S+TB2_R60_70M | 145867.9154 | 0 | 4.8333 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B2 for 70 MW metro gen trip option | Outage | FCAS | FCAS
N>>N-NIL_94K_3 | 145818.7306 | 0 | 16.4167 | 0 | Out= Nil, avoid O/L on Suntop Solar Farm to Wellington Suntop Tee 94K/3 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
V_BANSF_BBD_80 | 144591.5551 | 469301.5123 | 28.9167 | 86.0833 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
SVML_ROC_80 | 144001.7942 | 119792.831 | 76.8333 | 101.25 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
S>>PARB_RBTU_WTTP | 139135.795 | 84978.3439 | 19.6667 | 31.5 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_TASCAP_LREG_0210 | 138476.309 | 131289.5614 | 1087.4167 | 1482.6667 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
S>>RBTX_TWPA_TPRS | 137305.2457 | 0 | 23.0833 | 0 | Out= one Robertstown 275/132kV transforme, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
N>>N-PKWL_94K_2 | 136283.6318 | 477675.3362 | 9 | 79.4167 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
Q>NIL_MRTA_A | 134580.0788 | 9130.58 | 1.3333 | 0.083333 | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
N_WRWF1_ZERO | 132898.7346 | 0 | 10.1667 | 0 | White Rock WF upper limit of 0 MW and all turbines disconnected | Outage | Unit Zero | NSW
S_POR03_ZERO_E | 131768.419 | 0 | 0.75 | 0 | Direction to zero for Port Lincoln #3 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
SV_470_DYN | 130411.3074 | 0 | 132.3333 | 0 | SA to Victoria on Heywood upper transfer limit of 470 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
V:S_600_HY_TEST_DYN | 128697.9323 | 117434.9887 | 56.75 | 40.3333 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
Q>>PWSP_WOSP_PWSP | 128233.7208 | 0 | 13.9167 | 0 | Out= Palmwoods to South Pine (808) line, avoid O/L on parallel 110kV lines between Palmwoods and South Pine(745 /746) on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
N>>N-NIL_998 | 128139.8892 | 45829.4562 | 3.9167 | 2.5833 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
S>>NIL_RBTU_WEWT | 125765.8699 | 32570.2379 | 19.6667 | 5.8333 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
F_S+ML_R5 | 125060.8008 | 0 | 35.5 | 0 | Raise 5 min Service Requirement for SA island for loss of Murraylink | Outage | FCAS | FCAS
V^^N_LTYS_1 | 124087.1652 | 165918.9717 | 41.8333 | 98 | Out = Lower Tumut - Yass (3) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
NRM_VIC1_NSW1 | 123629.6966 | 13996.0903 | 2.3333 | 0.75 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
Q_MSTUART2_ZERO_E | 122303.0142 | 0 | 1.1667 | 0 | Direction to zero for Mt Stuart #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | Qld
V::S_NIL_SETB_SECP_1 | 119514.3022 | 93.9727 | 5.1667 | 0.33333 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | Transient Stability | SA
N>NIL_COTX_LV | 118954.3204 | 163465.6443 | 19.6667 | 14.8333 | Out= Nil, avoid O/L either Corowa 22kV/132kV Transformer on NIL trip, Feedback. NOTE: System normal is only one transformer in service. 90% of Rating and no operating margin is used as per Essential Energy advice. | NIL | Thermal | NSW
V_MC_SH_WF_600 | 118394.8484 | 0 | 13 | 0 | Limit the total MW from Macarthur and Stockyard Hill WF <= 600 MW to maintain generation contingency size in Victoria. | Outage | Discretionary | Vic
N_DARLSF_FLT_100 | 118283.2168 | 86732.719 | 8.4167 | 7.0833 | Limit Darlington Pt Solar Farm upper limit to 100 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>V_NIL_5 | 118175.4145 | 727.6405 | 20.0833 | 1 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Thermal | Vic
S>>X_RBPA+RBTX2_23 | 116909.481 | 0 | 17.5 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
N>>LDNC_964_82 | 116001.8752 | 0 | 75.1667 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, Swamps if 964 O/S, Feedback | Outage | Thermal | NSW
S::V_TBSE_TBSE | 115296.3754 | 0 | 81.4167 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
Q_EMERASF1_ZERO | 115033.3944 | 56855.6064 | 10.75 | 4.4167 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_T_NIL_FCSPS | 114616.0091 | 88382.5482 | 207.25 | 238.0833 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
N>>N-NIL-YS-TX | 110403.8786 | 0 | 7.8333 | 0 | Out= Nil, avoid O/L Either of Yass 132/330 Transformers on trip of Nil, Feedback | NIL | Thermal | NSW
T_MRWF_QLIM_xx | 107573.4367 | 55685.5424 | 10.3333 | 17 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
N>N-9GL-999_94U | 106784.9885 | 0 | 7.8333 | 0 | Out= Bango973 WF to Yass 132kV line(9GL), avoid O/L Cowra to Bango999 (999) on trip of line 94U, Feedback | Outage | Thermal | NSW
V_BANNERTON_ZERO | 106474.9637 | 96153.1654 | 9.0833 | 8 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V^^N_UTRV_1 | 106349.9816 | 1811.2466 | 21.5833 | 1.4167 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_8C7C2K_LVSF_2 | 106097.2891 | 0 | 8.5 | 0 | No limit to Lilyvale SF to if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8 ,NQLD>450&470(AVG),Ross_FN>250&270(AVG),or if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
V::N_SETB_xxx | 105365.6353 | 0 | 36.5833 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
NRM_NSW1_QLD1 | 104730.2175 | 28244.327 | 2.4167 | 0.25 | Negative Residue Management constraint for NSW to QLD flow. | NIL | Negative Residue | Negative Residue
V_MURRAWRWF_FLT_80 | 102706.1809 | 938488.0161 | 8.75 | 76.9167 | Limit Murra Warra Wind Farm 1+2 upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
S>HUWT_BWPA_RHBR-T | 102557.9585 | 0 | 9.25 | 0 | Out= Hummocks-Waterloo 132kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_S_LBBL1_L6 | 102270.7308 | 0 | 15.5 | 0 | Out= NIL, Lake Bonney Battery (Load Component) L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LBBL1_L60 | 102218.2148 | 0 | 15.75 | 0 | Out= NIL, Lake Bonney Battery (Load Component) L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V::S_SETB_TBSE_2 | 101796.5885 | 22532.606 | 46.9167 | 30.8333 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Transient Stability | SA
F_MAIN++NIL_MG_R60 | 101748.3718 | 234736.8562 | 1690.8333 | 2393.8333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_T+NIL_WF_TG_R60 | 101392.6066 | 116502.9461 | 1141.3333 | 1420.6667 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T++RREG_0050 | 100628.4774 | 68902.8145 | 524.4167 | 473.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
NQTE_ROC | 100134.1168 | 22979.3103 | 32.25 | 63.3333 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
F_S_LG1_R60 | 98941.6178 | 0 | 1.5833 | 0 | Out= NIL, Ladbroke Grove Unit1 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LG2_R60 | 98928.2478 | 0 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S_POR01_ZERO_E | 98204.9173 | 0 | 0.58333 | 0 | Direction to zero for Port Lincoln #1 and #2 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
T_NTH_ROCOF_1 | 97635.1363 | 0 | 149 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit non-synchronous generation and Basslink import to limit instantaneous Rate of Change of Frequency to < 3 Hz/sec in Nth TAS | Outage | ROC Frequency | Tas
F_S_LBBG1_R6 | 96868.626 | 0 | 14.9167 | 0 | Out= NIL, Lake Bonney Battery (Generation Component) R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LG1_R6 | 96839.276 | 0 | 2.5833 | 0 | Out= NIL, Ladbroke Grove Unit1 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S_LG2_R6 | 96830.276 | 0 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q_HAMISF1_ZERO | 95822.8007 | 1033.1051 | 5.4167 | 0.083333 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_YARANSF1_37 | 93973.2045 | 3174.5938 | 15.9167 | 2.8333 | Yarranlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
V^^N_DTMN_1 | 93932.4651 | 7547.3824 | 51.8333 | 5.25 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_ARARATWF_FLT_0 | 93755.3699 | 1112493.8165 | 7.5833 | 89.0833 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
CA_SYDS_5283EFAB_1 | 93535.8568 | 0 | 1.1667 | 0 | Constraint Automation, O/L NN_CS:LNNF:I:110@CHAPEL@TAS for CTG MTD9 on trip of N_NRFOLK - CREEK RD + NYRSTAR LD. Generated by STNET[BNECR2] Host NORREGEEMP4(EMPSYD) | Outage | Thermal | Constraint Automation
S>RBTX1_RBTX2_WEMWP4 | 93179.7705 | 630.2988 | 76.1667 | 3.8333 | Out= Robertstown 275/132kV TX1, avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, | Outage | Thermal | SA
N_FINLYSF_FLT_50 | 91831.2836 | 132751.4183 | 10.0833 | 10.6667 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_MBTE1_B | 91480.1905 | 87146.7771 | 102.1667 | 175.75 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
N_DARLSF_FLT_85 | 91329.6233 | 231716.3793 | 7.5833 | 17.8333 | Limit Darlington Pt Solar Farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>N_9U2_969_NIL | 91065.5843 | 0 | 7.5 | 0 | Out= 9U2 (Moree to Inverell ) 132kV line, avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
F_T+NTH_ML_L6 | 90867.1222 | 0 | 7.75 | 0 | Lower 6 sec requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S_LADBROK1_ZERO_E | 90600 | 0 | 0.5 | 0 | Direction to zero for Ladbroke Grove #1 for Dispatch and Predispatch and NOT PASA | Outage | Other | SA
S>NIL_BWMP_HUWT | 90322.4253 | 98565.5915 | 10.1667 | 8 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
V>V_NIL_8 | 89982.9905 | 86530.8674 | 13.3333 | 21.9167 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
F_MAIN+NIL_DYN_LREG | 89450.2952 | 133127.8034 | 259.4167 | 543.6667 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL | FCAS | FCAS
F_S+SNS_TG_R60 | 89228.562 | 0 | 66.9167 | 0 | Raise 60 sec Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line | Outage | FCAS | FCAS
Q_STR_7C8C_HASF | 89078.9341 | 338379.3162 | 7 | 30.8333 | Limit Haughton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>NIL_LSDU | 88439.2571 | 319145.9158 | 172.25 | 270 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
Q_STR_7C2K_HASF_5 | 88382.3 | 0 | 6.1667 | 0 | No limit to Haughton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
T_BLINK_TV_NGZ | 87034.6768 | 3778.5524 | 21.1667 | 4.25 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | NIL | Other | Tas
Q>>NIL_BCCP_RGLC | 86959.9101 | 60216.6863 | 25.8333 | 21.25 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
F_MAIN++LREG_0210 | 85493.0782 | 59384.6477 | 631.1667 | 681.5 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_T_NIL_MINP_R6 | 85033.5986 | 97413.2195 | 665.3333 | 833.25 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL | FCAS | FCAS
N_V_HV1100 | 84942.9969 | 0 | 1.5 | 0 | Discretionary constraint on transfer from NSW to VIC of 1100 MW on DDTS-NSW cutset | Outage | Discretionary | NSW
F_I+NIL_APD_TL_L60 | 84755.1674 | 83950.2271 | 5384.0833 | 6785.75 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
QNTE_ROC | 84458.0289 | 26296.7421 | 31.6667 | 59.5833 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
N_LIMOSF1_FLT_60 | 84298.3186 | 1518639.1521 | 8.0833 | 136.1667 | Limit Limondale 1 solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>NIL_MRTA_B | 83800.4957 | 606.0799 | 0.66667 | 0.16667 | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
Q>>CPWO1_CPWO2_WUGG | 83673.216 | 605446.9507 | 6.6667 | 67.5 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Woolooga (814) on trip of Wurdong to Teebar Creek (819) line, Feedback | Outage | Thermal | Qld
F_T+STH_RREG | 82052.4986 | 0 | 8.5833 | 0 | Raise Regulation requirement for Southern Tasmania | Outage | FCAS | FCAS
F_Q++ARTW_R5 | 81985.4488 | 762.6199 | 21.1667 | 5.5 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
V>V_X_HWRO12_5 | 81169.9214 | 0 | 12.8333 | 0 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, avoid O/L Yallourn to Rowville No. 6,7 or 8 220 kV lines on trip of Yallourn to Rowville No. 6, 7 or 8 220 kV lines, feedback, YWG1 on 220 kV, Radial mode | Outage | Thermal | Vic
N^^N_NIL_1 | 80796.6381 | 0 | 1.6667 | 0 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | Voltage Stability | NSW
F_S+TB2_R5_70M | 80124.5587 | 0 | 4.8333 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B2 for 70 MW metro gen trip option | Outage | FCAS | FCAS
S>>NIL_BWMP_TWPA | 79183.6849 | 74209.9977 | 7.75 | 7.75 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
V^SML_BUDP_3 | 79175.3113 | 19723.1089 | 16.9167 | 88.8333 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
V_KARADSF_FLT_20 | 79086.7383 | 1524714.3902 | 8.0833 | 120.3333 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_V_HYMO_1 | 78496.8213 | 9.368 | 5.6667 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line, Limit voltage unbalance at the APD 500 kV bus and Heywood 275 kV bus | Outage | Voltage Stability | Vic
F_T+MAXS_R60 | 78439.2737 | 0 | 426.25 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS R60 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
T>T_NIL_110_1 | 78319.8019 | 124562.0889 | 49.6667 | 41.8333 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
S_HALWF2_0 | 77808.9332 | 32475.3154 | 5.75 | 2.5833 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
N_FINLYSF_FLT_45 | 77511.6733 | 1238829.3461 | 7.3333 | 100.9167 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_YARANSF1_37MW_N-1 | 76484.1187 | 2171.3502 | 9.9167 | 0.83333 | Limit Yarrenlea Solar Farm to 37 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip, Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
Q_STR_SYN_HASF_ZERO | 75993.9007 | 0 | 6 | 0 | Limit 0MW to Haughton Solar farm if Haughton Syncon is OFF, swamp if Haughton Syncon is ON | Outage | System Strength | Qld
S>HUWT_NIL_STBG-T | 75899.9193 | 0.00434 | 9.5833 | 0.25 | Out= Hummocks-Waterloo 132kV line, avoid O/L Snowtown-Bungama T 132kV line on Nil trip, Feedback | NIL | Thermal | SA
F_S+TORRB4_R60 | 75860.0597 | 0 | 8.0833 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B4 | Outage | FCAS | FCAS
Q_WARWSF1_ZERO | 75525.6017 | 0 | 7.6667 | 0 | Warwick Solar Farm 1 upper limit of 0 MW | Outage | Unit Zero | Qld
N_BROKENHSF_FLT_30 | 75507.2385 | 852430.4192 | 6.6667 | 69.75 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>V_NIL_8_1 | 75108.5556 | 0 | 7.8333 | 0 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF O/S. | NIL | Thermal | Vic
T_JBUTTERS_100 | 74101.4051 | 0 | 49 | 0 | Discretionary 100 MW upper limit on John Butters | Outage | Discretionary | Tas
F_S_LBBL1_L5 | 73297.9823 | 0 | 14.75 | 0 | Out= NIL, Lake Bonney Battery (Load Component) L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V_S_NIL_ROCOF | 72951.7662 | 142367.5442 | 22 | 326.75 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
N>>994_99F_63 | 72757.7196 | 0 | 9.3333 | 0 | Out= Yanco to Wagga (994) 132kV line, avoid O/L Yanco to Uranquinty (99F) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,[Note: assumed X5 trip scheme disarmed, Wagga-Darlington Pt 132kV Solid)] | Outage | Thermal | NSW
V_YATPSF_FLT_20 | 72031.6833 | 1449502.8358 | 7.5833 | 115.4167 | Limit Yatpool solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_S+RREG_0070 | 71514.4892 | 0 | 2.25 | 0 | SA Raise Regulation Requirement greater than 70 MW | Other | FCAS | FCAS
Q_STR_7C8C_KIDSF | 69989.759 | 311935.4182 | 5.5833 | 26.0833 | Limit Kidston SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_OKYTX4 | 69775.6794 | 0 | 5.75 | 0 | Out = Oakey 4T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 71MW | Outage | Thermal | Qld
N>NIL_94B | 69481.6044 | 29280.214 | 9.0833 | 5.4167 | Out= Nil, avoid O/L Beryl to Wellington 132 kV (94B/1) on nil trip, Feedback. Metering at Wellington is used | NIL | Thermal | NSW
Q_STR_7C0K_HASF | 68914.348 | 0 | 5.0833 | 0 | No limit to Haughton Solar Farm if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
N>N-X_MOON_WLTX_B | 68789.2184 | 0 | 5.25 | 0 | Out= 94T (Molong to Orange North) 132kV line and one of the Wellington 132/330kV Transformer, avoid O/L to Wellington to Orange North (947) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
N_SUNRSF_FLT_60 | 68516.1838 | 1114808.5528 | 7.1667 | 101.8333 | Limit Sunraysia solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>>CLWU_BCCP_BCRG | 68064.2553 | 0 | 14 | 0 | Out = Calvale to Wurdong (871), avoid O/L Bouldercombe to Raglan (811) or Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
V>>V_NIL_26A | 67531.1654 | 0 | 0.91667 | 0 | Out = Kiamal 220kV CB (one or more MR2B or 7422A or 7422B), avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. DS only | NIL | Thermal | Vic
S>>BWMP_DVBR_RHBG-T | 65867.855 | 0 | 15.75 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | Thermal | SA
N>>NIL_86_8U_S | 65429.0894 | 4839.9619 | 73.1667 | 11.75 | Out= Nil, avoid O/L Armidale to Tamworth (8U or 86) on trip of the other Armidale to Tamworth line (86 or 8U), Feedback | NIL | Thermal | NSW
V_GANWR_BAT_L_ISL_0 | 65101.9556 | 867.1788 | 3.4167 | 4.4167 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_KIATAWF_FLT_15 | 64553.1044 | 230847.9186 | 8.5833 | 74.9167 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_KEP-HYB_30MW | 64334.3905 | 0 | 32 | 0 | Kennedy Energy Park upper limit of 30MW | Outage | Discretionary | Qld
N^^V_CNCW_1 | 63771.4778 | 66961.8583 | 40.6667 | 113.5833 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q^^NIL_CS | 63702.8537 | 0 | 8.6667 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL | Voltage Stability | Qld
S_PPT+SNPT_270 | 63625.4405 | 0 | 3.8333 | 0 | SA Pelican Point + Snapper Point generation <= 270 MW | Outage | Discretionary | SA
V::S_HYSE_MAXG | 63251.4406 | 0 | 0.83333 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | Transient Stability | SA
N_COLEASF1_FLT_45 | 63246.6853 | 1705895.3362 | 5.3333 | 136.9167 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_ESTN+MG_R6 | 62911.62 | 0 | 106.5 | 0 | Raise 6 sec Service Requirement for Eastern Generation Event | Outage | FCAS | FCAS
NQ_600_DYN_TEST | 62636.005 | 0 | 38.5833 | 0 | NSW to QLD on QNI upper transfer limit of 600 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
N^^Q_ARTW_B1 | 60857.5418 | 38056.051 | 15.6667 | 37.8333 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
Q_KEP-HYB_15MW | 60745.9864 | 0 | 20.9167 | 0 | Kennedy Energy Park upper limit of 15MW | Outage | Discretionary | Qld
N_CROOKWF2_ZERO | 60601.2593 | 0 | 4.5833 | 0 | Crookwell wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>NIL_BWMP_RHBR-T | 60405.0617 | 185.4587 | 9.6667 | 0.33333 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
S_DCBUS_DC2 | 60400 | 0 | 0.33333 | 0 | Outage of Dry Creek 66kV bus section, DRYCGT2<=0 | Outage | Unit Zero | SA
S_DC_CBG3 | 60400 | 0 | 0.33333 | 0 | Outage of Dry Creek 66kV CB G3, DRYCGT3<=0 | Outage | Unit Zero | SA
F_S+TORRB2_R5 | 60037.4411 | 0 | 1.25 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B2 | Outage | FCAS | FCAS
N_COLEASF1_FLT_50 | 59985.7027 | 25640.5191 | 4.5833 | 1.9167 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_32282_MEWF | 59630.5331 | 111638.7444 | 3.6667 | 7.6667 | Limit 50% to Mt Emerald WF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
V_BANNERTSF_FLT_25 | 59219.6966 | 1196814.8022 | 6.0833 | 101.6667 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_S_HEYWOOD_UFLS | 59179.2511 | 30983.1398 | 23.75 | 110.3333 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC. Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
N_LIMOSF2_FLT_15 | 58989.5863 | 1177396.721 | 5.6667 | 94.5833 | Limit Limondale 2 solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_MAIN++NIL_BL_L60 | 58948.3944 | 132302.6486 | 869.6667 | 1172.0833 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
S>>CNRB_MKRB_WEMWP4 | 57501.1172 | 0 | 9.8333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
N>NIL_947_94T | 57353.3966 | 0 | 5.0833 | 0 | Out= Nil, avoid O/L Wellington to Orange North (947) on trip of Molong to Orange North (94T), Feedback | NIL | Thermal | NSW
S>>BRTX3_BWMP_WTTP | 56857.2092 | 31345.0546 | 4.25 | 3.25 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N^^Q_ARDM_B1 | 56646.7947 | 19765.4932 | 13.9167 | 9.5 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
S-MTM_0 | 55854.5173 | 0 | 9.5 | 0 | Discretionary upper limit for Mt Millar windfarm generation of 0 MW | Outage | Unit Zero | SA
V^^N_BADP_1 | 55575.4422 | 20813.4191 | 4.8333 | 7.8333 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
VSML_165 | 55478.0921 | 0 | 6.75 | 0 | Vic to SA on ML upper transfer limit of 165 MW | Outage | Discretionary | Vic
V_CWWF_FLT_55 | 55118.4368 | 803103.1132 | 7.8333 | 65.1667 | Limit Crowlands Wind Farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN++APD_TL_L5 | 54105.2835 | 38454.9576 | 1810.3333 | 2029.5 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
N_SILVERTWF_FLT_119 | 54061.2185 | 0 | 9.6667 | 0 | Limit Silverton Wind Farm upper limit to 119 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
N>N-WNMR_9R5_9R6 | 53851.9574 | 0 | 5.4167 | 0 | Out= Wagga North to Murrumburrah 132kV line (991), avoid O/L Wagga North to Wagga330 (9R5) on trip of Wagga North to Wagga 132 (9R6) line, Feedback | Outage | Thermal | NSW
T_REECE2_100 | 53382.9582 | 0 | 20.5833 | 0 | Discretionary 100 MW upper limit on Reece unit 2 | Outage | Discretionary | Tas
Q-X_STR_7C8C_HAUSF | 53216.8754 | 0 | 3.5 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Haughton Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
V_CWWF_FLT_0 | 51899.265 | 994710.5302 | 8.75 | 80.25 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
T>T_X_LIPM_TWO_D | 51649.8788 | 0 | 23.75 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L Tungatinah to Meadowbank Tee 1 on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
N>>NIL_DPTX_LV | 50450.9235 | 0 | 0.33333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
F_S+SNS_TG_R5 | 49725.8406 | 0 | 59.0833 | 0 | Raise 5 min Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line | Outage | FCAS | FCAS
F_T+MAXS_RREG | 49160.063 | 0 | 143.75 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS RREG FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
S>BRDV_BWPA_RHBR | 48973.8077 | 63412.2883 | 2 | 5.8333 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V>V_X_HWRO12_1 | 48423.0663 | 0 | 4.9167 | 0 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, avoid O/L Yallourn to Rowville No. 6, 7 or 8 220 kV lines on trip of Yallourn to Rowville No. 5 220 kV line line, feedback, YWG1 on 220 kV, Radial mode | Outage | Thermal | Vic
F_T+NIL_ML_L5 | 48259.0338 | 10941.1957 | 2201.3333 | 1343.8333 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V>>V_NIL_23 | 48014.3422 | 20613.4454 | 23.4167 | 10.5 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
F_MAIN++APD_TL_L6 | 47566.8022 | 3135.3644 | 1021.8333 | 328.25 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_S_LG1_L6 | 47515.9741 | 0 | 1.5 | 0 | Out= NIL, Ladbroke Grove Unit1 L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V::S_HYSE_MG_PPGT1_2 | 47319.068 | 0 | 2 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors O/S). Co-optimised eq PPGT1 LHS | Outage | Transient Stability | SA
Q_STR_7C8C_RUGSF | 47294.0705 | 141215.6314 | 3.6667 | 12.75 | Limit Rugby Run SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q-X_STR_7C8C_HAMSF | 46829.5937 | 0 | 3.0833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Hamilton Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_SMSF | 46804.5169 | 0 | 3 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Sun Metals Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q_STR_7C2K_KIDSF_3 | 46478.9104 | 87960.4115 | 3 | 6.9167 | No limit to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_T+NTH_RREG | 46216.0107 | 0 | 1.75 | 0 | Raise Regulation requirement for Northern Tasmania, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
Q_COLNVSF1_ZERO | 46015.5167 | 0 | 2.75 | 0 | Collinsville solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_KENSF1_ZERO | 45753.9785 | 0 | 13.6667 | 0 | Kennedy Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
Q-X_STR_7C8C_DAYSF | 45220.4112 | 0 | 2.9167 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Daydream Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
N_FINLYSF_FLT_93 | 45070.0817 | 0 | 4.5833 | 0 | Limit Finley solar farm upper limit to 93 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V::N_BYPASS_HW_SY_xxx | 44916.0216 | 8204.4788 | 28.1667 | 12.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Transient Stability | Vic
T_GO2_100 | 44720.3624 | 0 | 9.8333 | 0 | Discretionary 100 MW upper limit on Gordon unit 2. DS only. | Outage | Discretionary | Tas
VT_000 | 44662.1054 | 0 | 1.5833 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Discretionary | Vic
N>N-9GL-999_998 | 43756.6121 | 0 | 3 | 0 | Out= Bango973 WF to Yass 132kV line(9GL), avoid O/L Cowra to Bango999 (999) on trip of line 998, Feedback | Outage | Thermal | NSW
F_MAIN+APD_TL_L60 | 43733.8554 | 27046.533 | 1160.0833 | 254.75 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_I+NIL_APD_TL_L6 | 43442.1545 | 5536.4109 | 3444.1667 | 751.0833 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
Q_STR_7C2K_RRSF_7 | 43375.2931 | 0 | 18.8333 | 0 | Limit to Ross River Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q-X_STR_7C8C_WHTSF | 43315.0281 | 0 | 2.8333 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Whitsunday Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
S>>X_RBTU+HUWT_11 | 42963.4004 | 0 | 4.5 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV lineon trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
S-RBTX1+RBTX2_MLNK | 42927.9313 | 0 | 7.5 | 0 | Out= Robertstown 132/275kV TX1 + Robertstown 132/275kV TX2 O/S, limit import limit into SA on the Murraylink | Outage | Other | SA
N>>N-DTSS_20 | 42737.0551 | 0 | 6.5 | 0 | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage | Thermal | NSW
F_T++CSGO_TG_R5 | 42704.2054 | 21.8434 | 11 | 0.5 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
Q-X_STR_7C8C_HAYSF | 41435.4912 | 0 | 2.75 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Hayman Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
N::N_CNCW_2 | 40918.75 | 412008.5023 | 7.75 | 17.5 | Out = Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line | Outage | Transient Stability | NSW
Q-X_STR_7C8C_KIDSF | 40900.7095 | 0 | 2.75 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Kidston Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q-X_STR_7C8C_COLSF | 40704.7859 | 0 | 2.5833 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Collinsville Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
S_PELPT_GT1+2+PV_190 | 40327.5449 | 0 | 0.91667 | 0 | Discretionary upper limit for (Pelican PT GT1 +SA rooftop PV trip <=190 MW)&(Pelican PT GT2 +SA rooftop PV trip <=190 MW). NOTE: Refer to SO_OG_SA_12 section 4.4 | Outage | Discretionary | SA
Q-X_STR_7C8C_RRSF | 40071.7333 | 0 | 3.1667 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Ross River Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
S>>V_NIL_DVBG_STBG | 39590.8767 | 1616.238 | 9.6667 | 0.41667 | Out= Nil, avoid O/L Snowtown - Bungama 132kV on trip of Davenport - Bungama 275kV line, Feedback | NIL | Thermal | SA
V>>V_BABU_6 | 39303.5559 | 0 | 3.4167 | 0 | Out = Balranald to Buronga (X3) 220 kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
F_T+STH_NYR_ML_L5 | 39059.637 | 0 | 606.5 | 0 | Lower 5 min requirement for South Tasmania for loss of Nyrstar load | Outage | FCAS | FCAS
V::N_SMSC_xxx | 38515.4048 | 0 | 64.1667 | 0 | Out = One South Morang 330 kV series capacitor bank, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
F_I+NIL_APD_TL_L5 | 38464.7904 | 31750.0375 | 5568.1667 | 7127.75 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
Q_KENWF1_ZERO | 38368.9558 | 0 | 11.25 | 0 | Kennedy Wind Farm upper limit of 0MW | Outage | Unit Zero | Qld
Q_STR_7C2K_COLSF_3 | 38253.7165 | 71346.9014 | 2.5 | 5.5833 | No limit to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_I+NIL_MG_R5 | 38208.6525 | 56365.183 | 5094.8333 | 6578.3333 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL | FCAS | FCAS
N>>N-NIL_68 | 37838.28 | 0 | 1 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) on trip of Collector to Marulan (4) line, Feedback | NIL | Thermal | NSW
CA_BRIS_511836F4_1 | 37665.1469 | 0 | 2.9167 | 0 | Constraint Automation, O/L 947:L947:I:132@WELLNGTN@NSW for CTG LNQR on trip of WELLNGTN-MT_PIPER 72 330KV LN. Generated by STNET[NORVM2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
S-MWPS2-PV_0 | 37505.1227 | 22926.7507 | 9.3333 | 1.75 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW | Outage | Unit Zero | SA
F_T+MINS_L5 | 37312.6517 | 0 | 290.75 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS L5 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
Q>>TRSP_BKSP_MESP | 37172.7257 | 0 | 2.5833 | 0 | Out= 832 (H18 Tarong to H2 South Pine) 275 kV feeder, avoid O/L 838 (H36 Blackwall to H2 South Pine) 275 kV feeder on trip of 825 (H12 Mt England to H2 South Pine) 275 kV feeder, Feedback | Outage | Thermal | Qld
S-MWPS1-PV_0 | 37046.7326 | 16430.2562 | 9.0833 | 1.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 1 PV generation of 0 MW | Outage | Unit Zero | SA
N_BROKENHSF_FLT_25 | 36690.485 | 1579166.9813 | 3.75 | 133.4167 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_HAYSF_3 | 36546.2292 | 80874.7978 | 2.3333 | 6.4167 | No limit to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_T+MAXS_L6 | 36289.0975 | 0 | 25 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS L6 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
Q_WHITSF1_ZERO | 35964.5256 | 9381.6215 | 5.75 | 0.75 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S-MWPS4-PV_0 | 35786.3552 | 146701.5028 | 7.0833 | 14.0833 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW | Outage | Unit Zero | SA
F_T+MINS_R60 | 35689.2225 | 0 | 64.6667 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS R60 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
T_LIPM_PMWA_1_N-3 | 35382.5711 | 0 | 1.3333 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to <= southern load + 15 MW | Outage | Other | Tas
TV_350 | 35328.7685 | 0 | 42.1667 | 0 | Tas to Vic on Basslink upper limit of 350 MW | Outage | Discretionary | Tas
T_LIPM1_SLOAD_1_N-2 | 35289.5744 | 0 | 4.4167 | 0 | Out=Liapootah-Waddamana-Palmerston #1 220kV line and associated 220kV CBs at Waddamana I/S, loss of #2 parallel 220 kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Thermal | Tas
T_GO1_100 | 34792.6768 | 0 | 10.5 | 0 | Discretionary 100 MW upper limit on Gordon unit 1 | Outage | Discretionary | Tas
Q_STR_7C2K_WHTSF_3 | 34643.4923 | 82900.6858 | 2.25 | 6.5833 | No limit to Whitsunday Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
V::S_HYSE_MG_TPSB2 | 34611.5769 | 0 | 1 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (TIPSB2+ DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors I/S). Co-optimised eq TIPSB2 LHS. | Outage | Transient Stability | SA
V^^N_SDUT_1 | 34268.3677 | 76980.1139 | 2.25 | 28.75 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_T++LREG_0050 | 34189.7669 | 37550.2011 | 283.4167 | 432.4167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
N_FINLYSF1_ZERO | 34095.0886 | 79947.9143 | 2.1667 | 4.1667 | Finley solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>>NIL_7_3 | 34018.8278 | 2988.0939 | 0.33333 | 2.5 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_DAYSF_3 | 33738.1537 | 73369.4903 | 2.1667 | 5.75 | No limit to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_NQ_SEMI_ZERO | 33505.9782 | 0 | 2.1667 | 0 | Limit all North Qld semi-scheduled generators to zero | Outage | Unit Zero | Qld
Q_YARANSF1_ZERO | 32880.4233 | 1316.4662 | 6.1667 | 1.3333 | Yarranlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
NRM_VIC1_SA1 | 32834.9049 | 4056.5873 | 2.5833 | 1.3333 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue | Negative Residue
T>T_X_LIPM_TWO_C | 32712.8228 | 0 | 20.8333 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Thermal | Tas
S_DVRB2_270 | 32619.3256 | 36089.0314 | 8.75 | 8.0833 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
S>>RBTU_RBPA_WEWT | 32579.5354 | 19447.6519 | 16.25 | 3.25 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
N>>99F_994_63 | 32549.7922 | 0 | 2.75 | 0 | Out= Uranquinty to Narrandera (99F) 132kV line, avoid O/L Yanco to Wagga330 (994) on trip of Darlington Point to Wagga330 (63) 330kV line, (Note: Option C on OM521) | Outage | Thermal | NSW
Q_STR_7C2K_SMSF_3 | 32154.0303 | 0 | 2.0833 | 0 | No limit to Sun Metals Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
V^^V_NIL_SWVIC | 31655.7743 | 0 | 20.5833 | 0 | Out = Nil, manage flow towards Moorabool across Haunted Gully to Moorabool and Mortlake to Moorabool 500kV lines to avoid voltage instability for the loss of Haunted Gully to Moorabool 500kV line and both APD potlines | NIL | Voltage Stability | Vic
S>>CNRB_MKRB_BWMP | 31617.1986 | 0 | 3.8333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Blyth West-Blyth Munno Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
N>NIL_99U | 31438.7548 | 0 | 3.0833 | 0 | Out= Nil avoid O/L Sebastipol to Wagga North (99U) 132kV line on trip of Nil, Feedback | NIL | Thermal | NSW
N>>NIL_84_88_S | 31347.2966 | 0 | 42.25 | 0 | Out= NIL, avoid O/L Tamworth to Liddell (84) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL | Thermal | NSW
Q_STR_7C2K_HAMSF_3 | 31170.9365 | 82932.3957 | 2 | 6.5 | No limit to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_S+TB1_R5_70M | 30999.11 | 0 | 0.83333 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B1 for 70 MW metro gen trip option | Outage | FCAS | FCAS
F_T+CSGO_TG_R6_3 | 30281.4961 | 0 | 0.25 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment3 | Outage | FCAS | FCAS
F_T++NIL_MG_RECL_R6 | 30249.129 | 12471.293 | 78.25 | 77.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
V^^S_SETB_TBSE_2 | 30238.4757 | 1438.5139 | 5 | 2.0833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Voltage Stability | SA
Q_KMBG_7184 | 30200 | 0 | 0.16667 | 0 | Out= 7184 Kamerunga Barron Gorge PS 132kV line | Outage | Unit Zero | Qld
F_I+GFT_TG_R60 | 30178.5804 | 22054.0644 | 467 | 262.9167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
N_SUNRSF_FLT_120 | 29658.3013 | 0 | 3.0833 | 0 | Limit Sunraysia solar farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_8C_7C2K_RGBSF | 29642.7978 | 42983.2873 | 2.3333 | 3.3333 | No limit to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
F_QNV+MG_R6 | 28667.7002 | 0 | 4 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_ESTN+LREG_0210 | 28432.4109 | 0 | 161.5833 | 0 | Eastern Lower Regulation Requirement greater than 210 MW | Outage | FCAS | FCAS
N>>N-PKWL_94K_1 | 28333.3381 | 225616.2755 | 7.3333 | 31.25 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
V_CWWF_FLT_48 | 28117.9241 | 0 | 6.8333 | 0 | Limit Crowlands Wind Farm upper limit to 48 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 28080.2866 | 7872.9906 | 23.5 | 31.0833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Thermal | Vic
V_ELAINEWF_ZERO | 27685.6741 | 3356.727 | 13.4167 | 2.3333 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
F_S+ML_L60 | 27555.7242 | 0 | 36.8333 | 0 | Lower 60 sec Service Requirement for SA island for loss of Murraylink | Outage | FCAS | FCAS
V_OWF_NRB_0 | 27422.717 | 58451.7233 | 2.0833 | 4.9167 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Discretionary | Vic
F_Q++ARTW_L5 | 27308.5591 | 158747.6903 | 52.5833 | 122.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
N::N_SDUT_2 | 27156.4935 | 69169.4866 | 21.1667 | 42.75 | Out = Upper Tumut-Stockdill (1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
N_WELLSF1_ZERO | 27115.7544 | 21017.405 | 1.5 | 1.6667 | Wellington solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_MURRAWRWF_FLT_135 | 26924.5028 | 0 | 7.25 | 0 | Limit Murra Warra Wind Farm 1+2 upper limit to 135 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
V::N_HYSE_xxx | 26795.5632 | 1880.3852 | 12.4167 | 3.4167 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
T^V_NIL_9 | 26772.4788 | 2645.1797 | 28.75 | 9.1667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
S>NIL_NWRB1_MWP3RB | 26508.1985 | 0 | 1.4167 | 0 | Out= NIL, avoid O/L Morgan Pipeline 3-Robertstown 132kV line on trip of North West Bend-Roberstown 132kV line, Feedback | NIL | Thermal | SA
T_LIPM_PMWA_2_N-3 | 25518.498 | 0 | 3.3333 | 0 | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to >= southern load - 15 MW | Outage | Other | Tas
Q_STR_7C2K_RRSF_3 | 25334.3196 | 9025.9404 | 2 | 5.9167 | No limit to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
S:V_PA_SVC_270 | 25316.9017 | 45901.9785 | 36.5833 | 45.5 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
F_T+CSGO_TG_R6_2 | 25172.9032 | 2129.9416 | 53.25 | 5.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS | FCAS
Q_STR_7C2K_KIDSF_7 | 24978.6297 | 0 | 18.75 | 0 | Limit to Kidston Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HASF_6 | 24754.1925 | 0 | 1.4167 | 0 | No limit to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>250&270(AVG),Ross_FN>100&120(AVG),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
V_KARADSF_FLT_54 | 24591.0735 | 0 | 6.5833 | 0 | Limit Karadoc solar Farm upper limit to 54 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_BANNERTSF_FLT_53 | 24177.0097 | 0 | 6.5 | 0 | Limit Bannerton Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_S_LG2_L6 | 24138.45 | 0 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V>S_460_DYN | 23720.666 | 919.5312 | 11.0833 | 1.8333 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | Vic
V_YATPSF_FLT_49 | 23415.9088 | 0 | 7 | 0 | Limit Yatpool solar Farm upper limit to 49 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^^V_DDSM1 | 22901.2299 | 60555.7224 | 22.6667 | 72.5833 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
I_CTRL_ISSUE_ML | 22740.2581 | 10186.1105 | 7.1667 | 4.0833 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
Q::N_8C8J_AR_2LG_N-2 | 22508.9333 | 0 | 3 | 0 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage | Transient Stability | Qld
N::Q_NIL_KC | 22305.5813 | 351.2527 | 0.16667 | 2.5833 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | Transient Stability | NSW
T>T_NIL_BL_IMP_6E | 22024.5462 | 0 | 0.75 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
S>>BWMP_BRTW_WTTP | 22008.0998 | 11.8593 | 9 | 0.083333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
S-CRK_0 | 21805.922 | 0 | 3.0833 | 0 | Discretionary upper limit for Cathedral Rocks windfarm generation of 0 MW | Outage | Unit Zero | SA
Q>>CPST_CLWU_RGLC | 21638.2275 | 844622.0053 | 19.5 | 101.9167 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
N>N_968_969_NIL_1 | 21590.9817 | 0 | 2 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line and 96M(Narrabri to Moree), avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
V_GANWRSF_FLT_25 | 21376.3361 | 387688.2672 | 2.25 | 31.5833 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_T+NIL_MG_R5 | 21035.5462 | 2524.4571 | 1724.3333 | 404.75 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
T_LIPM2_SLOAD_1_N-2 | 20497.8146 | 0 | 2.1667 | 0 | Out=Liapootah-Waddamana-Palmerston #2 220kV line and associated CBs at Waddamana I/S, loss of the #1 parallel 220kV line and Nyrstar load declared credible, limit Sth to Nth flow to rating of PM-WA 110kV line minus Nyrstar MW, feedback | Outage | Thermal | Tas
V_MOORBWF_150_0SWT | 20278.8536 | 0 | 6.1667 | 0 | Moorabool Wind Farm upper limit of 150 MW. Limit Moorabool wind farm to 0 MW if any turbine online from the Moorabool wind farm - South (Cluster 2) | Outage | Discretionary | Vic
V::N_ESTN_TBSE_O1 | 20272.2025 | 0 | 14.8333 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
Q_STR_7C2K_HASF_1 | 20226.6102 | 0 | 1.5 | 0 | No limit to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON, Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_RUGSF_1 | 20226.5858 | 0 | 1.5 | 0 | No limit to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_COLSF_1 | 20226.5822 | 0 | 1.5 | 0 | No limit to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,((NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
S>>BRDV_RBTU_WEWT | 19982.8538 | 25263.0637 | 2 | 2.6667 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S:V_XPAVC_310 | 19976.6095 | 50540.2322 | 24.1667 | 57.6667 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
F_T+MAXS_R5 | 19907.4229 | 0 | 264.5 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS R5 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
S>>X_RBTU+RBTX_16 | 19830.7441 | 0 | 4.25 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage | Thermal | SA
F_T+MINS_R6 | 19724.5057 | 0 | 12.25 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS R6 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
F_I+TTS_TG_R6 | 19642.6585 | 200.3546 | 395.9167 | 19.5833 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
T_FARC1_2 | 19479.5679 | 268.7431 | 12.9167 | 1.1667 | Out=Farrell - Reece 1 220KV line. Discretionary 144 MW limit on Reece 2 + Granville Harbour WF | Outage | Discretionary | Tas
N>>NIL_998 | 19405.0895 | 0 | 0.83333 | 0 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
N^^V_NIL_ARWBBA | 19390.0047 | 6121.3348 | 28.8333 | 22 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
V>S_460 | 19319.2194 | 1024.299 | 15.0833 | 4.0833 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage | Thermal | Vic
Q_OKYTX3 | 19257.1393 | 3966.8986 | 1.8333 | 11.0833 | Out = Oakey 3T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 67.3MW | Outage | Thermal | Qld
N_DARLSF_FLT_193 | 19097.322 | 0 | 1.3333 | 0 | Limit Darlington Pt Solar Farm upper limit to 193 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_T+NTH_WF_TG_R6 | 19035.625 | 0 | 1.8333 | 0 | Raise 6 sec requirement for North Tasmania for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+NIL_WF_TG_R5 | 18970.1923 | 7353.9339 | 1008.75 | 1430.5 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_MAIN++GFT_TG_R60 | 18936.8874 | 11974.9405 | 147 | 81.5833 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
N_BROKENHSF_FLT_32 | 18678.6453 | 0 | 5.4167 | 0 | Limit Broken Hill Solar Farm upper limit to 32 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_T+MINS_L60 | 18382.3769 | 0 | 126.5833 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS L60 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
V_WEMENSF_FLT_25 | 18272.3403 | 618317.0275 | 3.0833 | 51.3333 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_8C_7C2K_RGUSF | 18036.5827 | 0 | 1.3333 | 0 | No limit to Rugby Run SF to if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8+ one SVC(Dysart or Nebo or Strathmore) OS OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2+Dysart SVC OS ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
S-OUT_WTPT_SC+INV_1 | 17922.4136 | 0 | 2.25 | 0 | Out=HUBG Or HUWT line Or one CB(HU 6135/6060,BG 6246,WT 7022/7021), limit output of Wattle Pt WF based on Wattle Pt statcom status & the number of Dalrymble battery inverters I/S (Note:swamped for No. of Dalrymple bat. inverters < 10 && 1or2 SC O/S) | Outage | Other | SA
Q_STR_7C2K_WHTSF_7 | 17892.2617 | 0 | 12.8333 | 0 | Limit to Whitsunday Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>NIL_RBPA_RBTU | 17790.958 | 0 | 2.5833 | 0 | Out= Nil, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | NIL | Thermal | SA
V>>V_DDTX_C | 17727.5965 | 0 | 3 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage | Thermal | Vic
N>Q-NIL_757_758 | 17679.7296 | 52062.6586 | 56.6667 | 115.25 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL | Thermal | NSW
NQ_700_DYN_TEST | 17523.3538 | 0 | 15.75 | 0 | NSW to QLD on QNI upper transfer limit of 700 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | NSW
F_Q++8C_L6 | 17492.6259 | 8308.0308 | 24.8333 | 56.4167 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C2K_CLRSF_1 | 17133.141 | 0 | 1 | 0 | No limit to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Kar>=2+ Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q>>CLWU_BCRG_BCCP | 16976.4181 | 213.8838 | 3.5 | 0.66667 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
Q_STR_32282_RGBSF | 16954.648 | 0 | 1.25 | 0 | Limit 50% to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
S>>MKRB_BRTW_WTTP | 16937.2073 | 0 | 1.5833 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
Q^FNQ_MEWF_-60_-100 | 16703.8682 | 0 | 0.16667 | 0 | Nominated Offset= -60MW (Fdr7139 and Fdr7301 closed),-100 (Fdr7139 and Fdr7301 opened) Far North Qld Voltage Stability limit for loss of Mt Emerald Windfarm during system normal configuration (Fdr857+877 IS) | Outage | Voltage Stability | Qld
N>>X-WG5012+TX2_02_L | 16678.4915 | 0 | 1.6667 | 0 | Out = Wagga 330kV CB 5012 (Option 1) + Wagga 330/132kV TX2 O/S, avoid O/L one Yass 132/330kV TX on trip of other Yass 132/330kV TX , Feedback | Outage | Thermal | NSW
Q_YARANSF1_ZERO_N-1 | 16399.3476 | 0 | 1.6667 | 0 | Limit Yarrenlea Solar Farm to 0 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip,Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
F_T+NIL_MG_RECL_R5 | 16300.89 | 6333.9442 | 1232.0833 | 1486.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_S_HPRL_RREG-5MW | 16176.6102 | 0 | 0.33333 | 0 | Out= NIL, Hornsdale Battery (Load Component) RREG Requirement <= 5MW | Outage | FCAS | FCAS
V_KIAMSF_40INV_DYN | 16173.2608 | 0 | 1.5833 | 0 | Limit Kiamal Solar Farm upper limit to 0 MW if number of inverter available exceeds 40 and Murra Warra 2 WF Syncon O/S. Constraint swamps out otherwise. DS only | Outage | System Strength | Vic
Q::N_BI_POT_-450 | 16069.9784 | 0 | 4 | 0 | Nominated Offset -450MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage | Transient Stability | Qld
S>>CNRB+BRTW_01 | 15918.4352 | 0 | 2.75 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown- Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_T+MAXS_LREG | 15688.4065 | 0 | 132.9167 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS LREG FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
Q_STR_32282_DAYSF | 15624.9511 | 0 | 1.1667 | 0 | Limit 50% to Daydream SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_I+BIP_ML_L6 | 15529.5447 | 0 | 33.3333 | 0 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL | FCAS | FCAS
F_I+BIP_ML_L60 | 15515.33 | 0 | 23.9167 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL | FCAS | FCAS
Q_NIL_STRGTH_SMSF | 15500 | 2532.59 | 0.083333 | 3.1667 | Out = Nil, limit Sun metals solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
S_PPT_0 | 15500 | 0 | 0.083333 | 0 | Pelican Pt Power Station out of service | Outage | Unit Zero | SA
S>>BRTW_BWPA_WTTP | 15335.9192 | 1548.8083 | 1.3333 | 2 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N_V_HV1150 | 15100 | 0 | 0.083333 | 0 | Discretionary constraint on transfer from NSW to VIC of 1150 MW on DDTS-NSW cutset | Outage | Discretionary | NSW
Q_BRBRA_8838 | 15100 | 0 | 0.083333 | 0 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 | Outage | Unit Zero | Qld
S-SNPT_0 | 15100 | 0 | 0.083333 | 0 | Snapper Pt Power Station out of service | Outage | Unit Zero | SA
S>NIL_NIL_NWMH2 | 15100 | 31.2715 | 0.083333 | 0.5 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
N>>NIL_84_83_OPEN | 15071.9643 | 0 | 5.5 | 0 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | Thermal | NSW
Q_STR_7C8C_COLSF | 14986.0178 | 175361.4387 | 1.1667 | 14.4167 | Limit Collinsville SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_S+PAREP_R60 | 14903.0055 | 0 | 10.9167 | 0 | Raise 60 sec Service Requirement for SA island for loss of Davenport - Pt Patterson 275kV line | Outage | FCAS | FCAS
N>N_96M_969_NIL | 14721.2882 | 0 | 2.3333 | 0 | Out= Any one 132kV feeder between Moree to Boggabri East (96M,9UH,9UJ),avoid O/L on 969 (Gunnedah to Tamworth) 132 kV on Nil trip, Feedback | NIL | Thermal | NSW
S-SA_DVRB_GEN_0300 | 14677.9074 | 0 | 1.6667 | 0 | Discretionary upper limit for SA generation connected at Davenport and between Davenport-Robertstown 275kV lines of 300MW. | Outage | Discretionary | SA
S>>X_RBTU+RX+HUSN_10 | 14668.5653 | 0 | 1 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Templers-Roseworthy 132 kV on trip of Templers West-Para 275 kV line, Feedback | Outage | Thermal | SA
F_Q++8C_L60 | 14609.1328 | 9073.8119 | 24.5 | 55.8333 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
N_SILVERTWF_FLT_100 | 14563.132 | 787783.7307 | 1.25 | 66.75 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
Q_STR_32282_HAMSF | 14332.235 | 0 | 1.0833 | 0 | Limit 50% to Hamilton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_T++NIL_MG_R6 | 14290.9587 | 4697.8029 | 13.5 | 18.25 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_QNV++MG_R6 | 14239.5359 | 0 | 36.25 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>SETX_NIL_SETX | 14084.6734 | 321265.7892 | 4.0833 | 84.5833 | Out= One South East 275/132kV transformer O/S, avoid O/L of other South East 132/275kV TX on Nil trip, | NIL | Thermal | SA
N::V_DDSM_MSDD | 14059.3789 | 193.002 | 3.8333 | 1.1667 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
VSML_ZERO | 13872.9695 | 66397.2129 | 3.5833 | 19.6667 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
Q_STR_7C8C_DAYSF | 13821.8458 | 161889.5294 | 1.0833 | 13.3333 | Limit Daydream SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_KIATAWF_FLT_18 | 13746.1819 | 26252.0081 | 3.0833 | 2.5 | Limit Kiata Wind Farm upper limit to 18 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V::S_SEVC_MAXG | 13620.8126 | 0 | 4.8333 | 0 | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
Q^^CS_-360 | 13617.542 | 0 | 4.8333 | 0 | Nominated Offset -360MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage | Voltage Stability | Qld
F_MAIN+APD_TL_L5 | 13614.9113 | 8393.8681 | 963 | 255.5 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_KIAMSF_40INV | 13503.6887 | 0 | 1.5833 | 0 | Limit Kiamal Solar Farm upper limit to 0 MW if number of inverter available exceeds 40. Constraint swamps out otherwise. DS only | Outage | System Strength | Vic
V^T_NIL_9 | 13344.4892 | 3554.6364 | 24.4167 | 6.3333 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL | Voltage Stability | Vic
F_I+NIL_WF_TG_R6 | 13343.1911 | 0 | 0.083333 | 0 | Out= Nil, Global Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line | NIL | FCAS | FCAS
Q_STR_32282_KEP | 13252.6125 | 0 | 2.5 | 0 | Limit 50% to kennedy Energy Park if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_I+TTS_TG_R60 | 13235.6879 | 2553.1752 | 675.5833 | 92.1667 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
F_MAIN+APD_TL_L6 | 13017.5543 | 157.98 | 814.25 | 14.9167 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q>>CPPW_WOSP_WOGP_2 | 12919.1769 | 0 | 4 | 0 | Out= Calliope River to Palmwoods (813+810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
Q-X_STR_7C8C_RUGSF | 12884.2619 | 0 | 0.83333 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Rugby Run Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
Q_CHILDSF1_ZERO | 12715.4267 | 0 | 1.0833 | 0 | Childers Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
V::S_SEVC1+PWSE_MAXG | 12710.2628 | 0 | 2.75 | 0 | Out= Either one of the South East SVC+Penola West-South East 132kV (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
Q_STR_7C2K_CLRSF_7 | 12673.56 | 0 | 15.8333 | 0 | Limit to Clare Solar Farm 80% if Stan>=2+Stan+Cal>=3+Glad>=2+ (Stan+Cal+Glad) >=7,Kareeya >=2, NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_BULGANAWF_FLT_111 | 12608.6256 | 0 | 1.0833 | 0 | Limit Bulgana Wind Farm upper limit to 111 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V::S_KNPW_MAXG | 12495.1409 | 0 | 7.8333 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA.. | Outage | Transient Stability | SA
Q_STR_7C8C_HAYSF | 12155.7347 | 180502.0552 | 1.0833 | 15.6667 | Limit Hayman SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
CA_BRIS_52460E76_1 | 12075.2913 | 0 | 1.5 | 0 | Constraint Automation, O/L XFMR T_1@R_TOWN@SA for CTG LS6W on trip of W_LOO - WATE_E 132KV 1 LINE. Generated by STNET[BNECR1] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
Q_STR_7C2K_COLSF_5 | 12068.6169 | 0 | 1 | 0 | No limit to Collinsville Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
N_LIMOSF1_FLT_132 | 11862.2401 | 0 | 1.25 | 0 | Limit Limondale 1 solar farm upper limit to 132 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
T>T_NIL_BL_IMP_7CC | 11823.9287 | 455.1487 | 12.9167 | 1.8333 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
VS_250_DYN | 11796.8367 | 37928.4376 | 4.75 | 8.5 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
F_ESTN+RREG_0220 | 11791.2561 | 0 | 53.8333 | 0 | Eastern Raise Regulation Requirement greater than 220 MW | Outage | FCAS | FCAS
Q_STR_7C2K_RUGSF_3 | 11632.4244 | 54975.5767 | 0.75 | 4.3333 | No limit to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_NIL_STRGTH_HAUSF | 11500.0971 | 2457197.1515 | 1.25 | 191.4167 | Out = Nil, limit Haughton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
S>>NIL_TBTU_TBMO_1 | 11454.835 | 2161.3316 | 4.75 | 2.8333 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S>>X_RBTU+RX+HUSN_13 | 11356.7307 | 0 | 1.75 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
N>>V-LTYS_64_7_15M | 11337.6365 | 0 | 5 | 0 | Out= Lower Tumut to Yass(3), avoid O/L Lower Tumut to Upper Tumut (64), on trip of Lower Tumut to Canberra (7) ,Feedback | Outage | Thermal | NSW
T>T_NIL_BL_110_4 | 10928.8514 | 55426.4294 | 8.5833 | 68.9167 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
S>>CNRB+BRTW_04 | 10913.253 | 0 | 5.75 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Morgan Whyalla 4 -Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
S:VS_PA_SVC_620 | 10866.8527 | 0 | 9.9167 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage | Oscillatory Stability | SA
Q_STR_7C8C_WHTSF | 10797.0614 | 86626.6142 | 1 | 8 | Limit Whitsunday SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>>N-964_DC | 10768.9664 | 0 | 11.5833 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage | Thermal | NSW
N^^V_NIL_1 | 10754.1215 | 82621.9489 | 17.75 | 114.8333 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
N>NIL_9GL | 10711.9335 | 0 | 1.0833 | 0 | Out= Nil, avoid O/L Bango973 to Yass (9GL) on trip of Nil, (Note: Swamped when 999 is O/S) | NIL | Thermal | NSW
V>NWB6022_TX1 | 10655.4464 | 0 | 3.3333 | 0 | Out= North West Bend CB 6022 O/S, avoid O/L North West Bend 275/132kV TX1 on trip of North West Bend 275/132kV TX3, Feedback | Outage | Thermal | SA
V^^N_DPWG_X5_1 | 10649.7071 | 189341.2673 | 7.6667 | 73.3333 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S>>X_RBTU+RX+HUSN_14 | 10423.3973 | 0 | 2.9167 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line + Hummocks??Snowtown 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
S>NIL_RBMWP3_RBNW1 | 10412.1751 | 0 | 15.1667 | 0 | Out= Nil, avoid O/L Robertstown-North West Bend #1 132kV line on trip of Robertstown-Morgan Pipeline 3-Morgan Pipeline 2-Morgan Pipeline 1-North West Bend 132kV #2 line, Feedback | NIL | Thermal | SA
F_MAIN++NIL_MG_R5 | 10397.952 | 33925.0508 | 922 | 1525.0833 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
N^^Q-X_AR_LS_VC_B1, 2, 3, 4, 5, 6 | 10291.4944 | 0 | 5.5833 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
Q_RGBYRSF1_ZERO | 10290.1982 | 37461.469 | 0.75 | 2.75 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_Q++8E_L6 | 10214.3999 | 3270.9847 | 24.9167 | 18.5833 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V::S_SEVC1_MAXG | 10158.7589 | 0 | 1 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
Q::N_BI_POT_-500 | 10139.1917 | 0 | 2.9167 | 0 | Nominated Offset -500MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage | Transient Stability | Qld
N_METZSF_85 | 10135.4631 | 0 | 3.6667 | 0 | Metz Solar farm upper limit of 85 MW | Outage | System Strength | NSW
V>>N_NIL_65 | 10104.6593 | 48318.6877 | 10.25 | 5.75 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
S_HALWF_0 | 9961.2389 | 82442.991 | 0.75 | 6.8333 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW | Outage | Unit Zero | SA
V_WEMENSF_FLT_53 | 9948.964 | 0 | 2.6667 | 0 | Limit Wemen Solar Farm upper limit to 53 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_Q++BCDM_L6 | 9879.941 | 22246.2802 | 24.4167 | 122 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C8C_RRSF | 9865.7305 | 153767.5436 | 5.8333 | 26.6667 | Limit Ross River SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_T++NIL_MG_RECL_R5 | 9708.2977 | 6903.7099 | 72 | 120 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
N_MOLNGSF1_ZERO | 9569.4516 | 0 | 0.75 | 0 | Molong solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
S^NIL_CRK+MTM+PLN110 | 9408.4173 | 0 | 2.5 | 0 | Out= Nil, upper limit for Cathedral Rocks WF + Mt Millar WF + Port Lincoln generation <= 110 MW to maintain voltage stability limits | NIL | Voltage Stability | SA
F_Q++8E_L60 | 9282.8411 | 3821.7053 | 24.3333 | 18.5 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
N>>LDTM_964_81_OPEN | 9008.2314 | 0 | 5 | 0 | Out= Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage | Thermal | NSW
N_MOREESF1_23INV | 8991.3321 | 0 | 0.58333 | 0 | Limit Moree Solar Farm upper limit to 0 MW if number of inverter available exceed 23. Constraint swamp out otherwise. | Outage | System Strength | NSW
S>>X_RBTU+RX+HUSN_15 | 8989.1168 | 0 | 1.5 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
T>T_NIL_BL_IMP_7C | 8978.2643 | 572.955 | 13.25 | 1 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
N_LIMOSF2_FLT_18 | 8918.42 | 0 | 1.0833 | 0 | Limit Limondale 2 solar farm upper limit to 18 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N>999_9GL_NIL | 8816.4778 | 0 | 1 | 0 | Out= Bango999 WF to Cowra 132kV line(999), avoid O/L Bango973 to Yass (9GL) on trip of Nil, Feedback | NIL | Thermal | NSW
V^^N_CNYS_1 | 8803.7639 | 197.7762 | 4.25 | 0.33333 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_S+PAREP_R5 | 8762.6966 | 0 | 11.8333 | 0 | Raise 5 min Service Requirement for SA island for loss of Davenport - Pt Patterson 275kV line | Outage | FCAS | FCAS
S:VS_PA_SVC_420 | 8687.1593 | 2272.2299 | 9.75 | 2.4167 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
Q_CS_1700 | 8546.4133 | 0 | 2.0833 | 0 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary) | Outage | Discretionary | Qld
S>>MKRB_BWMP_WTTP | 8529.0009 | 0 | 1.4167 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
T_CTHLWF_020 | 8522.7861 | 0 | 0.91667 | 0 | Wild Cattle Hill Wind Farm upper limit of 20 MW | Outage | Discretionary | Tas
V_KIAMSF_FLT_120 | 8514.4334 | 0 | 4.5833 | 0 | Limit Kiamal Solar Farm upper limit to 120 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_I+GFT_TG_R6 | 8504.5289 | 1403.6462 | 241.0833 | 40.3333 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
N_COLEASF1_ZERO | 8477.8521 | 871283.0566 | 0.66667 | 66.75 | Coleambally solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_STOCKYH_ZERO | 8454.7822 | 123694.7207 | 0.66667 | 105.6667 | Stockyard Hill wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
VSML_195 | 8434.2478 | 0 | 1.0833 | 0 | Vic to SA on ML upper transfer limit of 195 MW | Outage | Discretionary | Vic
Q_NIL_STRGTH_KBWF | 8414.4033 | 0 | 0.75 | 0 | Out = Nil, limit Kaban Wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
S_DVCN_270 | 8412.1671 | 0 | 1.8333 | 0 | Out = Mt Lock 275 kV CB8020 or CB8018, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+ Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
F_MAIN++ML_L6_0400 | 8400.7408 | 16004.7461 | 809.9167 | 1166.25 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
CA_BRIS_5233A5C6_1 | 8347.8056 | 0 | 1.5833 | 0 | Constraint Automation, O/L XFMR 3H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
V_COHUNASF_ISL_0 | 8345.2502 | 975.0012 | 0.66667 | 0.083333 | Cohuna Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_MAIN+NIL_MG_R5 | 8247.339 | 2201.6914 | 1064.3333 | 234.9167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
N_SUNRSF_FLT_50 | 8182.968 | 462687.4758 | 1.1667 | 37.8333 | Limit Sunraysia solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V^S_HYCP | 8150.7335 | 0 | 14.5833 | 0 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL | Voltage Stability | Vic
F_Q++BCDM_L60 | 8087.7004 | 32699.3051 | 22.5833 | 126.5 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
F_QNV++MG_R60 | 8042.4536 | 0 | 52.3333 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
Q_STR_7C2K_RUGSF_5 | 8026.1701 | 0 | 0.58333 | 0 | No limit to Rugby Run Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
S>>X_RBTU+HUWT_10 | 7957.796 | 0 | 2.25 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage | Thermal | SA
NQ_600_TEST | 7951.9739 | 0 | 10.8333 | 0 | NSW to Qld on QNI upper transfer limit of 600 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
V>>NIL_ELML_BAML2 | 7869.5737 | 0 | 16.9167 | 0 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL | Thermal | Vic
T>>T_NIL_BL_EXP_7C | 7833.7266 | 1594.9968 | 9.9167 | 6.5833 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
NQ_700_TEST | 7751.4379 | 0 | 6.6667 | 0 | NSW to Qld on QNI upper transfer limit of 700 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | NSW
N_LIMOSF1_FLT_50 | 7703.337 | 317589.9724 | 1.9167 | 26 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_MIDDLSF1_ZERO | 7676.0818 | 0 | 0.58333 | 0 | Middlemount Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N^^Q_AR_330_BS5_1_B1 | 7609.2217 | 2618.6242 | 3.9167 | 4.25 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
V_KIAMSF_0 | 7474.4361 | 0 | 0.75 | 0 | Out = Kiamal Syncon, limit Kiamal solar farm to 0 MW | Outage | Discretionary | Vic
N>>N-DTKV_CTMN | 7472.6922 | 0 | 1.25 | 0 | Out= Dapto- Kangaroo Valley (18), avoid O/L Crookwell to Bannaby (61) on trip Collector WF to Marulan (4) line, Feedback | Outage | Thermal | NSW
S-BUPV1_0 | 7352.1577 | 105166.9595 | 0.5 | 8.5 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
F_MAIN+GFT_TG_R6 | 7346.3423 | 20.79 | 39.4167 | 0.33333 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q^WOPW_CS_WOSP_O | 7339.5763 | 0 | 2.4167 | 0 | Out= Any of the 275kV lines between Woolooga to South Pine (807,808 or 810),avoid voltage instability on CQSQ on trip of the remaining 275kV Parallel line lines between Woolooga to South Pine (807,808 or 810) (132kV and 110kV parallel network open) | Outage | Voltage Stability | Qld
F_T++CSGO_TG_R6 | 7319.2019 | 56.9453 | 8 | 0.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
V_MTMERCER_ZERO | 7305.2108 | 313648.9415 | 2.0833 | 25.8333 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
S>>BWMP_RBTU_WTTP | 7299.4794 | 6747.1843 | 2.5833 | 1.1667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V_GANWR_SF_BAT_50 | 7152.6995 | 38920.0484 | 3.0833 | 11.75 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
N^^V_BADP_1 | 7074.9398 | 0 | 4.6667 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N>>NIL_88_84_S | 7022.2759 | 0 | 10.5833 | 0 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | NIL | Thermal | NSW
N>>AVMA-17_39_11 | 7008.7787 | 0 | 5.3333 | 0 | Out = Avon - Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage | Thermal | NSW
S_CRK_20 | 6995.559 | 0 | 0.58333 | 0 | Discretionary upper limit for Cathedral Rocks windfarm generation of 20 MW | Outage | Discretionary | SA
V_T_NIL_BL1 | 6934.8003 | 6289.4855 | 8.8333 | 11.9167 | Out=Nil, Basslink no go zone limits Vic to Tas. Limit Basslink lower limit to -125 MW on 1st DI out of no go zone. i.e. BL >= -125 MW | NIL | Other | Vic
F_QNV++GFT_TG_R60 | 6862.3463 | 0 | 24.1667 | 0 | Raise 60 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S_DV-RB2_DYNAMIC | 6768.9872 | 0 | 0.5 | 0 | Discretionary DYNAMIC upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= MAXG SA(i.e.function X_SA_MAXG_ST_DS) | Outage | Discretionary | SA
Q_STR_7C8C_HAMSF | 6432.0662 | 206553.1839 | 0.5 | 17.4167 | Limit Hamilton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_BLUEGSF1_ZERO | 6411.6469 | 0 | 0.58333 | 0 | Bluegrass Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_T+NIL_TL_L5_DS | 6411.5 | 0 | 0.083333 | 0 | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T+FARE_N-2_TG_R5 | 6388.8578 | 70.9174 | 8.5833 | 6.6667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
VT_100 | 6340.7298 | 0 | 0.5 | 0 | Vic to Tas on Basslink upper limit of 100 MW | Outage | Discretionary | Vic
S_DV-RB2_050 | 6328.1476 | 0 | 0.5 | 0 | Discretionary upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 50 MW | Outage | Discretionary | SA
S>>MKRB_CNRB_WEMWP4 | 6312.8418 | 0 | 4.25 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Morgan Whyalla 4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | Thermal | SA
N>>N-NIL_8E_8C | 6269.6059 | 0 | 0.16667 | 0 | Out = Nil, avoid O/L Sapphire to Armidale (8E) on trip of Dumaresq to Armidale (8C) line, Feedback | NIL | Thermal | NSW
Q_STR_32282_COLSF | 6268.2065 | 0 | 0.5 | 0 | Limit 50% to Collinsville SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C_7C2K_EMSF | 6203.9878 | 42983.2741 | 0.5 | 3.3333 | No limit to Emerald SF if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8 OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_MIDSF | 6203.9872 | 0 | 0.5 | 0 | No limit to Middlemount SF to if Stan>=3+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=8 OR Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar.=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise | Outage | System Strength | Qld
T_T_MC_ZERO | 6154.0234 | 30000 | 0.5 | 0.16667 | Discretionary 0 MW upper limit on Macintosh generation | Outage | Discretionary | Tas
T>T_NIL_BL_5C | 6121.2085 | 559.5568 | 4.5833 | 1.3333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
V_GANWRSF_ISL_0 | 6108.5025 | 109211.7462 | 0.5 | 8.4167 | Gannawarra Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
CA_SYDS_51A7040E_1 | 6080.4627 | 0 | 0.41667 | 0 | Constraint Automation, O/L 61:LN61:Z:330@CROOKWF@NSW for CTG LNQT on trip of COLLECWF-MARULAN 4 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP4(EMPSYD) | Outage | Thermal | Constraint Automation
Q>NIL_SRMB_M020/1 | 6078.2159 | 130999.4408 | 1.3333 | 10.5833 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
S>>BRDV_RBTU_RBPA | 6056.1217 | 0 | 1.5833 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Robertstown-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N^^V_LTWG_1 | 6038.7247 | 7336.0875 | 2.25 | 3.75 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_7C2K_SMSF_5 | 6024.0939 | 0 | 0.5 | 0 | No limit to Sun Metals Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
T^T_LIPM_1 | 5941.5322 | 13540.375 | 6.3333 | 8 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Voltage Stability | Tas
V^^N_SMF2_1 | 5893.5955 | 0 | 1.9167 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>>N-DTMN_39_16 | 5861.544 | 0 | 1.4167 | 0 | Out = Dapto-Marulan(8), avoid O/L Bannaby to Sydney West (39) on trip of Marulan to Avon (16) line, Feedback | Outage | Thermal | NSW
T_ROCOF_3 | 5834.9215 | 237.4438 | 8.5833 | 0.58333 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
F_T+FARE_N-2_TG_R6_2 | 5743.8334 | 604.7219 | 4.8333 | 3.4167 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS | FCAS
N>>N-NIL_2XN | 5525.8129 | 0 | 0.083333 | 0 | Out=Nil, avoid O/L Collector to Marulan (4) on trip of Yass to Marulan (5) line, Feedback | NIL | Thermal | NSW
F_T+FARE_N-2_RREG | 5375.6777 | 217.8092 | 7.5833 | 1.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | Unit Zero - FCAS | FCAS
S>>RBTU_RBPA_WTTP | 5360.3061 | 19923.4284 | 2.3333 | 2.5833 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
S_IBR_LB_600 | 5306.5848 | 0 | 0.41667 | 0 | Discretionary upper limit of 600 MW for SA non-synchronous generation excluding Lake Bonney 1,2,3 and Canunda | Outage | Discretionary | SA
S>>NIL_RBTU_RBPA | 5172.4286 | 0 | 1.5833 | 0 | Out= Nil, avoid O/L Robertstown-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S_ISLE_LKB1+2+3_40 | 5119.8367 | 0 | 0.33333 | 0 | Discretionary upper limit on Lake Bonney (1+2+3) windfarms<=40 MW & No. in-service wind turbines for LKB at 14 Turbines.(Note otherwise, LKB 2+3 +1 will be constrained to 0 MW) | Outage | Discretionary | SA
N>>V_NIL_0X1_60 | 5043.8828 | 0 | 4.1667 | 0 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL | Thermal | NSW
F_T+CSGO_TG_R5 | 5039.9323 | 562.4021 | 75.4167 | 18.1667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>RBTU_TWPA_TPRS | 5011.8949 | 16504.4514 | 0.5 | 1.3333 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
F_S+TB3_R5_70M | 4999 | 0 | 0.083333 | 0 | Raise 5 min Service Requirement for SA island for loss of Torrens Island B3 for 70 MW metro gen trip option | Outage | FCAS | FCAS
F_T+FASH_N-2_RREG | 4966.3238 | 3376.7454 | 10.3333 | 16.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | Unit Zero - FCAS | FCAS
F_T++NIL_MG_RECL_R60 | 4964.7734 | 6756.6436 | 83.0833 | 70.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
N_WR_57_WT-INV | 4930.7996 | 0 | 0.41667 | 0 | Constraint to violate if White Rock wind/solar farm wind turbine + inverter availability greater than 57. Dispatch only. swamped out otherwise. DS only. | Outage | System Strength | NSW
F_S+TB1_R60_70M | 4902.7981 | 0 | 0.5 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B1 for 70 MW metro gen trip option | Outage | FCAS | FCAS
V::N_NIL_xxx | 4899.8779 | 20352.5606 | 23.8333 | 44.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL | Transient Stability | Vic
F_Q++8C_L5 | 4885.1575 | 4390.3037 | 10.5833 | 13.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage | FCAS | FCAS
S_SNOW_N+S_210 | 4884.0505 | 0 | 0.91667 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 210 MW | Outage | Discretionary | SA
N_MOREESF1_40INV | 4876.4468 | 0 | 0.33333 | 0 | Constraint to violate if Moree Solar Farm inverter availability greater than 40. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
F_S+NBH_TG_R60 | 4857.5873 | 0 | 0.83333 | 0 | Raise 60 sec Service Requirement for SA island for loss of North Brown Hill windfarm to Belalie 275 kV line | Outage | FCAS | FCAS
N>>81_964_82 | 4824.6192 | 0 | 3.25 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage | Thermal | NSW
F_I+ML_L6_0400 | 4779.4291 | 26697.5694 | 1591.6667 | 5952.5 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
F_ESTN+MG_R60 | 4777.2976 | 0 | 87.1667 | 0 | Raise 60 sec Service Requirement for Eastern Generation Event | Outage | FCAS | FCAS
N>>N-DTMN_08 | 4739.2276 | 0 | 0.83333 | 0 | Out = Dapto-Marulan(8), avoid O/L Marulan to Avon (16) on trip of Dapto to Kangaroo Valley (18) line, Feedback | Outage | Thermal | NSW
V::N_HYTR_O2 | 4698.8364 | 0 | 2.75 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
F_S++HYSE_L5 | 4630.1343 | 484.7436 | 30.1667 | 0.83333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage | FCAS | FCAS
Q_STR_7C2K_CLRSF_3 | 4545.0721 | 4990.7646 | 0.41667 | 6.6667 | No limit to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_S+ML_L6_2_LB_0 | 4513.8681 | 0 | 19.25 | 0 | Lower 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage | FCAS | FCAS
F_T+NTH_MG_R5 | 4462.5633 | 0 | 7.3333 | 0 | Raise 5 min requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>NIL_RBTX_RBTX_2 | 4400.5656 | 639.8669 | 0.91667 | 0.33333 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL | Thermal | SA
S>>BWMP_RBTU_RBPA | 4375.1532 | 0 | 1.6667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Robertstown-Para 275kV line on trip of Robertstown -Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N_COLMBSF_60_INV | 4335.2578 | 0 | 0.33333 | 0 | Limit Coleambally Solar Farm upper limit to 0 MW if number of inverter available exceed 60. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
SVML_FLT_150 | 4316.6024 | 4380.8613 | 2.0833 | 8.9167 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
F_I+TTS_TG_R5 | 4298.3472 | 603.1347 | 699.8333 | 89.5 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
V>V_NIL_RADIAL_10 | 4288.0457 | 0 | 0.33333 | 0 | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Thermal | Vic
S_SNOW_N+S_190 | 4208.0391 | 0 | 0.41667 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 190 MW | Outage | Discretionary | SA
S_LB3_0 | 4198.7413 | 252.0501 | 2 | 0.16667 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | Unit Zero | SA
S-LB2_0 | 4183.1257 | 0 | 2 | 0 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | Unit Zero | SA
S_NBH_0 | 4166.1489 | 123213.0345 | 0.41667 | 9.75 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | Unit Zero | SA
F_T+NTH_MG_R60 | 4159.4359 | 0 | 7.3333 | 0 | Raise 60 sec requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
VS_250 | 4136.5407 | 2999.3127 | 3.9167 | 7.9167 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
V^^S_SEVC1_SETB | 4022.835 | 0 | 4.4167 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
T>T_FASH_2_N-2 | 3999.7117 | 134.4468 | 1.1667 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.1 transformer | Outage | Thermal | Tas
F_S+TB3_R60_70M | 3996 | 0 | 0.33333 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B3 for 70 MW metro gen trip option | Outage | FCAS | FCAS
Q_STR_32282_HASF | 3962.0705 | 509630.3352 | 1.3333 | 41.0833 | Limit 50% to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
T>T_FASH_1_N-2 | 3926.3678 | 2616.1803 | 2.9167 | 3.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Thermal | Tas
Q_RRSF1_ZERO | 3923.0904 | 6239.2867 | 1.0833 | 0.5 | Ross River solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
T^V_NIL_11 | 3920.3576 | 17559.7133 | 1.5 | 30.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink harmonic filter, swamped if TVCC in service | NIL | Voltage Stability | Tas
S_LB2WF_CONF | 3913.0209 | 39.8494 | 2.9167 | 0.25 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
NSA_T_GO2_10 | 3892.1326 | 0 | 1.25 | 0 | Gordon unit 2 >= 10 MW for Network Support Agreement | Outage | Network Support | Tas
T>T_HA_TX_2 | 3819.6473 | 0 | 7.4167 | 0 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 110 kV to 220 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Thermal | Tas
V::S_2SE+PAVC_SETB | 3814.6232 | 0 | 6.6667 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S(Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
S-MWPS3-PV_0 | 3733.1051 | 104198.1971 | 2.1667 | 9.9167 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW | Outage | Unit Zero | SA
V::S_BLKRG_MAXG_3 | 3714.4108 | 13.5619 | 2.75 | 0.083333 | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | Outage | Transient Stability | SA
F_MAIN+TTS_TG_R60 | 3673.3009 | 171.1952 | 26.3333 | 3.4167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S_SNOW_N+S_130 | 3656.0463 | 0 | 0.5 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 130 MW | Outage | Discretionary | SA
Q^^N_AR_SVC_1 | 3635.5919 | 8662.9268 | 2 | 22 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
N_GOONSF1_ZERO | 3633.1848 | 1299.9896 | 0.75 | 0.083333 | Goonumbla solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
QNTE_OSCILLATE | 3592.1323 | 101.4323 | 2.9167 | 3.3333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Discretionary | Qld
Q>>CPST_CLWU_BCST | 3584.978 | 101212.3243 | 11.0833 | 33.8333 | Out = 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Stanwell to Bouldercombe 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
T>T_X_LIPM_WACB_A | 3584.9269 | 0 | 4.5 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, with associated 220kV CB at WA O/S, limit southern generators to <= southern load + 15 MW | Outage | Thermal | Tas
S>>BWMP_HUWT_RHBG-T | 3561.9079 | 0 | 0.66667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill-Brinkworth 132kV T line on trip of Hummocks-Waterloo 132kV line, Feedback | Outage | Thermal | SA
F_T+STH_MG_R5 | 3555.3778 | 0 | 9.0833 | 0 | Raise 5 min requirement for a South Tasmania Generation Event | Outage | FCAS | FCAS
N_COLEASF1_FLT_30 | 3537.0395 | 504862.5446 | 0.25 | 40.75 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_GOONSF_11_INV | 3476.1174 | 2093.2196 | 0.5 | 0.16667 | Limit Goonumbla Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
V_BULGANAWF_FLT_40 | 3462.5162 | 459006.1728 | 0.58333 | 40.9167 | Limit Bulgana Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_I+GFT_TG_R5 | 3448.8548 | 2260.6095 | 537.9167 | 265.4167 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
N>Q-TEMU_757_758 | 3434.1763 | 0 | 9.9167 | 0 | Out= 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line, avoid O/L on remaining T174 Terranora to H4 Mudgeeraba line (758 or 757), Feedback | Outage | Thermal | NSW
S>>SETB_TBSE_TBKH2_1 | 3370.3582 | 0 | 0.75 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend-Keith #2 132kV Line on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
V::S_PWSE_MAXG | 3322.8646 | 0 | 5.9167 | 0 | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
S>NIL_NIL_SETX12 | 3298.8053 | 54230.4708 | 0.83333 | 14.5 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | Thermal | SA
N_MOREESF1_ZERO | 3295.59 | 5854.6672 | 0.25 | 0.58333 | Moree Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
T_BLINK_TV_NGZ | 3271.7012 | 3778.5524 | 2 | 4.25 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | Outage | Other | Tas
F_MAIN++GFT_TG_R6 | 3222.1995 | 86.0092 | 52.3333 | 5.9167 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
Q_STR_7C2K_RRSF_1 | 3176.5412 | 0 | 1.4167 | 0 | No limit to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG)or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
V>>SML_NSWRB_11_1 | 3170.0902 | 318.6812 | 0.083333 | 0.16667 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Balranald to Buronga (X3) 220 kV line, feedback | NIL | Thermal | Vic
TV_150 | 3167.1284 | 0 | 3.1667 | 0 | Tas to Vic on Basslink upper limit of 150 MW | Outage | Discretionary | Tas
F_T+FARE_N-2_TG_R6_1 | 3140.5103 | 335.1434 | 3.3333 | 2.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS | FCAS
V>>V_NIL_26 | 3114.4272 | 0 | 0.83333 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
S>>X_RBPA+RBTX2_07 | 3093.7868 | 0 | 4.25 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), Feedback | Outage | Thermal | SA
V^^S_PAVC1_MAXG | 3081.408 | 0.83221 | 2 | 0.083333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
N_BANGOWF2_ZERO | 3074.0746 | 0 | 0.25 | 0 | Bango 999 wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>N-WLWO_B | 3003.7387 | 0 | 0.66667 | 0 | Out = Wellington to Wollar line (79), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Mt_Piper line (72), Feedback | Outage | Thermal | NSW
V::S_PAVC1_SETB | 3003.5211 | 108.559 | 3.3333 | 0.5 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
V_DDWF_SHWF_600 | 2992.2004 | 0 | 0.66667 | 0 | Limit Dundonnell and Stockyard Hill Wind Farms combined upper limit to 600 MW | Outage | Discretionary | Vic
N>N-WLMP_A | 2964.9524 | 0 | 0.25 | 0 | Out = Wellington to Mt_Piper line (72), avoid O/L on Molong to Orange North (94T) on trip of Wellington to Wollar (79), Feedback | Outage | Thermal | NSW
Q_STR_7C2K_CLRSF_5 | 2961.4852 | 0 | 0.25 | 0 | No limit to Clare Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_DAYSF_5 | 2961.4836 | 0 | 0.25 | 0 | No limit to Daydream Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
CA_BRIS_51934522_1 | 2939.2215 | 0 | 0.58333 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG LVK1 on trip of KMTS - RCTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
F_S_DLBAT-G_R6 | 2911.6022 | 85.47 | 18.8333 | 3.4167 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>BRDV_RBTU_WTTP | 2909.8053 | 0 | 0.58333 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>RBTX_BWPA_WTTP | 2863.5634 | 0 | 1.3333 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_BWMP_WTTP | 2818.3299 | 0 | 0.25 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
F_T+GTTE_TL_L6 | 2803.8678 | 0.18 | 116.6667 | 0.5 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_HYTR_O1 | 2790.317 | 0 | 1.4167 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
N_SAPHWF1_56WT | 2786.6801 | 0 | 0.41667 | 0 | Constraint to violate if Sapphire WF turbines On greater than 56. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
F_S++HYSE_L6_2 | 2781.9607 | 206.3564 | 0.33333 | 4.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage | FCAS | FCAS
F_T+CSGO_TG_R60 | 2771.1331 | 1204.1256 | 27.3333 | 18.25 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_HYTR_xxx | 2729.7103 | 0 | 1.25 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
V::S_SEVC1+PWSE_SETB | 2728.8085 | 0 | 3.6667 | 0 | Out= Either one of the South East SVC+Penola West-South East 132kV (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
Q>COLTX | 2710.4158 | 4355.4895 | 0.58333 | 0.33333 | Out = Collinsville North T1 or T2 132/33 kV transformer, limit Collinsville Solar Farm to 33.9MW to prevent overload on RMU of the remaining transformer | Outage | Thermal | Qld
V_KM_TX | 2700.566 | 0 | 0.41667 | 0 | Out =One Kiamal 220/33 kV Transformer, manage continuous rating on remaining transformer | Outage | Thermal | Vic
Q_KSP1_ZERO | 2686.226 | 183661.2895 | 0.83333 | 16.25 | Kidston solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S:V_550_HY_TEST_DYN | 2681.3269 | 6161.6853 | 6.5 | 26.25 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
S>NIL_NWMH1_NWMH2 | 2679.5128 | 212.2442 | 1.5833 | 0.083333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on trip of North West Bend-Monash #1 132kV line, Feedback | NIL | Thermal | SA
N:V_DDSM_BWRG | 2636.7186 | 602.4983 | 0.66667 | 0.083333 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage | Transient Stability | NSW
Q_KEP-HYB_11MW | 2633.763 | 0 | 2.3333 | 0 | Kennedy Energy Park upper limit of 11MW | Outage | Discretionary | Qld
S>>BRTX3_RBTU_WTTP | 2631.9413 | 0 | 0.5 | 0 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
Q_STR_32282_WHTSF | 2624.8975 | 0 | 1.1667 | 0 | Limit 50% to Whitsunday SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_T+STH_LREG | 2613.0366 | 0 | 9.0833 | 0 | Lower Regulation requirement for Southern Tasmania | Outage | FCAS | FCAS
F_ESTN+ML_L6_0400 | 2600.3325 | 0 | 141.5833 | 0 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS | FCAS
V_COHUNASF_FLT_17 | 2576.282 | 0 | 0.75 | 0 | Limit Cohuna Solar Farm upper limit to 17 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_WAGGNSF1_ZERO | 2572.4802 | 0 | 0.25 | 0 | Wagga North solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_WR_30_WT-INV | 2555.4082 | 674.4556 | 0.33333 | 0.25 | Constraint to violate if White Rock wind/solar farm wind turbine + inverter availability greater than 30. Dispatch only. swamped out otherwise. DS only. | Outage | System Strength | NSW
N^^Q_TW_330_BUS1_B1 | 2540.2118 | 455364.3546 | 4.3333 | 35.9167 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
V::S_NIL_TBSE_1 | 2468.3893 | 321.8602 | 2.9167 | 0.75 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | Transient Stability | SA
F_ESTN+GFT_TG_R6 | 2456.2224 | 0 | 12.3333 | 0 | Raise 6 sec requirement for a Eastern Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | Outage | FCAS | FCAS
N::V_DDSM_UTMS | 2448.0937 | 0 | 0.41667 | 0 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit for trip of Upper Tumut - Murray (65) line | Outage | Transient Stability | NSW
T_MRWF_ZERO | 2422.8745 | 3720.1224 | 0.5 | 1 | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Unit Zero | Tas
Q_STR_7C8C_CLRSF | 2414.3223 | 76686.9059 | 2.6667 | 15.25 | Limit Clare SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_MAIN++TTS_TG_R60 | 2359.1855 | 215.9586 | 70.25 | 7.4167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_MAIN+ML_L6_0400 | 2340.2399 | 6948.8211 | 154.5833 | 237 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
Q_STR_7C2K_KIDSF_1 | 2330.1951 | 0 | 1.5833 | 0 | No limit to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
N_FINLYSF_FLT_30 | 2300.8687 | 433252.713 | 0.66667 | 34.6667 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_ESTN+TTS_TG_R6 | 2259.1001 | 0 | 17.9167 | 0 | Raise 6 sec requirement for a Eastern Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | Outage | FCAS | FCAS
N>>X-17+76_39_11 | 2240.5466 | 0 | 0.91667 | 0 | Out= Avon to Macarthur (17) and Sydney South to Wallerawang (76), avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage | Thermal | NSW
T>T_NIL_BL_3C | 2229.135 | 987.7957 | 2.1667 | 1.9167 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
V^^S_NIL_MAXG_xxx | 2219.8773 | 0 | 1.4167 | 0 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Voltage Stability | SA
S>>PARB_RBTU_RBMWP4 | 2170.9552 | 271.0556 | 1.25 | 0.083333 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N_GNNDHSF1_ZERO | 2138.4317 | 2070.5918 | 0.16667 | 0.16667 | Gunnedah solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q>>BCRG_BCCP_CLWU | 2133.0978 | 0 | 2.3333 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
F_S_DLBAT-G_R60 | 2130.0857 | 136.0579 | 18.9167 | 3.4167 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T+GTTE_TL_L60 | 2112.9849 | 1.08 | 112.4167 | 0.5 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
Q_STR_7C2K_DAYSF_2 | 2013.828 | 13720.5231 | 0.16667 | 1.0833 | Limit 80% to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
T_GO_300 | 1998.8176 | 777.7333 | 2 | 0.58333 | Discretionary 300 MW upper limit on total Gordon generation | Outage | Discretionary | Tas
F_QNV+LREG_0210 | 1996.2525 | 0 | 4.1667 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T>T_NWSD_110_1 | 1993.1867 | 0 | 0.66667 | 0 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752, avoid O/L Scottsdale Tee to Norwood 110kV line on Nil trip, Feedback | Outage | Thermal | Tas
Q_STR_32282_CLRSF | 1984.7314 | 0 | 1.25 | 0 | Limit 50% to Clare SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_1 | 1961.0429 | 0 | 1.1667 | 0 | No limit to Whitsunday Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG)or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_SMSF_1 | 1950.6717 | 0 | 1 | 0 | No limit to Sun Metals Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG)or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
N>N-X_MOON_WLTX_A | 1922.851 | 0 | 1.5833 | 0 | Out= 94T (Molong to Orange North) 132kV line and one of the Wellington 132/330kV Transformers, avoid O/L Molong to Wellington (945) on trip of Wellington Suntop Tee to Wellington 94K/1 132kV line, Feedback. 94K/1Metering at Wellington end | Outage | Thermal | NSW
N^^V_CNLT_1 | 1897.3568 | 0 | 5.25 | 0 | Out = Canberra - Lower Tumut (07) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N^^V_X_SMF2_SMSC_1 | 1882.4942 | 0 | 1.6667 | 0 | Out = South Morang F2 500/330kV txfmr and both South Morang Series Capacitors, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N^^V_MLNK_1 | 1874.6589 | 0 | 2.4167 | 0 | Out = Murraylink, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_MAIN+GFT_TG_R5 | 1856.9405 | 108.277 | 111.9167 | 8 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
T_FASH_MAXGEN_1 | 1846.6927 | 18149.395 | 1.25 | 22.75 | Upper limit on Mackintosh + Bastyan + John Butters with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Other | Tas
T>T_X_LIPM_TWO_E | 1821.2437 | 0 | 1.0833 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, both lines must be open at least at Palmerston, avoid O/L Tungatinah to Meadowbank Tee 2 on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
F_T++NIL_MG_R60 | 1819.2865 | 6661.4977 | 30.3333 | 34.6667 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
Q_KEP-HYB_27MW | 1803.6098 | 0 | 1 | 0 | Kennedy Energy Park upper limit of 27MW | Outage | Discretionary | Qld
S>>X_RBPA+RBTX2_13 | 1795.7497 | 0 | 0.083333 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Templers-Roseworthy 132 kV on trip of Templers West-Para 275 kV line, Feedback | Outage | Thermal | SA
N>>V_NIL_66_65 | 1774.5976 | 0 | 0.33333 | 0 | Out = Nil, avoid Lower Tumut to Murray(66) using 15 mins rating O/L on Upper Tumut to Murray(65) trip; (Note: Swamped when TL 64 is O/S) | NIL | Thermal | NSW
Q_KEP-HYB_01MW | 1771.1218 | 0 | 3.4167 | 0 | Kennedy Energy Park upper limit of 1MW | Outage | Discretionary | Qld
Q-X_STR_7C8C_KEP | 1769.75 | 0 | 0.33333 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Kennedy Energy park output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
V::N_ROSM_O2 | 1748.5978 | 0 | 1.25 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
QNI_SOUTH_1150_DYN | 1693.8708 | 1936.6596 | 0.83333 | 1.6667 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Transient Stability | Qld
V_BRYBWF_ZERO | 1693.3997 | 630.8505 | 0.41667 | 0.33333 | Berrybank Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V^^S_SEVC1_MAXG | 1677.1121 | 0 | 0.75 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V^^S_2SE+PAVC_MAXG | 1669.1153 | 0 | 1.9167 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V_KIAMAL_SC_0 | 1661.3108 | 0 | 0.16667 | 0 | Out = Nil, Limit Kiamal solar farm to 0 MW when Kiamal Syncon is out of service. DS only. Swamp out if Kiamal Syncon is in service | NIL | Discretionary | Vic
N^^V_DPWG_X5_RVYS_1 | 1649.5069 | 0 | 1.1667 | 0 | Out = Darlington Point to Wagga with line X5 open and Ravine to Yass (2+63) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_T++NIL_WF_TG_R60 | 1646.3629 | 3802.4751 | 29.8333 | 56.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_QNV++GFT_TG_R6 | 1646.3525 | 0 | 6.1667 | 0 | Raise 6 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
Q_STR_32282_HAYSF | 1633.7826 | 0 | 1.0833 | 0 | Limit 50% to Hayman SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_T++NIL_MG_R5 | 1632.1514 | 12797.291 | 59.4167 | 41.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_QNV++LREG_0210 | 1630.3492 | 0 | 5.6667 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage | FCAS | FCAS
N>N-GITN_TE_C1 | 1624.2066 | 431.0752 | 3.4167 | 3.1667 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
V::S_SEVC1_SETB | 1618.415 | 0 | 1.25 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
F_QNV++ML_L6_0400 | 1611.099 | 0 | 27.0833 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS | FCAS
I_CTRL_ISSUE_TE | 1605.6657 | 81.9072 | 6 | 2.3333 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
N^^V_DPWG_X5_1 | 1597.5124 | 978.9133 | 2.3333 | 4.0833 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V::S_SETB_MAXG | 1575.6409 | 0 | 1 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with one Black Range series capacitors I/S). | Outage | Transient Stability | SA
Q_NIL_STRGTH_MEWF | 1526.0049 | 683834.4755 | 0.083333 | 37.0833 | Out = Nil, limit Mt Emerald wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_DAYSF | 1526.0035 | 390925.0697 | 0.083333 | 12.1667 | Out = Nil, limit Daydream solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_RUGSF | 1526.0033 | 0 | 0.083333 | 0 | Out = Nil, limit Rugby run solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_COLSF | 1526.0032 | 424045.9216 | 0.083333 | 14.8333 | Out = Nil, limit Collinsville solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
S>>MKRB_BWPA_BRTW | 1521.777 | 0 | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
N>>V_SMDD3 | 1510.6454 | 0 | 0.58333 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the Eildon to Thomastown 220 kV line (flow to South) on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
Q>N-MUTE_757 | 1483.2135 | 0 | 9.0833 | 0 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
V_KIAMSF_DYN | 1481.5497 | 0 | 0.33333 | 0 | Out = Kiamal Syncon, Limit Kiamal solar farm to 100 MW when Murra Warra 2 WF syncon I/S. Limit Kiamal solar farm to 50 MW when Murra Warra 2 WF syncon O/S | Outage | Discretionary | Vic
N>>N-NIL_64 | 1465.648 | 47.0305 | 0.25 | 0.58333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | Thermal | NSW
F_Q++LDTW_R60 | 1463.4603 | 2425211.2442 | 2.3333 | 102.5 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_MAIN++94_96_TL_L60 | 1430.6146 | 0 | 15.0833 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink able transfer FCAS | Outage | FCAS | FCAS
Q_STR_32282_RRSF | 1416.2127 | 0 | 0.91667 | 0 | Limit 50% to Ross River SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
N::Q_LDNC_TNT | 1415.2231 | 0 | 2.75 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage | Transient Stability | NSW
SV_240_DYN | 1399.3242 | 0 | 0.66667 | 0 | SA to Victoria on Heywood upper transfer limit of 240 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
Q-X_STR_7C8C_CLRSF | 1393.5457 | 0 | 0.41667 | 0 | Out=One or more 275KV Fdrs in NQLD, limit Clare Solar farm output depends on the number units online in Stanwell, Callide, Gladstone and Kareeya generators, Haughton Syncon and NQLD demand, Zero if it does not meet minimum requirement | Outage | System Strength | Qld
F_QNV+MG_R60 | 1388.5327 | 0 | 3.5 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_X_SMSC_V | 1381.9815 | 0 | 6.8333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage | Transient Stability | Vic
F_S_DLBAT-L_L60 | 1345.3308 | 1137.7718 | 18.9167 | 3.3333 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q_STR_32282_KIDSF | 1345.3126 | 0 | 1.0833 | 0 | Limit 50% to Kidston SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
T_FARC1 | 1329.4793 | 0 | 0.083333 | 0 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
V::N_ROSM_O1 | 1329.1353 | 0 | 1.1667 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
S>LFTI_PPPW_LFTX4 | 1299.4391 | 10565.3791 | 0.083333 | 0.83333 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX4 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Thermal | SA
N_MOREESF1_040 | 1293.2797 | 0 | 0.083333 | 0 | Moree Solar Farm upper limit of 40 MW | Outage | System Strength | NSW
N::N_CNSD_2 | 1281.9885 | 1688.2748 | 2.25 | 1.4167 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
Q_CHCR | 1268.3391 | 0 | 1 | 0 | Out = Charters Towers to Cape River 66kV line, limit Kennedy Energy Park to 11MW | Outage | Unit Zero | Qld
S>>BWMP_DVBR_BGTX2 | 1265.013 | 0 | 1.1667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Bungama 275/132kV (TX2) on trip of Davenport-Brinkworth 275 kV line, Feedback | Outage | Thermal | SA
F_T+CSGO_TG_R6_1 | 1264.8866 | 256.2599 | 5.3333 | 4.5 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS | FCAS
N>>V_SMDD6 | 1240.5915 | 1869.1197 | 1.4167 | 5.6667 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
V::N_JNWG_xxx | 1233.6945 | 0 | 1.5833 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_HWCB_xxx | 1194.3794 | 241.4411 | 0.16667 | 0.41667 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
CA_SYDS_525B969A_1 | 1186.9743 | 0 | 3.75 | 0 | Constraint Automation, O/L NN_CR:LCRK:Z:110@N_NRFOLK@TAS for CTG LTBG on trip of CHAPEL ST_NEW NORFOLK 110KV LINE. Generated by STNET[BNECR3] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
F_T+FASH_N-2_TG_R6_2 | 1184.3617 | 2394.2372 | 0.58333 | 8.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS | FCAS
S>>V_MOTB_TUTB_CGTB | 1171.1414 | 0 | 0.58333 | 0 | Out=Mobilong - Tailem Bend 132kV line; avoid O/L Cherry Gardens -Tailem Bend 275kV on trip Tungkillo -Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
S:V_550_HY_TEST | 1170.5179 | 17926.0538 | 3.6667 | 17.75 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
T_REECE1_100 | 1169.9654 | 0 | 6.75 | 0 | Discretionary 100 MW upper limit on Reece unit 1 | Outage | Discretionary | Tas
S>>X_RBTX1_WTHU_02 | 1155.1373 | 0 | 0.16667 | 0 | Out= Robertstown 132/275kV TX1 + Waterloo-Hummocks 132kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
N^^V_SMTXF2_1 | 1143.3133 | 1306.9925 | 2.5 | 0.83333 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N>WLTX_94T_WLTX | 1135.1008 | 0 | 0.25 | 0 | Out= one of the Wellington 132/330kV Transformers, avoid O/L on Molong to Orange North (94T) on trip of remaining Wellington 132/330kV transformer, Feedback | Outage | Thermal | NSW
S>NIL_PL_GENMAX_YDMD | 1125.9306 | 0 | 2.5833 | 0 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | Thermal | SA
S-MAPS2-PV_0 | 1115.6693 | 0 | 0.33333 | 0 | Discretionary upper limit for SA WATER Mannum Adelaide Pumping Station No 2 PV (Palmer) generation of 0 MW | Outage | Unit Zero | SA
V>>V_ROTS_TX_2A_R | 1103.4844 | 0 | 1.5833 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Thermal | Vic
S::V_TBSE_TBSE_2 | 1102.8311 | 69225.0629 | 1.0833 | 11.4167 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
Q_CRCRE_6383 | 1102.5912 | 0 | 0.66667 | 0 | Out = Cape River to Cape River East 66kV line, limit Kennedy Energy Park to 0MW | Outage | Unit Zero | Qld
N::Q_LDNC_KC | 1094.5604 | 0 | 1.4167 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
N^^V_CNYS_1 | 1090.7012 | 0 | 1.9167 | 0 | Out = Canberra - Yass (9), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>V_460_DYN | 1073.722 | 0 | 1.5 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | SA
Q_STR_7C2K_KIDSF_2 | 1058.8358 | 71714.3614 | 0.16667 | 5.9167 | Limit 80% to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S>BRTW_BWMP_STHU | 1049.2733 | 0 | 0.58333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Snowtown T - Hummocks 132kV line on trip of Blyth West- Munno Para 275kV line, Feedback | Outage | Thermal | SA
VSML_110 | 1047.7027 | 0 | 1.6667 | 0 | Vic to SA on ML upper transfer limit of 110 MW | Outage | Discretionary | Vic
Q_STR_7C2K_HAMSF_5 | 1045.4952 | 0 | 0.25 | 0 | No limit to Hamilton Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_T++NIL_WF_TG_R6 | 1036.5455 | 6093.6326 | 12.6667 | 50.3333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
Q>COL_CBEB05Q00 | 1031.0008 | 0 | 0.083333 | 0 | Out = Collinsville North 33kV bus coupler CB EB05Q00, limit Collinsville Solar Farm to 33.9 MW to prevent overload on RMU of no 1 transformer | Outage | Thermal | Qld
T>T_LIPM_110_2B | 1025.7351 | 0 | 1.6667 | 0 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
S_BF_0 | 1009.7151 | 0 | 0.083333 | 0 | Discretionary upper limit for Bluff Windfarm generation of 0 MW | Outage | Unit Zero | SA
Q>>NIL_STCP_RGLC | 1001.3583 | 2442.2762 | 3 | 1.5 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Stanwell to Calliope River (848+812) line, Feedback | NIL | Thermal | Qld
F_S+OD_TL_L6_2_LB_0 | 999 | 0 | 0.083333 | 0 | Lower 6 sec Service Requirement for SA island for loss of Olympic Dam (FFR ZERO) | Outage | FCAS | FCAS
F_QNV+RREG_0220 | 960.7303 | 0 | 1.25 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_S+NBH_TG_R5 | 956.8399 | 0 | 0.58333 | 0 | Raise 5 min Service Requirement for SA island for loss of North Brown Hill windfarm to Belalie 275 kV line | Outage | FCAS | FCAS
S>>TPRS_RBPA_RBTU | 956.567 | 0 | 0.33333 | 0 | Out= Templers-Roseworthy 132kV line, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
F_I+ML_L6_APD | 953.3375 | 432.7765 | 28.0833 | 102.9167 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
V::N_SMF2_O1 | 933.4024 | 0 | 0.91667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
QN_1200_DYN_TEST | 889.1208 | 0 | 3.1667 | 0 | QLD to NSW on QNI upper transfer limit of 1200 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage | Transient Stability | Qld
N::V_DTKV_MSDD | 882.4245 | 0 | 0.58333 | 0 | Out=Dapto - Kangaroo Valley (18), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
F_MAIN+ST2_ML_L5 | 881.5205 | 0 | 6.9167 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ML_L6_APD | 877.9991 | 52.49 | 24.3333 | 1.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS | FCAS
Q>>X_CLWU+BCST_2 | 863.4314 | 0 | 0.58333 | 0 | Out= 871 (H24 Calvale to H40 Wurdong) 275kV line and 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line, avoid O/L remaining 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line on trip of 8811 (Calvale to Halys) line, Feedback | Outage | Thermal | Qld
F_MAIN++NIL_BL_L6 | 844.6895 | 8969.6091 | 33.4167 | 149.75 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
Q>ISTX | 842.668 | 0 | 0.33333 | 0 | Out = Isis T2 132/66 kV transformer, limit Childers Solar Farm to 46MW to prevent overload on remaining transformer | Outage | Thermal | Qld
F_QNV++TTS_TG_R60 | 838.4645 | 0 | 6.4167 | 0 | Raise 60 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>>NIL_TBCG_TBTU_1 | 817.3915 | 0 | 0.58333 | 0 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | Thermal | SA
N>>NIL_4 | 816.0391 | 6542.7552 | 0.5 | 2.0833 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL | Thermal | NSW
F_MAIN++GFT_TG_R5 | 815.8731 | 671.8792 | 87.6667 | 39.8333 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V::N_SMF2_O2 | 814.528 | 0 | 0.66667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
N>N-9GM_9GL_NIL | 802.2645 | 0 | 0.083333 | 0 | Out= Bango999 WF to Yass 132kV line(9GM), avoid O/L Bango973 to Yass (9GL) on trip of Nil, Feedback | NIL | Thermal | NSW
V^^S_PAVC1_SETB | 760.3296 | 0 | 1.9167 | 0 | Out= Para one SVC(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
N^^Q_LS_SVC_KPP_1 | 743.6296 | 0 | 1.1667 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage | Voltage Stability | NSW
S^CNRB_SA_NORTH | 729.7725 | 0 | 0.58333 | 0 | Out = Canowie-Robertstown 275kV line, Manage voltage collapse in northern SA for the trip of one 275kV line between Davenport-Para or Davenport-Tungkillo. | Outage | Voltage Stability | SA
S>>PARB_TWPA_TPRS | 716.7741 | 0 | 0.33333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
F_Q++8E_R60 | 700.443 | 3.9588 | 1.1667 | 0.16667 | Out = Sapphire to Armidale (8E) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_ESTN+MG_R5 | 700.3362 | 0 | 100.3333 | 0 | Raise 5 min Service Requirement for Eastern Generation Event | Outage | FCAS | FCAS
V>>N-LTUT_G | 698.2539 | 0 | 2.3333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage | Thermal | Vic
SV_240 | 689.2502 | 0 | 0.5 | 0 | SA to Victoria on VicSA upper transfer limit of 240 MW | Outage | Discretionary | SA
F_QNV+DYN_LREG | 681.5288 | 0 | 1.5833 | 0 | Qld, NSW and Vic Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | Outage | FCAS | FCAS
F_T++NIL_WF_TG_R5 | 678.7516 | 4138.1551 | 41.1667 | 84.1667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_ESTN+TTS_TG_R60 | 667.3033 | 0 | 18.9167 | 0 | Raise 60 sec requirement for a Eastern Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | Outage | FCAS | FCAS
S>>CNRB_BWPA_BGTX | 655.0103 | 0 | 1.3333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Bungama 275/132kV (TX2) on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_T+GO_C752_TG_R6 | 640.6353 | 0 | 1.0833 | 0 | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
Q>>CPST_LCCP_CLWU | 638.9943 | 22447.4907 | 0.83333 | 2.3333 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage | Thermal | Qld
Q_NIL_STRGTH_KEP | 619.55 | 0 | 0.083333 | 0 | Out = Nil, limit Kennedy energy park output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N::N_GRYS_2 | 604.6273 | 0 | 1.1667 | 0 | Out = Gullen Range to Yass (3J), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
V>>N_051_66_65_R | 594.2216 | 0 | 1.5 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line,(Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage | Thermal | Vic
T_V_NIL_FCSPS | 589.3048 | 1941.3167 | 0.5 | 1 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Other | Tas
Q>>NIL_BCCP_LCCP | 587.5698 | 0 | 0.75 | 0 | Out= Nil, avoid O/L Larcom Creek to Calliope River (8859) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
T>T_LIPM_110_2A | 565.3955 | 763.5422 | 0.5 | 0.75 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
F_MAIN++ML_L6_APD_LD | 560.611 | 134.8281 | 32.1667 | 32.0833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_S_DLBAT-L_L6 | 554.872 | 73.3866 | 15.4167 | 3.3333 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN+GFT_TG_R60 | 554.7424 | 0 | 13.9167 | 0 | Raise 60 sec requirement for a Eastern Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | Outage | FCAS | FCAS
S^NIL_MTM_VCS_STATUS | 541.787 | 0 | 0.91667 | 0 | Out= Nil, upper limit for Mt Millar WF based on Mt Millar Voltage Control System (VCS) availability, (Note: MTM <=16 MW when VCS OFF; MTM<= 70 MW when VCS ON) | NIL | Voltage Stability | SA
F_MAIN+ST2_ML_L6 | 540.2976 | 0 | 6.9167 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
Q_WOOLGSF1_ZERO | 539.3468 | 0 | 0.91667 | 0 | Woolooga Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
V>>N-LTMS_1 | 535.1614 | 279.6433 | 1 | 2.0833 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage | Thermal | Vic
N^^V_MLNK_ARWBBA | 535.1539 | 0 | 1.3333 | 0 | Out = Murraylink, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | Outage | Voltage Stability | NSW
N_SHPUMP_ZERO_E | 534.11 | 0 | 0.083333 | 0 | Direction to zero for Shoalhaven Pump for Dispatch and Predispatch and NOT PASA | Outage | Other | NSW
F_QNV++RREG_0220 | 531.5912 | 0 | 2.9167 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink able transfer FCAS | Outage | FCAS | FCAS
VT_050 | 530.9858 | 0 | 0.66667 | 0 | Vic to Tas on Basslink upper limit of 50 MW | Outage | Discretionary | Vic
V^^N_LTYS_MNYS_1 | 529.1002 | 0 | 0.33333 | 0 | Out = 3 (Lower Tumut to Yass) 330kV line and 5 (Marulan to Yass) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_N_LD01_RREG | 520.1778 | 0 | 0.41667 | 0 | Out= NIL, Liddell 1 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_LD04_RREG | 520.1778 | 0 | 0.41667 | 0 | Out= NIL, Liddell 4 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++ML_L6_APD | 517.9621 | 92.3545 | 20.1667 | 10.4167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_T+NTH_LREG | 503.53 | 0 | 2.9167 | 0 | Lower Regulation requirement for Northern Tasmania, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_N_LD02_RREG | 488.1878 | 0 | 0.33333 | 0 | Out= NIL, Liddell 2 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V::S_SETB_MG_PPGT2 | 484.4643 | 0 | 0.41667 | 0 | Out= one South East -Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT2 + DPV trip) in SA (SE Cap Available). (NOTE: with one Black Range series capacitors I/S. Co-optimised eq PPGT2 LHS | Outage | Transient Stability | SA
F_T++NIL_ML_L60 | 477.7059 | 4785.5397 | 33.6667 | 344.5 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
N_METZSF_ZERO | 476.7512 | 0 | 0.16667 | 0 | Metz Solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
S>>V_NIL_NIL_RBMW3 | 476.547 | 2214.0401 | 0.5 | 1.4167 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
Q_STR_32282_SMSF | 474.4328 | 1172.0722 | 0.41667 | 1.9167 | Limit 50% to Sun Metals SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Strathmore SVC IS. Zero otherwise. | Outage | System Strength | Qld
F_QNV+TTS_TG_R60 | 471.1024 | 0 | 0.58333 | 0 | Raise 60 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>>SML_NIL_7B | 454.6006 | 0 | 0.16667 | 0 | Out = Nil, avoid O/L Buangor to Ararat 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL | Thermal | Vic
N>>V_DBUSS_4 | 452.2833 | 0 | 0.083333 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage | Thermal | NSW
F_MAIN++TTS_TG_R5 | 449.0555 | 15.0405 | 27.8333 | 1.9167 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
Q>CPWO1_CPWU_CPWO2 | 441.445 | 0 | 0.41667 | 0 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Wurdong (818) on trip of Calliope River to Woolooga (814) line, Feedback | Outage | Thermal | Qld
F_QNV+ML_L6_0400 | 439.993 | 0 | 4.1667 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_I+94_96_TL_L5 | 433.2 | 0 | 22.25 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load | Outage | FCAS | FCAS
V::N_LTWG_xxx | 431.2204 | 4938.647 | 1.8333 | 15.4167 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
S>V_460 | 430.4155 | 0 | 0.91667 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage | Thermal | SA
CA_BRIS_52155A1A_2 | 428.2818 | 0 | 0.41667 | 0 | Constraint Automation, O/L ELTS_MLTS_220:LMLT:Z:220@ELTS@VIC for CTG LVAI on trip of BATS-MLTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
F_T+NTH_WF_TG_R60 | 416.59 | 0 | 1.75 | 0 | Raise 60 sec requirement for North Tasmania for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++94_96_TL_L5 | 416.2521 | 0 | 7.6667 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+TTS_TG_R6 | 414.1223 | 0 | 5.9167 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_Q++8E_R6 | 408.0811 | 2.8439 | 1.1667 | 0.16667 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_I+ML_L6_APD_LD | 398.4676 | 147.999 | 11.5 | 97.0833 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS | FCAS
Q_STR_7C2K_KEP_3 | 396.0634 | 0 | 0.083333 | 0 | No limit to Kennedy Energy Park if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_Q++8E_L5 | 390.8095 | 2817.0114 | 1.5833 | 9.9167 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_I+TL_L5_0700 | 388.71 | 0 | 6.1667 | 0 | Lower 5 min Service Requirement for a NEM Network Event, TL = 700 | Outage | FCAS | FCAS
F_I+94_96_TL_L6 | 388.6895 | 0 | 22.5833 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load | Outage | FCAS | FCAS
F_T+STH_MG_R60 | 373.1181 | 0 | 9.0833 | 0 | Raise 60 sec requirement for a South Tasmania Generation Event | Outage | FCAS | FCAS
F_T+STH_ML_L6 | 366.55 | 0 | 7.5833 | 0 | Lower 6 sec requirement for a South Tasmania Load Event | Outage | FCAS | FCAS
F_I+94_96_TL_L60 | 363.0068 | 0 | 22.5833 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load | Outage | FCAS | FCAS
CA_BRIS_51201D29_1 | 356.4656 | 0 | 0.16667 | 0 | Constraint Automation, O/L 0X1:L0X1:I:220@BURONGA@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORVM1] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_MAIN++94_96_TL_L6 | 346.4966 | 0 | 10.25 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink able transfer FCAS | Outage | FCAS | FCAS
F_N_BW04_RREG | 334.4502 | 0 | 0.58333 | 0 | Out= NIL, Bayswater 4 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++CSGO_TG_R60 | 331.201 | 65.9599 | 6.75 | 0.16667 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
S>NIL_PL_GENMAX | 331.0092 | 0 | 0.083333 | 0 | Out = Nil, Maximum generation at Port Lincoln Due to Port Lincoln-Yadnarie line rating. | NIL | Thermal | SA
F_MAIN+ST2_ML_L60 | 330.897 | 0 | 6.9167 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>TBTU_CGTB_MOTB | 323.4555 | 0 | 2.25 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of Cherry Gardens-Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
N_METZSF_40INV | 320.2437 | 0 | 0.083333 | 0 | Constraint to violate if Metz Solar Farm inverter availability greater than 40. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
F_T+NTH_WF_TG_R5 | 315 | 0 | 1.75 | 0 | Raise 5 min requirement for North Tasmania for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
CA_BRIS_5120191F_1 | 306.5465 | 0 | 0.16667 | 0 | Constraint Automation, O/L 0X1:L0X1:I:220@BURONGA@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORVM1] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
N_WRSF1_ZERO | 302.7118 | 0 | 0.083333 | 0 | White Rock solar farm upper limit of 0 MW and all inverters disconnected | Outage | Unit Zero | NSW
Q>>NIL_LCCP_BCCP | 300.5116 | 0 | 0.5 | 0 | Out= Nil, avoid O/L Bouldercombe to Calliope River (812) on trip of Larcom Creek to Calliope River (8859) line, Feedback | NIL | Thermal | Qld
F_Q++BCDM_L5 | 297.3008 | 10200.1978 | 1.3333 | 34.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_S+SA_ISLE_LB_R6_1 | 290.1175 | 0 | 62 | 0 | Raise 6 sec Service Requirement for SA island | Outage | FCAS | FCAS
T>T_NIL_BL_110_8_1 | 287.9863 | 33.6479 | 0.33333 | 0.083333 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Thermal | Tas
S-WP_0 | 286.7313 | 0 | 0.083333 | 0 | Discretionary upper limit for Wattle Point windfarm generation of 0 MW | Outage | Unit Zero | SA
N^N_KKLS_1 | 272.1603 | 1116.2019 | 1.4167 | 14.5 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
F_T+STH_ML_L60 | 269.35 | 0 | 8.1667 | 0 | Lower 60 sec requirement for a South Tasmania Load Event | Outage | FCAS | FCAS
V>>V_NIL_14 | 267.7091 | 335628.5433 | 0.25 | 39.75 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
F_N_BW01_RREG | 267.3578 | 0 | 0.58333 | 0 | Out= NIL, Bayswater 1 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T+MINS_L6 | 265.6862 | 0 | 11.1667 | 0 | Out = Credible TAS Nth-Sth separation risk, minimum fraction of overall TAS L6 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
F_I+TL_L60_0700 | 258.1744 | 0 | 6.75 | 0 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 700 | Outage | FCAS | FCAS
V::N_DDMB_xxx | 258.0914 | 1041.1558 | 0.16667 | 4.0833 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q_NIL_STRGTH_SSNRV | 255.4602 | 0 | 0.16667 | 0 | Limit Susan River SF to 25 inverters on trip of Maryborough 66kV CB E352. (managed by Ergon Fast Tripping scheme by tripping inverter strings in less than 200ms when CB E352 trips) | NIL | System Strength | Qld
Q::N_ARSVC_AR_2L-G | 248.5635 | 851.4563 | 0.33333 | 3.5 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
N_WALGR_BAT_L_ZERO | 245.1662 | 0 | 0.25 | 0 | Wallgrove Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | NSW
F_T++NTH_LREG | 244.28 | 0 | 1.4167 | 0 | Lower Regulation requirement for Northern Tasmania, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T++NIL_ML_L6 | 242.9106 | 872.7038 | 47.4167 | 135.9167 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
F_N_ER02_RREG | 239.3578 | 0 | 0.58333 | 0 | Out= NIL, Eraring 2 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_ER03_RREG | 239.3578 | 0 | 0.58333 | 0 | Out= NIL, Eraring 3 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_ER04_RREG | 239.3578 | 0 | 0.58333 | 0 | Out= NIL, Eraring 4 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+94_96_TL_L60 | 239.118 | 0 | 0.58333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink unable transfer FCAS | Outage | FCAS | FCAS
N^^V_JNWG_63_X5_1 | 238.6665 | 0 | 0.75 | 0 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_MAIN++TTS_TG_R6 | 237.933 | 0 | 18.3333 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
S>>BWMP_BGBR_HUWT | 235.8477 | 9814.3336 | 0.16667 | 0.83333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | Thermal | SA
S>>DVBL_TWPA_TPRS | 233.0667 | 0 | 0.16667 | 0 | Out= Davenport-Belalie 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
T>>T_NIL_BL_EXP_6E | 225.5389 | 0 | 0.16667 | 0 | Out = Nil, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
F_T++NIL_ML_L5 | 224.28 | 5.64 | 11.5 | 2 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
V>>S_MOTB_TBCG_TBTU | 221.355 | 0 | 1.4167 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
F_MAIN+TTS_TG_R5 | 218.2273 | 8.7409 | 26.4167 | 2.75 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V::V_1900 | 217.7356 | 346.2501 | 0.25 | 0.33333 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
Q_STR_7C2K_KEP_5 | 213.4718 | 0 | 0.25 | 0 | No limit to Kennedy Energy Park if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
T:T_LIPM_1 | 213.2373 | 4016.2225 | 0.5 | 5 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South). Swamp if no Gordon units online. | Outage | Transient Stability | Tas
F_S_LG1_L60 | 208.72 | 0 | 2.5 | 0 | Out= NIL, Ladbroke Grove Unit1 L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
Q_STR_7C2K_RRSF_5 | 201.4719 | 0 | 0.25 | 0 | No limit to Ross River Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_Q++NIL_R60 | 201.334 | 0 | 0.16667 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
T_T_TI_GH_RC12_250 | 192.2968 | 114317.9809 | 0.16667 | 29.3333 | Discretionary 250 MW upper limit on Tribute, Granville Harbour, Reece 1 and 2 generation | Outage | Discretionary | Tas
T>>T_NIL_BL_EXP_5F | 191.6069 | 0 | 0.25 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
N>>964_88_84_S | 191.0389 | 0 | 0.5 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage | Thermal | NSW
F_S_DLBAT-L_L5 | 189.76 | 310.0303 | 15 | 3.3333 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V>>N-LTMS_4 | 189.3482 | 0 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L(15m rating) on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Thermal | Vic
F_T+FARE_N-2_TG_R60 | 189.2568 | 27.91 | 3.5 | 0.58333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_S_LG2_L5 | 187.2907 | 0 | 1.4167 | 0 | Out= NIL, Ladbroke Grove Unit2 L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V_MOORBWF_FLT_150 | 185.1374 | 0 | 1.1667 | 0 | Limit Moorabool Wind Farm upper limit to 150 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
T>T_NIL_BL_IMP_1B | 180.168 | 0 | 0.58333 | 0 | Out = Nil, avoid O/L either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line with no SPS action, feedback | NIL | Thermal | Tas
Q>>BCST_BCST_STBS | 179.8277 | 0 | 0.91667 | 0 | Out = 848 or 849 (H29 Stanwell to H10 Bouldercombe 275 kV line), avoid O/L the remaining 848 or 849(H29 Stanwell to H10 Bouldercombe 275 kV line) on trip of Stanwell to Broadsound (8331) line with 7114/1 open post contingent or pre contingent. Feedback | Outage | Thermal | Qld
Q>N-MUTE_758 | 179.4182 | 0 | 4.5833 | 0 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Thermal | Qld
CA_SYDS_5233E05E_1 | 167.1215 | 0 | 0.25 | 0 | Constraint Automation, O/L XFMR T_2@R_TOWN@SA for CTG LSIR on trip of R_TOWN - TUNKIL 275KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
S>V_RBNW_RBMWP3 | 163.1108 | 3835.3871 | 0.33333 | 2.8333 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage | Thermal | SA
F_MAIN++TL_L60_0700 | 162.898 | 0 | 2.25 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>>TBTU_TBCG_TBMO | 156.4482 | 1525.3891 | 0.91667 | 3 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
F_ESTN+GFT_TG_R5 | 155.4423 | 0 | 25.4167 | 0 | Raise 5 min requirement for a Eastern Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | Outage | FCAS | FCAS
S^NIL_SA_NORTH | 155.2054 | 0 | 0.25 | 0 | Out = NIL, Manage voltage collapse in northern SA for the trip of one 275kV line between Davenport-Para or Davenport-Tungkillo.(Note:for both DV + RB Syn Cons are I/S, OR one DV Syn Con O/S, OR one RB Syn Con O/S, OR one DV +RB Syn Con O/S) | NIL | Voltage Stability | SA
F_I+TL_L6_0700 | 153.4956 | 0 | 6.75 | 0 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 700 | Outage | FCAS | FCAS
F_N_ER03_LREG | 152.5124 | 0 | 0.58333 | 0 | Out= NIL, Eraring 3 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_ER04_LREG | 152.5124 | 0 | 0.58333 | 0 | Out= NIL, Eraring 4 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN+94_96_TL_L5 | 149.39 | 0 | 0.58333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load , Basslink unable transfer FCAS | Outage | FCAS | FCAS
V>>V_BUDP_6 | 148.5039 | 0 | 0.25 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
T>T_NIL_BL_5A | 147.9458 | 0 | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Hadspen to Georgetown No. 1 220kV line (flow to North), feedback | NIL | Thermal | Tas
F_S_DLBAT-G_R5 | 144.78 | 19.52 | 18.9167 | 2.9167 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN+TTS_TG_R5 | 138.522 | 0 | 17.9167 | 0 | Raise 5 min requirement for a Eastern Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | Outage | FCAS | FCAS
F_Q++BCDM_R60 | 137.2522 | 224.547 | 1.5 | 7.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
N>>V_NIL_65_66 | 136.5806 | 0 | 0.083333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL | Thermal | NSW
QN_1200_TEST | 126.4013 | 0 | 0.83333 | 0 | Qld to NSW on QNI upper transfer limit of 1200 MW, limit for testing of QNI minor interconnection upgrade. | Outage | Discretionary | Qld
N_X_MBTE2_A & N_X_MBTE2_B | 121.9433 | 1048.5675 | 0.41667 | 11.0833 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
F_Q++LDTW_R6 | 118.4483 | 2949473.2448 | 1.5833 | 96.75 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
Q>>CLWU_BCCP_LCCP | 116.6649 | 0 | 0.083333 | 0 | Out= Calvale to Wurdong (871), avoid O/L Larcom Creek to Calliope River (8859) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Thermal | Qld
F_N_LD01_LREG | 115.8524 | 0 | 0.41667 | 0 | Out= NIL, Liddell 1 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_N_LD04_LREG | 115.8524 | 0 | 0.41667 | 0 | Out= NIL, Liddell 4 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>N-NIL_996_IN | 115.576 | 0 | 0.16667 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL | Thermal | NSW
V::S_HYSE_MG_PPGT1 | 115.0204 | 0 | 0.41667 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors I/S). Co-optimised eq PPGT1 LHS | Outage | Transient Stability | SA
F_QNV++MG_R5 | 113.6295 | 0 | 17 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+GTTE_TL_L5 | 113.45 | 0 | 4.4167 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+NIL_BB_TG_R6 | 112.71 | 0 | 5.25 | 0 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_S_LG2_L60 | 112.55 | 0 | 3 | 0 | Out= NIL, Ladbroke Grove Unit2 L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N_LIMOSF11_ZERO | 112.0561 | 522533.6444 | 0.083333 | 42.0833 | Limondale 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>>V-NIL_0X1 | 111.0315 | 451.3389 | 0.16667 | 0.58333 | Out= NIL, avoid O/L Buronga to Red cliffs (OX1) on Nil trip, Feedback | NIL | Thermal | NSW
Q_WARWSF2_16 | 110.73 | 0 | 0.083333 | 0 | Warwick Solar Farm 2 upper limit of 16 MW | Outage | Discretionary | Qld
F_MAIN++MG_R60_0850 | 109.67 | 0 | 1.6667 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+94_96_TL_L6 | 108.56 | 0 | 0.58333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_N_LD02_LREG | 105.4624 | 0 | 0.33333 | 0 | Out= NIL, Liddell 2 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++FARE_N-2_TG_R6 | 103.6889 | 2894.9167 | 0.25 | 10.3333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_MAIN+TL_L60_0700 | 99.2 | 0 | 0.41667 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>X_RBTU+RX+HUSN_22 | 98.5653 | 0 | 0.5 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Robertstown 132 kV line, Feedback | Outage | Thermal | SA
S>>X_RBPA+RBTX2_05 | 94.4438 | 0 | 0.083333 | 0 | Out= Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown-Morgan Whyalla 4 (1) on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage | Thermal | SA
N_V_HV1500 | 93.183 | 0 | 0.33333 | 0 | Discretionary constraint on transfer from NSW to VIC of 1500 MW on DDTS-NSW cutset | Outage | Discretionary | NSW
F_Q++8C_R60 | 90.6069 | 686.9751 | 0.75 | 7.0833 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
V>>V_ROTS_TX_3A_R | 84.6935 | 0 | 0.083333 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Thermal | Vic
S>>RBTX1_NIL_RBTX2 | 83.888 | 0 | 0.083333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Robertstown 275/132kV TX2 on Nil trip, Feedback | NIL | Thermal | SA
V::N_ROSM_xxx | 81.2518 | 813.6206 | 0.16667 | 3 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
F_MAIN+MG_R60_0850 | 81.03 | 0 | 1.4167 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_ESTN++HYMO_L60 | 80.8853 | 96.4629 | 9.5 | 14 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
N>>UTRV-6X_64_1 | 78.9767 | 0 | 0.083333 | 0 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, avoid O/L Lower Tumut to Upper Tumut (64) on trip of Upper Tumut to Stockdill (1) line, Feedback | Outage | Thermal | NSW
V_MOORBWF_50WT | 78.0201 | 0 | 0.16667 | 0 | Limit Moorabool Wind Farm upper limit to 0 MW if number of turbine ON exceed 50. Constraint swamp out if number of turbine ON not exceed 50. DS only | Outage | System Strength | Vic
F_ESTN++HYTR_L60 | 77.6 | 19.17 | 8.5833 | 0.5 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
SA_IBR_1800 | 75.4136 | 0 | 0.16667 | 0 | Discretionary upper limit of 1800 MW for SA non-synchronous generation | Outage | Discretionary | SA
F_QNV+MCSH_TG_R5 | 75.12 | 0 | 3.6667 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>CNRB_MKRB_DVBR | 75.1091 | 0 | 0.083333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Davenport-Brinkworth 275kV line on trip of Mokota-Robertstown 27kV line(this trips Hallet Hill WF), Feedback | Outage | Thermal | SA
F_T++GO_C752_TG_R6 | 72.154 | 0 | 0.33333 | 0 | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
S_PPT+SNPT_225 | 72.0455 | 0 | 0.16667 | 0 | SA Pelican Point + Snapper Point generation <= 225 MW | Outage | Discretionary | SA
F_T+GO_C752_TG_R60 | 70.61 | 0 | 1.1667 | 0 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_N_BW04_LREG | 68.8491 | 0 | 0.16667 | 0 | Out= NIL, Bayswater 4 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T+NIL_BB_TG_R60 | 67.881 | 0 | 5.25 | 0 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q>>NIL_CLWU_RGLC | 66.5527 | 39810.0475 | 0.16667 | 3.4167 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL | Thermal | Qld
F_MAIN++MG_R6_0850 | 65.95 | 0 | 1.6667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_L60_APD | 65.9116 | 46.2937 | 4.6667 | 4.6667 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
F_QNV++MCSH_TG_R60 | 62.3758 | 0 | 3.8333 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_ST2_L60 | 62.18 | 0 | 8.6667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
V>>N-LTYS_CH | 60.9117 | 18.5758 | 0.083333 | 0.16667 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
F_MAIN++TL_L5_0700 | 60.68 | 0 | 0.83333 | 0 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ML_L60_APD | 60.52 | 9.6 | 4.0833 | 0.083333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS | FCAS
N::Q_RGSW_KC | 60.3071 | 0 | 0.16667 | 0 | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | Transient Stability | NSW
F_QNV+MCSH_TG_R60 | 59.14 | 0 | 2.9167 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+MG_R6_0850 | 56.54 | 0 | 1.4167 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N_MBTE1_A | 55.8806 | 3530.7554 | 0.66667 | 6 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
F_QNV++ML_L60_0400 | 54.7 | 0 | 2.3333 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS | FCAS
N^^V_LTYS_1 | 53.9213 | 11831.4758 | 0.41667 | 9.3333 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_Q++8C_R6 | 53.907 | 1041.2222 | 0.75 | 7.1667 | Out = Armidale to Dumaresq (8C), Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_T+MAXS_L60 | 52.9652 | 0 | 2.5 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS L60 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
F_T+NTH_ML_L60 | 51.769 | 0 | 5.25 | 0 | Lower 60 sec requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
N:V_NIL_BWRG | 50.3849 | 0 | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | NIL | Transient Stability | NSW
F_MAIN+TL_L5_0700 | 49.98 | 0 | 0.41667 | 0 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 700, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+TL_L6_0700 | 48.68 | 0 | 0.41667 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV++GFT_TG_R5 | 48.243 | 0 | 8.5833 | 0 | Raise 5 min requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
Q_STR_7C2K_HAYSF_5 | 46.4201 | 0 | 0.16667 | 0 | No limit to Hayman Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_MAIN++TL_L6_0700 | 46.12 | 0 | 0.58333 | 0 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV+TTS_TG_R6 | 45.05 | 0 | 0.25 | 0 | Raise 6 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_S_LG1_L5 | 44.5563 | 0 | 1.5 | 0 | Out= NIL, Ladbroke Grove Unit1 L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V::S_TBCP1_MAXG | 42.7643 | 0 | 0.083333 | 0 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage | Transient Stability | SA
F_S+SNS_TG_R6_2_LB_0 | 41.73 | 0 | 8.9167 | 0 | Raise 6 sec Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line (FFR ZERO) | Outage | FCAS | FCAS
S>>CNRB_RBTU_WTTP | 41.4683 | 0 | 0.25 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>CGTB1_TUTB_MOTB | 41.2225 | 6521.4772 | 0.91667 | 2.8333 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
Q>>CPST_BCRG_CLWU | 40.1139 | 61446.3222 | 0.083333 | 6.0833 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
F_MAIN++MG_R5_0850 | 37.98 | 0 | 1.6667 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_ST2_L6 | 36.9509 | 0 | 8.6667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
F_I+ML_ST2_L5 | 36.62 | 0 | 8 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
Q:NIL_CS | 35.1609 | 0 | 0.16667 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Transient Stability | Qld
F_I+ML_ST3_L60 | 34.18 | 0 | 4.3333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
F_ESTN++HYTR_L6 | 33.84 | 4.45 | 9.1667 | 0.41667 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_ESTN++HYMO_L6 | 33.73 | 23.95 | 9.75 | 8.8333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C2K_KEP_1 | 33.55 | 0 | 0.083333 | 0 | No limit to Kennedy Energy Park if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,(NQLD>350&370(AVG),Ross_FN>150&170(AVG) or Kar>=2+ NQLD>250&270(AVG),Ross_FN>100&120(AVG)),Haughton Syncon is ON (80% if Haughton Syncon is OFF +Kar>=2),Zero otherwise. | Outage | System Strength | Qld
F_T+FASH_N-2_TG_R5 | 33.36 | 220.1974 | 0.66667 | 9.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V:S_570_OSC_AUTO | 33.1285 | 0 | 0.083333 | 0 | Out = NIL (Note: with both Black Range series capacitors I/S), Upper transfer limit of 570 MW on VIC to SA on Heywood, Active only when I25 mode cannot be monitored. | NIL | Oscillatory Stability | Vic
F_QNV+MG_R5 | 32.89 | 0 | 3.5 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_ESTN+ML_L60_0400 | 32.7 | 0 | 7.1667 | 0 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS | FCAS
F_Q++BCDM_R6 | 32.45 | 203.2908 | 1 | 8.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_QNV++ML_L5_0400 | 31.7379 | 0 | 0.83333 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_QNV+HYMO_L60 | 28.33 | 28.4268 | 1.5 | 1.25 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_L5_APD | 27.78 | 13.43 | 5.0833 | 4.3333 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
V>SML_NSWRB_10 | 27.5933 | 0 | 0.083333 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL | Thermal | Vic
Q_STR_7C2K_CLRSF_2 | 26.9962 | 1777.4169 | 0.16667 | 3.1667 | Limit 80% to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
F_I+ML_L60_0400 | 26.41 | 208.0117 | 7.75 | 57.5 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
F_ESTN+ML_L5_0400 | 26.36 | 0 | 8.1667 | 0 | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage | FCAS | FCAS
V::N_HWRO3_O1 | 26.0773 | 0 | 0.083333 | 0 | Out = Hazelwood to Rowville No.3 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage | Transient Stability | Vic
F_T+NTH_ML_L5 | 24.17 | 0 | 3.25 | 0 | Lower 5 min requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV++MCSH_TG_R5 | 23.67 | 0 | 2.8333 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T++GO_C752_TG_R60 | 23.35 | 0 | 0.41667 | 0 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_S+QPS5_R60 | 23.21 | 0 | 2.5833 | 0 | Raise 60 sec Service Requirement for SA island for loss of Quarantine 5 | Outage | FCAS | FCAS
F_MAIN++ST2_ML_L60 | 22.2662 | 0 | 0.66667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV++TTS_TG_R6 | 22.1654 | 0 | 0.91667 | 0 | Raise 6 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N::V_NIL_MSDD | 22.0678 | 0 | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | NIL | Transient Stability | NSW
F_ESTN+MCSH_TG_R5 | 21.11 | 0 | 4.75 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line | Outage | FCAS | FCAS
F_MAIN+BIP_ML_L6 | 20.53 | 0 | 8.5833 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_MAIN++ST2_ML_L6 | 19.93 | 0 | 0.66667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ST1_ML_L6 | 19.39 | 0 | 0.33333 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
VSML_VFRB_OFF | 19.0895 | 0 | 0.083333 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Other | Vic
F_MAIN+MG_R5_0850 | 19.08 | 0 | 1.4167 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 850, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV++HYTR_L6 | 18.89 | 0 | 0.83333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV++HYTR_L60 | 18.069 | 0 | 0.33333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V::N_HYMO_O2 | 17.3153 | 0 | 0.083333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage | Transient Stability | Vic
F_T+NIL_BB_TG_R5 | 17.11 | 0 | 3.5 | 0 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_QNV++HYMO_L60 | 16.9 | 9.46 | 1.3333 | 0.91667 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_N_MP2_RREG | 16.18 | 0 | 0.083333 | 0 | Out= NIL, MT Piper 2 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
T>T_X_LIPM_WACB_C | 15.86 | 0 | 0.66667 | 0 | Out = Both Liapootah - Waddamana - Palmerston 220 kV lines, with associated 220kV CB at WA O/S, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Thermal | Tas
F_QNV+MO_TG_R60 | 15.81 | 0 | 0.16667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>>V_NIL_3_SIPS | 15.7582 | 0 | 0.083333 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, 5 min line rating, feedback. Swamp if SIPS not available | NIL | Thermal | Vic
V>>V_NIL1A_R | 15.2352 | 0 | 0.25 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL | Thermal | Vic
F_T+BB_N-2_TG_R5 | 14.4 | 0 | 1.3333 | 0 | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV++TTS_TG_R5 | 14.0015 | 0 | 1 | 0 | Raise 5 min requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+GO_C752_TG_R5 | 13.65 | 0 | 1.9167 | 0 | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ST3_ML_L60 | 13.48 | 0 | 1.5 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_ST3_L6 | 13.42 | 0 | 5.1667 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
F_I+ML_ST1_L6 | 12.93 | 0 | 4.4167 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
F_MAIN+ST3_ML_L6 | 12.25 | 0 | 1.5 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_S+QPS5_R5 | 12.07 | 0 | 2.5833 | 0 | Raise 5 min Service Requirement for SA island for loss of Quarantine 5 | Outage | FCAS | FCAS
F_S+ML_R6_2_LB_0 | 11.7 | 0 | 2.5 | 0 | Raise 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage | FCAS | FCAS
F_I+ML_ST3_L5 | 11.46 | 0 | 2.9167 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a NEM Load Event- loss of Surat load on trip of remaining parallel feeder | Outage | FCAS | FCAS
S>LFTI_PPPW_NOTI4 | 11.4281 | 0 | 0.083333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L New Osborne-TIPS #4 66kV line, on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Thermal | SA
F_MAIN++ML_L5_APD | 11.2455 | 4.4 | 1 | 1.0833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ML_L6_APD_LD | 10.92 | 32.8706 | 1.5 | 3.25 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_MAIN+BIP_ML_L60 | 10.58 | 0 | 5.25 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_N_BW01_LREG | 10.2724 | 0 | 0.083333 | 0 | Out= NIL, Bayswater 1 LREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S+TB4_R6_2_LB0_70M | 10.14 | 0 | 2.1667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B4 (FFR ZERO) for 70 MW metro gen trip option | Outage | FCAS | FCAS
F_QNV++MCSH_TG_R6 | 9.8469 | 0 | 1.25 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+FASH_N-2_TG_R6_1 | 9.8253 | 168.7479 | 0.083333 | 0.83333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS | FCAS
F_MAIN+ML_L5_APD | 9.66 | 0.79 | 4.25 | 0.083333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_N_WALGR_BAT_G_R60 | 9.61 | 0 | 0.25 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise 60 sec Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S+PAREP_R6_2_LB_0 | 9.4025 | 0 | 2.0833 | 0 | Raise 6 sec Service Requirement for SA island for loss of Davenport - Pt Patterson 275kV line (FFR ZERO) | Outage | FCAS | FCAS
F_ESTN+MCSH_TG_R60 | 9.125 | 0 | 1.5 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line | Outage | FCAS | FCAS
F_QNV+HYMO_L6 | 8.93 | 11.8293 | 1.5 | 0.91667 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+ML_L5_0400 | 8.23 | 0 | 0.91667 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage | FCAS | FCAS
S>>MOTB_TBTU_TBCG | 8.1157 | 0 | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_MAIN+ST3_ML_L5 | 8.08 | 0 | 1.5 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+ML_L60_0400 | 8.01 | 0 | 0.58333 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage | FCAS | FCAS
S>NIL_HUWT_STBG2 | 8.01 | 1903054.8793 | 0.083333 | 217.0833 | Out = Nil; avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=60 MW && when Dalymple Battery (i.e. both Gen and Load component) is I/S].[Note:Swamped when WTTPT<80 && DALR OFF OR DalrB OFF] | NIL | Thermal | SA
V^^SML_NIL_3 | 7.6323 | 0 | 0.083333 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Voltage Stability | Vic
F_QNV+GFT_TG_R60 | 7.43 | 0 | 0.16667 | 0 | Raise 60 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T_FARC2_R6 | 7.19 | 0 | 0.25 | 0 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_QNV++MO_TG_R60 | 6.76 | 0 | 0.33333 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_QNV+TTS_TG_R5 | 6.44 | 0 | 0.58333 | 0 | Raise 5 min requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_I+BIP_ML_L5 | 6.37 | 0 | 2.1667 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, for loss of the largest Boyne Island potline. | NIL | FCAS | FCAS
S>>CGTB1_TBTU_TBMO | 6.1545 | 35910.0207 | 0.16667 | 22.75 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
SVML_FLT_125 | 5.9665 | 24373.5438 | 0.16667 | 34.8333 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
F_I+ML_L5_0400 | 5.55 | 59.67 | 4.0833 | 53.5833 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
F_T++FASH_N-2_TG_R60 | 5.55 | 1942.5108 | 0.16667 | 9.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_S+TORRB2_R60 | 5.3632 | 0 | 0.75 | 0 | Raise 60 sec Service Requirement for SA island for loss of Torrens Island B2 | Outage | FCAS | FCAS
S>>SETB_TBSE_KHKN_1 | 4.7446 | 0 | 0.083333 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith-Kincraig 132kV Line on trip of other Tailem Bend-South East 275kV line, (Note: with both SE series caps I/S or O/S) | Outage | Thermal | SA
F_MAIN++BIP_ML_L6 | 4.69 | 0 | 1.5833 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_N_WALGR_BAT_G_R6 | 4.29 | 0 | 0.25 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise 6 sec Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S+SNS_TG_R6_3_LB_0 | 4.29 | 0 | 0.91667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Blyth West - Snowtown 275kV line (FFR ZERO) | Outage | FCAS | FCAS
F_S+HL_TG_R60 | 4.27 | 0 | 0.75 | 0 | Raise 60 sec Service Requirement for SA island for loss of Canowie to Hallett 275 kV line | Outage | FCAS | FCAS
F_S+HL_TG_R5 | 3.51 | 0 | 0.75 | 0 | Raise 5 min Service Requirement for SA island for loss of Canowie to Hallett 275 kV line | Outage | FCAS | FCAS
S>>X_RBTU+HUWT_23 | 3.3699 | 0 | 0.083333 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Redhill T-Brinkworth 132kV line on trip of Bungama 132/275 kV TX, Feedback | Outage | Thermal | SA
F_ESTN+MCSH_TG_R6 | 3.16 | 0 | 0.41667 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line | Outage | FCAS | FCAS
F_QNV+MCSH_TG_R6 | 3.1 | 0 | 0.58333 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>CNRB_BRTW_WTTP | 2.4003 | 0 | 0.083333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
F_MAIN++BIP_ML_L5 | 2.16 | 0 | 0.41667 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_QNV+MO_TG_R5 | 2.16 | 0.12 | 0.5 | 0.083333 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
CA_SYDS_5125A47F_1 | 2.0225 | 0 | 0.083333 | 0 | Constraint Automation, O/L X3:LX3:I:220@BALRANLD@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP4(EMPSYD) | Outage | Thermal | Constraint Automation
Q_STR_7C2K_KIDSF_5 | 2.0201 | 0 | 0.16667 | 0 | No limit to Kidston Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld
F_MAIN++ST1_ML_L6 | 2.02 | 0 | 0.66667 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++BIP_ML_L60 | 2.01 | 0 | 1.1667 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_ESTN++HYMO_L5 | 1.97 | 2.57 | 0.83333 | 1.6667 | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_S+PPT_R6_2_LB_0 | 1.95 | 0 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Pelican Point (FFR ZERO) | Outage | FCAS | FCAS
F_S+TB2_R6_2_LB0_70M | 1.95 | 0 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA island for loss of Torrens Island B2 (FFR ZERO) for 70 MW metro gen trip option | Outage | FCAS | FCAS
F_ESTN+MO_TG_R5 | 1.86 | 34.58 | 0.66667 | 2.6667 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line | Outage | FCAS | FCAS
F_QNV+GFT_TG_R5 | 1.47 | 0 | 0.16667 | 0 | Raise 5 min requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++ML_L5_0400 | 1.45 | 9.71 | 1.1667 | 3.75 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_N_WALGR_BAT_G_R5 | 1.28 | 0 | 0.25 | 0 | Out= Nil, Wallgrove BESS (generation component) Raise 5 min Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_QNV++HYMO_L6 | 1.23 | 3.0949 | 0.25 | 0.58333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ML_L60_0400 | 1.22 | 311.1993 | 0.58333 | 3.5 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_STHN++ARTW_L60 | 1.1 | 0 | 0.66667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage | FCAS | FCAS
F_MAIN++ML_L60_0400 | 1.02 | 7.5852 | 0.33333 | 1.1667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_QNV++MO_TG_R5 | 1.01 | 0 | 0.41667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T++FASH_N-2_TG_R5 | 0.58 | 63.5258 | 0.16667 | 8.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_MAIN++NIL_BL_L5 | 0.57 | 0 | 0.5 | 0 | Mainland Lower 5 min Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
F_T++GO_C752_TG_R5 | 0.47 | 0 | 0.083333 | 0 | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_MAIN++ST3_ML_L5 | 0.39 | 0 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++ST3_ML_L6 | 0.39 | 0 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN++ST3_ML_L60 | 0.39 | 0 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T++GTTE_TL_L6 | 0.18 | 0 | 0.083333 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
F_MAIN+ML_L5_0400 | 0.15 | 22.32 | 0.083333 | 3.3333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_MAIN+BIP_ML_L5 | 0.12 | 0 | 0.16667 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_ESTN++HYTR_R60 | 0.09 | 0 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Raise 60 sec Requirement | Outage | FCAS | FCAS
F_MAIN++ST2_ML_L5 | 0.08 | 0 | 0.16667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+BLFCTRL_L60 | 0.06 | 0 | 0.083333 | 0 | Out = Nil, Lower 60 sec requirement for up to 100 MW fast response on Basslink for a Tasmanian event. | NIL | FCAS | FCAS
F_T+MAXS_L5 | 0.03 | 0 | 0.083333 | 0 | Out = Credible TAS Nth-Sth separation risk, maximum fraction of overall TAS L5 FCAS procurement from south of Palmerston | Outage | FCAS | FCAS
F_QNV++HYMO_L5 | 0.02 | 0.23 | 0.083333 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S_HDWF3_0 | 0.01103 | 0 | 0.75 | 0 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
S-HDWF2_0 | 0.00836 | 0 | 0.75 | 0 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
S_HDWF1_0 | 0.00796 | 0 | 0.75 | 0 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
Q-HAYSF_MVAR | 0.0026 | 0 | 0.16667 | 0 | Constraint to violate if Reactive power output of Hayman Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
V>>V_KM_CB_2 | 0.00156 | 0 | 0.083333 | 0 | Out= Kiamal 220kV CB (one or more MR2B or 7422A or 7422B), avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | Outage | Thermal | Vic
Q_NIL_STRGTH_KIDSF | 0.00103 | 509611.1012 | 0.083333 | 19.4167 | Out = Nil, limit Kidston solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q-CLRSF_MVAR | 0.00099 | 0 | 0.083333 | 0 | Constraint to violate if Reactive power output of Clare Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q_STR_7C2K_WHTSF_5 | 0.00017 | 0 | 0.083333 | 0 | No limit to Whitsunday Solar Farm if Stan>=2+(Stan+Cal)>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Haughton Syncon is ON (80% if Haughton Syncon is OFF),Zero otherwise. | Outage | System Strength | Qld

## Summary By Region
Binding Hours
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Ad-Hoc |  |  |  | 0 | 0 | 0
Constraint Automation | 4.75 | 1.3333 | 8.5833 | 22.75 | 14.4167 | 13
Direction | 1152.0833 | 8190.0833 | 4093.5833 | 6243.5 | 10937 | 8580.4167
FCAS | 88959.4167 | 95124.9167 | 105057.75 | 103359.8333 | 108605.1667 | 116665.9167
NSW | 4260.0833 | 3057.8333 | 4993.6667 | 5560.75 | 9057.9167 | 18965.6667
Negative Residue | 25.75 | 10.4167 | 24.1667 | 31.25 | 126.0833 | 135.9167
Non-Conformance | 97.3333 | 61.0833 | 93.75 | 110.5833 | 75.5 | 999
Other | 311.8333 | 115.25 | 64.3333 | 48.4167 | 7.25 | 14.1667
Outage Ramping | 142.25 | 174.4167 | 475.0833 | 645.8333 | 912.5 | 656.3333
Qld | 996.6667 | 511.3333 | 3120.5833 | 8015.5 | 4006.25 | 8083.5833
Quick | 1918.25 | 12617.6667 | 10994.8333 | 9862.0833 | 11963.75 | 11952.1667
SA | 2013.25 | 3285.75 | 3935.6667 | 4110 | 6565.9167 | 8702.3333
Tas | 923.1667 | 1027.6667 | 966.5833 | 1886.6667 | 3197.8333 | 3445.25
Vic | 2618 | 1914.5 | 5095.75 | 6439.6667 | 8030.75 | 9178.4167
Binding Impact
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Ad-Hoc | 0 | 0 | 0 | 0 | 0 | 0
Constraint Automation | 6287.0142 | 4494.9703 | 59181.5539 | 14369.9689 | 44668.7651 | 163091.1969
FCAS | 24018595.0767 | 11563905.7935 | 14750181.9392 | 28959781.4212 | 22909324.6631 | 52721054.5674
NSW | 3811263.7887 | 4130424.9984 | 20853119.0897 | 20558572.6087 | 70853460.552 | 170481451.2232
Negative Residue | 65879.5695 | 190929.9383 | 357086.6257 | 778063.9302 | 5915845.9777 | 3211345.7111
Other | 19441.5552 | 11515.5764 | 31229.546 | 199098.2389 | 13605.2418 | 24345.9237
Qld | 1557960.0849 | 1092572.6105 | 14405785.5151 | 58969747.1872 | 29235595.5037 | 61043423.9559
SA | 19603528.2545 | 49743082.8304 | 23177002.4614 | 19911748.8298 | 32002902.6706 | 133245974.3113
Tas | 4771966.3751 | 2671514.9731 | 5630711.8908 | 7676693.2707 | 5526650.8229 | 17849391.7548
Vic | 3681628.8597 | 3495766.3104 | 19701434.9435 | 29835220.6476 | 46172027.4914 | 82285810.649
Total | 57536550.5786 | 72904208.0013 | 98965733.5652 | 166903296.1032 | 212674081.6883 | 521025889.2934
Note on A6: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Commissioning | 501.9167 | 12116 | 10389.25 | 7565 | 10437.3333 | 8302.0833
FCAS - NIL | 83335.5 | 89035.8333 | 86275.9167 | 87403.0833 | 97807.5 | 100439.9167
FCAS - Outage | 5623.9167 | 6087.5833 | 18781.8333 | 15954.5833 | 10797.6667 | 16226
System Normal | 6047.6667 | 4947.25 | 8902 | 12236.5 | 17536.9167 | 19164.3333
Network Support | 55.6667 | 210.3333 | 74.25 | 123.4167 | 49.4167 | 547.3333
Negative Residues | 25.75 | 10.4167 | 24.1667 | 31.25 | 126.0833 | 135.9167
Outage | 5121.75 | 4817.0833 | 9302.6667 | 13833.9167 | 13369.5 | 29689.75
Total (non-FCAS) | 11752.75 | 22101.0833 | 28692.3333 | 33790.0833 | 41519.25 | 57839.4167
Binding Impact
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Commissioning | 933870.4383 | 48442546.0203 | 68138620.5509 | 20610054.6861 | 29730094.3355 | 12911695.4812
FCAS - NIL | 9691374.8176 | 8309289.3932 | 10234061.3339 | 8943329.8904 | 9672529.6493 | 21598657.9262
FCAS - Outage | 14327220.2591 | 3254616.4004 | 4516120.6054 | 20016451.5307 | 13236795.0138 | 31122396.6412
System Normal | 16979263.4586 | 20382744.3293 | 37998718.3151 | 76531698.5404 | 99527702.8232 | 185551562.8222
Network Support | 965379.2057 | 30414067.7368 | 683796.7041 | 243610.7044 | 1310271.1961 | 36649220.8145
Negative Residues | 65879.5695 | 190929.9383 | 357086.6257 | 778063.9302 | 5915845.9777 | 3211345.7111
Outage | 15507433.2681 | 10352560.2034 | 45175949.9811 | 60390141.5071 | 83010937.0281 | 242892705.3782
Total | 58470421.0169 | 121346754.0216 | 167104354.1161 | 187513350.7893 | 242404176.0239 | 533937584.7746

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2022 Hours | 2021 Hours | Description | Type
N-Q-MNSP1 Export | N^N-LS_SVC | 4283.1667 | 64.75 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; Swamp out when three directlink cables are O/S; TG formulation only | Outage
N-Q-MNSP1 Export | N_X_MBTE_3A | 298.1667 | 157.9167 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 171.1667 | 314.1667 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 165.25 | 4.25 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^^Q_NIL_A | 141.1667 | 37.4167 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
N-Q-MNSP1 Export | N>N-NIL_LSDU | 89.5833 | 175.8333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | N>Q-NIL_757_758 | 58.9167 | 110.0833 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL
N-Q-MNSP1 Export | NQTE_ROC | 31.6667 | 61 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Export | N^^Q_TW_330_BUS3_B1 | 24.0833 | 25.4167 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B4 | 19.25 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage
N-Q-MNSP1 Export | N^^Q_ARDM_B1 | 7 | 8.3333 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 6.1667 | 40.6667 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B5 | 5.5 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Callide C3 | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 4.8333 | 2.3333 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N^^Q_TW_330_BUS1_B1 | 4.1667 | 30.6667 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | N^^Q_AR_330_BS5_1_B1 | 3.9167 | 4.25 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R6 | 3.3333 | 10.3333 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B3 | 3 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Millmerran 2 | Outage
N-Q-MNSP1 Export | N>N-GITN_TE_C1 | 2.6667 | 2.75 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | Q>>BCRG_BCCP_CLWU | 1.9167 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
N-Q-MNSP1 Export | N^^Q-X_AR_LS_VC_B1 | 1.75 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | QNTE_OSCILLATE | 1.6667 | 3.3333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R5 | 1.4167 | 1.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | Q>>TRSP_BKSP_MESP | 1.4167 | 0 | Out= 832 (H18 Tarong to H2 South Pine) 275 kV feeder, avoid O/L 838 (H36 Blackwall to H2 South Pine) 275 kV feeder on trip of 825 (H12 Mt England to H2 South Pine) 275 kV feeder, Feedback | Outage
N-Q-MNSP1 Export | N^^Q_LS_SVC_KPP_1 | 0.91667 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage
N-Q-MNSP1 Export | #R024579_001_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 22/06/2018, Version: 1 | Other
N-Q-MNSP1 Export | N^^Q_LS_VC_B2 | 0.66667 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Millmerran 1 | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 0.66667 | 5.6667 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N>NIL_LSDU | 0.58333 | 0 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | NRM_NSW1_QLD1 | 0.58333 | 0.16667 | Negative Residue Management constraint for NSW to QLD flow. | NIL
N-Q-MNSP1 Export | #R026764_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R026771_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024734_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024901_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024909_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024979_005_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R026591_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | N::Q_LDNC_TNT | 0.41667 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage
N-Q-MNSP1 Export | Q>>CPST_LCCP_CLWU | 0.41667 | 2 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage
N-Q-MNSP1 Export | #R025038_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R025489_005_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 19/04/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R025855_005_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 19/04/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R024609_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R024617_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R025039_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | N_X_MBTE2_A | 0.25 | 0.91667 | Out= two Directlink cables, NSW to Qld limit | Outage
N-Q-MNSP1 Export | #R024609_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024609_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024617_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024617_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024688_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q-X_AR_LS_VC_B2, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024734_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R025037_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R025039_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R025855_005_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 19/04/2022, Version: 1 | Other
N-Q-MNSP1 Export | #R026591_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | F_Q++ARTW_R60 | 0.16667 | 2.5 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N::Q_RGSW_KC | 0.16667 | 0 | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Export | N^^Q-X_AR_LS_VC_B2 | 0.16667 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Millmerran 1 | Outage
N-Q-MNSP1 Export | N^^Q-X_AR_LS_VC_B3 | 0.16667 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Millmerran 2 | Outage
N-Q-MNSP1 Export | #R024688_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R024895_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024912_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R025013_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R025460_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R025806_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R025859_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R026123_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 19/04/2022, Version: 1 | Other
N-Q-MNSP1 Export | F_STHN++ARTW_L60 | 0.083333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage
N-Q-MNSP1 Export | Q>>CPST_BCRG_CLWU | 0.083333 | 4.9167 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 162.8333 | 183.6667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 141.9167 | 163.1667 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 102.4167 | 174.9167 | Out= one Directlink cable, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N_NIL_TE_B | 92.75 | 26.8333 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | N>>LDNC_964_82 | 73 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, Swamps if 964 O/S, Feedback | Outage
N-Q-MNSP1 Import | N>>NIL_86_8U_S | 49.5 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (8U or 86) on trip of the other Armidale to Tamworth line (86 or 8U), Feedback | NIL
N-Q-MNSP1 Import | N>NIL_MBDU | 42.3333 | 0 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Import | Q>NIL_757_758_ECS | 40 | 0 | Out= Nil, ECS for managing Mudgeeraba to Terranora (757 or 758) 110kV lines, Summer and Winter ECS ratings selected by SCADA status | NIL
N-Q-MNSP1 Import | QNTE_ROC | 34.4167 | 58.9167 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | N>>NIL_84_88_S | 33.9167 | 0 | Out= NIL, avoid O/L Tamworth to Liddell (84) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 33.1667 | 91.9167 | Negative Residue Management constraint for QLD to NSW flow | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 26.4167 | 54.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 15.75 | 23.5833 | Out= Nil, avoid overloading Mudgeeraba to Terranora (757) 110kV line, swamped out when ECS is in service | NIL
N-Q-MNSP1 Import | N>>N-964_DC | 11.25 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage
N-Q-MNSP1 Import | N>>NIL_88_84_S | 9.25 | 0 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | NIL
N-Q-MNSP1 Import | Q>N-MUTE_757 | 9.1667 | 0 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | N>N-NIL_DC | 9 | 9.5833 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
N-Q-MNSP1 Import | Q^^NIL_CS | 7.9167 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL
N-Q-MNSP1 Import | N>N-NIL_MBDU | 6.3333 | 53.4167 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Import | N>>N-DTSS_20 | 6.0833 | 0 | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 6.0833 | 0 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | N>>LDTM_964_81_OPEN | 5.25 | 0 | Out= Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage
N-Q-MNSP1 Import | N>>AVMA-17_39_11 | 4.8333 | 0 | Out = Avon - Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
N-Q-MNSP1 Import | Q^^CS_-360 | 4.8333 | 0 | Nominated Offset -360MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage
N-Q-MNSP1 Import | N::V_DDSM_MSDD | 3.8333 | 0.75 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
N-Q-MNSP1 Import | N>>81_964_82 | 3.25 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage
N-Q-MNSP1 Import | I_CTRL_ISSUE_TE | 2.0833 | 0 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Import | N>>N-DTMN_39_16 | 1.1667 | 0 | Out = Dapto-Marulan(8), avoid O/L Bannaby to Sydney West (39) on trip of Marulan to Avon (16) line, Feedback | Outage
N-Q-MNSP1 Import | N>>X-17+76_39_11 | 0.91667 | 0 | Out= Avon to Macarthur (17) and Sydney South to Wallerawang (76), avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
N-Q-MNSP1 Import | #R024746_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025747_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025760_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N>>N-DTMN_08 | 0.66667 | 0 | Out = Dapto-Marulan(8), avoid O/L Marulan to Avon (16) on trip of Dapto to Kangaroo Valley (18) line, Feedback | Outage
N-Q-MNSP1 Import | #R024734_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024940_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025459_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026591_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024746_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024940_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024952_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025065_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025449_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025449_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025459_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025747_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025760_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025806_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025806_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026764_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024952_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025065_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026135_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R026771_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024997_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025649_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_MBTE1_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026134_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R026771_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | F_Q++ARTW_L60 | 0.25 | 0.91667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 0.25 | 10.25 | Out= two Directlink cables, Qld to NSW limit | Outage
N-Q-MNSP1 Import | #R025649_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_MBTE1_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R025813_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026135_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R026764_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N>>N-NIL_64 | 0.16667 | 0.58333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
N-Q-MNSP1 Import | #R025813_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R026134_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 15/06/2017, Version: 1 | Other
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 322.75 | 9.4167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 250.25 | 410 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
NSW1-QLD1 Export | N^^Q_NIL_A | 174.75 | 38.1667 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
NSW1-QLD1 Export | Q>>BCST_BCST_CLWU | 139.1667 | 88.5 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line, avoid O/L the remaining Stanwell to Bouldercombe 848 or 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | NQ_600_DYN_TEST | 45.6667 | 0 | NSW to QLD on QNI upper transfer limit of 600 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B4 | 37.1667 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage
NSW1-QLD1 Export | Q>>BCRG_CLWU_BCCP | 34.9167 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS3_B1 | 32.1667 | 27.75 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | Q>>NIL_BCCP_RGLC | 25.5 | 20.4167 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL
NSW1-QLD1 Export | Q>>WOPW_WOSP_WOGP_2 | 23.3333 | 27.6667 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | F_Q++ARTW_R6 | 20 | 11.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | Q>>CPST_CLWU_RGLC | 18.3333 | 95.0833 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 16.3333 | 40.6667 | Out = Armidale to Tamworth (85 or 86 or 8U), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Export | NQ_700_DYN_TEST | 15.5833 | 0 | NSW to QLD on QNI upper transfer limit of 700 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
NSW1-QLD1 Export | Q>>PWSP_WOSP_PWSP | 14 | 0 | Out= Palmwoods to South Pine (808) line, avoid O/L on parallel 110kV lines between Palmwoods and South Pine(745 /746) on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | Q>>CLWU_BCCP_BCRG | 13.75 | 0 | Out = Calvale to Wurdong (871), avoid O/L Bouldercombe to Raglan (811) or Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_ARDM_B1 | 13.5 | 8.75 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B5 | 12.0833 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Callide C3 | Outage
NSW1-QLD1 Export | Q>>CPST_CLWU_BCST | 10.4167 | 32.1667 | Out = 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Stanwell to Bouldercombe 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++ARTW_R5 | 7.8333 | 1.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | N>>NIL_84_83_OPEN | 5.8333 | 0 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | Q>>CPWO1_CPWO2_WUGG | 5.5833 | 65.4167 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Woolooga (814) on trip of Wurdong to Teebar Creek (819) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q-X_AR_LS_VC_B1 | 5 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B3 | 4.5833 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Millmerran 2 | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS1_B1 | 3.75 | 33.4167 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | F_Q++ARTW_R60 | 3.3333 | 2.6667 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_AR_330_BS5_1_B1 | 3.1667 | 4.25 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | Q>>CLWU_BCRG_BCCP | 3.1667 | 0.66667 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
NSW1-QLD1 Export | Q>>NIL_STCP_RGLC | 3 | 1.3333 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Stanwell to Calliope River (848+812) line, Feedback | NIL
NSW1-QLD1 Export | N::Q_LDNC_TNT | 2.75 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability for a trip of Tarong North generators. | Outage
NSW1-QLD1 Export | NRM_NSW1_QLD1 | 2.3333 | 0.16667 | Negative Residue Management constraint for NSW to QLD flow. | NIL
NSW1-QLD1 Export | Q>>BCRG_BCCP_CLWU | 2.25 | 0 | Out= Bouldercombe to Raglan (811), avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
NSW1-QLD1 Export | Q>>TRSP_BKSP_MESP | 1.9167 | 0 | Out= 832 (H18 Tarong to H2 South Pine) 275 kV feeder, avoid O/L 838 (H36 Blackwall to H2 South Pine) 275 kV feeder on trip of 825 (H12 Mt England to H2 South Pine) 275 kV feeder, Feedback | Outage
NSW1-QLD1 Export | F_Q++LDTW_R6 | 1.4167 | 72.5833 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_LDNC_KC | 1.4167 | 0 | Out= Liddell-Newcastle(81), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | Q>>CPPW_WOSP_WOGP_2 | 1.3333 | 0 | Out= Calliope River to Palmwoods (813+810) 275kV line, avoid O/L Woolooga to Gympie (747/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | F_Q++8E_R6 | 1.1667 | 0 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_LS_SVC_KPP_1 | 1.1667 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage Collapse on loss of Kogan Creek MW | Outage
NSW1-QLD1 Export | #R024579_001_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 22/06/2018, Version: 1 | Other
NSW1-QLD1 Export | N^^Q_LS_VC_B2 | 0.91667 | 0 | Out= Lismore SVC, avoid Voltage Collapse on loss of Millmerran 1 | Outage
NSW1-QLD1 Export | Q>>BCST_BCST_STBS | 0.91667 | 0 | Out = 848 or 849 (H29 Stanwell to H10 Bouldercombe 275 kV line), avoid O/L the remaining 848 or 849(H29 Stanwell to H10 Bouldercombe 275 kV line) on trip of Stanwell to Broadsound (8331) line with 7114/1 open post contingent or pre contingent. Feedback | Outage
NSW1-QLD1 Export | #R024609_004_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024617_004_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | Q>>CPST_LCCP_CLWU | 0.75 | 2.0833 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage
NSW1-QLD1 Export | Q>>NIL_BCCP_LCCP | 0.75 | 0 | Out= Nil, avoid O/L Larcom Creek to Calliope River (8859) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL
NSW1-QLD1 Export | F_Q++LDTW_R60 | 0.66667 | 10.0833 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | #R024912_004_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | Q>>X_CLWU+BCST_2 | 0.58333 | 0 | Out= 871 (H24 Calvale to H40 Wurdong) 275kV line and 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line, avoid O/L remaining 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line on trip of 8811 (Calvale to Halys) line, Feedback | Outage
NSW1-QLD1 Export | Q>>NIL_LCCP_BCCP | 0.5 | 0 | Out= Nil, avoid O/L Bouldercombe to Calliope River (812) on trip of Larcom Creek to Calliope River (8859) line, Feedback | NIL
NSW1-QLD1 Export | #R024901_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024909_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R025038_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | F_Q++8C_R6 | 0.41667 | 5.1667 | Out = Armidale to Dumaresq (8C), Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | #R024875_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q>>CPST_CLWU_RGLC, Effective Date: 10/03/2022, Version: 1 | Other
NSW1-QLD1 Export | #R024970_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025037_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024609_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024617_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024901_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024909_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R025039_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | N^^Q-X_AR_LS_VC_B2 | 0.25 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Millmerran 1 | Outage
NSW1-QLD1 Export | #R024688_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q-X_AR_LS_VC_B2, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024875_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>>CPST_CLWU_RGLC, Effective Date: 10/03/2022, Version: 1 | Other
NSW1-QLD1 Export | #R024895_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024951_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025035_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025039_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | F_Q++BCDM_R6 | 0.16667 | 8.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++BCDM_R60 | 0.16667 | 0.41667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_RGSW_KC | 0.16667 | 0 | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | N^^Q-X_AR_LS_VC_B3 | 0.16667 | 0 | Out= Armidale SVC and Lismore SVC, avoid Voltage Collapse on loss of Millmerran 2 | Outage
NSW1-QLD1 Export | Q>>NIL_CLWU_RGLC | 0.16667 | 3.1667 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL
NSW1-QLD1 Export | #R024922_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R025007_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025013_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025038_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025460_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R025855_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q-X_AR_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R025859_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R026123_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q-X_AR_LS_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | F_Q++8E_R60 | 0.083333 | 0 | Out = Sapphire to Armidale (8E) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N>>N-NIL__2_OPENED | 0.083333 | 0 | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | Q>>CLWU_BCCP_LCCP | 0.083333 | 0 | Out= Calvale to Wurdong (871), avoid O/L Larcom Creek to Calliope River (8859) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
NSW1-QLD1 Export | Q>>CPST_BCRG_CLWU | 0.083333 | 5.75 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
NSW1-QLD1 Import | Q^^NIL_QNI_SRAR | 271.3333 | 131.6667 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL
NSW1-QLD1 Import | F_Q++ARTW_L6 | 170 | 203 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>>LDNC_964_82 | 74 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, Swamps if 964 O/S, Feedback | Outage
NSW1-QLD1 Import | N>>NIL_86_8U_S | 61.25 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (8U or 86) on trip of the other Armidale to Tamworth line (86 or 8U), Feedback | NIL
NSW1-QLD1 Import | N>>NIL_84_88_S | 41.75 | 0 | Out= NIL, avoid O/L Tamworth to Liddell (84) on trip of Tamworth to Muswellbrook (88) line, Feedback | NIL
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 33.9167 | 100 | Negative Residue Management constraint for QLD to NSW flow | NIL
NSW1-QLD1 Import | F_Q++ARTW_L5 | 27.5833 | 62.9167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++BCDM_L6 | 23.9167 | 104.0833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++8E_L6 | 23.75 | 11.5 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++8C_L6 | 20.0833 | 48.4167 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>>NIL_88_84_S | 11 | 0 | Out= NIL, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | NIL
NSW1-QLD1 Import | Q:N_1078 | 9.25 | 3 | QNI oscillatory stability limit of 1078 MW | Outage
NSW1-QLD1 Import | N>>N-964_DC | 8.6667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L one Armidale to Tamworth (85/86) on trip of the other Armidale to Tamworth (85/86) line, Feedback | Outage
NSW1-QLD1 Import | Q^^NIL_CS | 8.5 | 0 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation | NIL
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 7.1667 | 29.6667 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL
NSW1-QLD1 Import | N>N-NIL_DC | 6.3333 | 7.5 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
NSW1-QLD1 Import | N>>N-DTSS_20 | 6.25 | 0 | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
NSW1-QLD1 Import | N>>AVMA-17_39_11 | 5.3333 | 0 | Out = Avon - Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
NSW1-QLD1 Import | N>>LDTM_964_81_OPEN | 5.25 | 0 | Out= Liddell to Tomago (82) with Singleton-Kurri 132kV open, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Newcastle (81) line, Feedback | Outage
NSW1-QLD1 Import | Q^^CS_-360 | 4.8333 | 0 | Nominated Offset -360MW, CQ-SQ voltage stability limit, 2008/2009 implementation | Outage
NSW1-QLD1 Import | F_Q++8C_L5 | 4.75 | 6 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 4 | 13.5 | NSW1-QLD1 >= MIN(-217, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | Q::N_BI_POT_-450 | 4 | 0 | Nominated Offset -450MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage
NSW1-QLD1 Import | N::V_DDSM_MSDD | 3.8333 | 1.0833 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
NSW1-QLD1 Import | N>>81_964_82 | 3.25 | 0 | Out = Liddell to Newcastle (81) line, avoid O/L Port Macquarie to Herron Creek Tee (964/2) on trip of Liddell to Tomago (82) line, (Note: Swamps if 964 O/S) | Outage
NSW1-QLD1 Import | QN_1200_DYN_TEST | 3.1667 | 0 | QLD to NSW on QNI upper transfer limit of 1200 MW, dynamic headroom, DS formulation only, limit for testing of QNI minor interconnection upgrade. | Outage
NSW1-QLD1 Import | Q::N_BI_POT_-500 | 2.9167 | 0 | Nominated Offset -500MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage
NSW1-QLD1 Import | Q::N_8C8J_AR_2LG_N-2 | 2.8333 | 0 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for trip of either Armidale to Dumaresq (8C) or Armidale to Sapphire (8E) 330kV line and loss of a single phase of the remaining line declared credible | Outage
NSW1-QLD1 Import | Q^^N_AR_SVC_1 | 2 | 22 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | N>>N-DTMN_39_16 | 1.1667 | 0 | Out = Dapto-Marulan(8), avoid O/L Bannaby to Sydney West (39) on trip of Marulan to Avon (16) line, Feedback | Outage
NSW1-QLD1 Import | QNI_SOUTH_1150_DYN | 1.0833 | 1.6667 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL
NSW1-QLD1 Import | F_Q++8E_L5 | 1 | 5.3333 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>X-17+76_39_11 | 0.91667 | 0 | Out= Avon to Macarthur (17) and Sydney South to Wallerawang (76), avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_E_F | 0.75 | 0 | NSW1-QLD1 <= MAX(4, InitialFlow - 200) (Wt=35) | Other
NSW1-QLD1 Import | F_Q++NIL_R60 | 0.66667 | 0 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | N>>N-DTMN_08 | 0.66667 | 0 | Out = Dapto-Marulan(8), avoid O/L Marulan to Avon (16) on trip of Dapto to Kangaroo Valley (18) line, Feedback | Outage
NSW1-QLD1 Import | Q^^N_NIL_SRAR | 0.58333 | 0 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL
NSW1-QLD1 Import | F_Q++BCDM_L5 | 0.5 | 18.0833 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | N>>964_88_84_S | 0.5 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Tamworth to Muswellbrook (88) on trip of Tamworth to Liddell (84) line, Feedback | Outage
NSW1-QLD1 Import | #R025642_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q::N_BI_POT_-450, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R025642_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q::N_BI_POT_-450, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | N::V_DTKV_MSDD | 0.41667 | 0 | Out=Dapto - Kangaroo Valley (18), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
NSW1-QLD1 Import | #R025633_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q::N_BI_POT_-500, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | Q::N_ARSVC_AR_2L-G | 0.33333 | 3.5 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | #R025633_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q::N_BI_POT_-500, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | F_Q++ARTW_L60 | 0.25 | 1.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | N>>N-NIL_64 | 0.16667 | 0.58333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
NSW1-QLD1 Import | N::V_NIL_MSDD | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 906.9167 | 1341.6667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 469.9167 | 593.0833 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 358.4167 | 556.8333 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T_V_BL_ZERO_E | 107.9167 | 0 | Direction to zero for Basslink (Tas to Vic) for Dispatch and Predispatch and NOT PASA | Outage
T-V-MNSP1 Export | F_MAIN++GFT_TG_R60 | 79.1667 | 45.8333 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0220 | 75.5 | 213.3333 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 44.75 | 105.1667 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | TV_350 | 44.4167 | 0 | Tas to Vic on Basslink upper limit of 350 MW | Outage
T-V-MNSP1 Export | F_MAIN++TTS_TG_R60 | 42.5833 | 4.4167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R5 | 33.5 | 16.5 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_QNV++MG_R60 | 22.4167 | 0 | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++GFT_TG_R6 | 21.5833 | 2 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 21 | 28.4167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
T-V-MNSP1 Export | F_QNV++MG_R6 | 19.9167 | 0 | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++GFT_TG_R60 | 14.5833 | 0 | Raise 60 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 12.3333 | 39.0833 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 12.3333 | 6.4167 | Out=Nil, Basslink no go zone limits Tas to Vic. Limit Basslink upper limit to 125 MW on 1st DI out of no go zone. i.e. BL <= 125 MW | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 11.1667 | 113.75 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_MAIN++TTS_TG_R6 | 7.75 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++TTS_TG_R5 | 7.5 | 0.41667 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_QNV++MG_R5 | 6.5833 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | TVBL_ROC | 5.5 | 22.1667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Export | T^V_NIL_8 | 4.3333 | 4.5833 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | F_QNV++TTS_TG_R60 | 3.9167 | 0 | Raise 60 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T^V_NIL_9 | 3.5 | 8.5 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | TV_150 | 3.1667 | 0 | Tas to Vic on Basslink upper limit of 150 MW | Outage
T-V-MNSP1 Export | T_BLINK_TV_BID | 2.75 | 0 | Out = Nil, limit Basslink to 0 MW if Basslink bid zero. Constraint to swamp otherwise. | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 2.6667 | 0.75 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_QNV++GFT_TG_R5 | 2.4167 | 0 | Raise 5 min requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++GFT_TG_R6 | 1.9167 | 0 | Raise 6 sec requirement for a QLD, NSW and VIC Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_2A_R | 1.5833 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | T^V_NIL_11 | 1.4167 | 25 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink harmonic filter, swamped if TVCC in service | NIL
T-V-MNSP1 Export | F_QNV++RREG_0220 | 1 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 220 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++MCSH_TG_R5 | 0.66667 | 0 | Out= Heywood to Tarrone line, Eastern Raise 5 min requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++MCSH_TG_R60 | 0.66667 | 0 | Out= Heywood to Tarrone line, Eastern Raise 60 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++MG_R60_0850 | 0.5 | 0 | Raise 60 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++TTS_TG_R5 | 0.5 | 0 | Raise 5 min requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 0.5 | 1 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | F_MAIN++MG_R5_0850 | 0.33333 | 0 | Raise 5 min Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++MCSH_TG_R6 | 0.25 | 0 | Out= Heywood to Tarrone line, Eastern Raise 6 sec requirement for Macarthur and Stockyard Hill Generation loss on trip of MLTS-HGTS line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | #R026121_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 11/05/2022, Version: 1 | Other
T-V-MNSP1 Export | F_MAIN++MG_R6_0850 | 0.16667 | 0 | Raise 6 sec Service Requirement for a Mainland Generation Event, MG = 850, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_QNV++TTS_TG_R6 | 0.083333 | 0 | Raise 6 sec requirement for a Qld,NSW,Vic Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++NTH_LREG | 0.083333 | 0 | Lower Regulation requirement for Northern Tasmania, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | TV_000 | 0.083333 | 0 | Tas to Vic on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_3A_R | 0.083333 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 572.3333 | 672.8333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 522.0833 | 532.9167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L6 | 301.6667 | 123.6667 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 278.8333 | 373.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_DDSM_V1 | 179.0833 | 51.4167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | T_NTH_ROCOF_1 | 174.5 | 0 | Out = Credible risk of, or actual, Tas Nth-Sth separation. Limit non-synchronous generation and Basslink import to limit instantaneous Rate of Change of Frequency to < 3 Hz/sec in Nth TAS | Outage
T-V-MNSP1 Import | V_T_NIL_FCSPS | 159.8333 | 181.0833 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 134.9167 | 272.9167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | T::T_NIL_3 | 118.1667 | 13.25 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0210 | 91.75 | 118 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | VT_ZERO | 91.25 | 71.25 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | V::N_X_SMSC_O1 | 85.6667 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | #T-V-MNSP1_E_O_E | 84.75 | 0 | T-V-MNSP1.ENERGY * 1 >= 150 (Wt = 65) | Other
T-V-MNSP1 Import | V::N_X_SMSC_V1 | 76.9167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | F_T++RREG_0050 | 44.0833 | 63.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_SMSC_S1 | 43.5 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_X_SMSC_V2 | 42.25 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | T_BLINK_TV_NGZ | 37.4167 | 4.0833 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | NIL
T-V-MNSP1 Import | V::N_X_SMSC_O2 | 29.0833 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 27.6667 | 30.5 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 26.0833 | 17.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V^T_NIL_9 | 23.9167 | 6 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL
T-V-MNSP1 Import | V::N_DDSM_S1 | 21.0833 | 13.6667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 20.8333 | 15.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_NILxxx | 19.9167 | 41.4167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
T-V-MNSP1 Import | V::N_SETB_S2 | 17.75 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V3 | 15.6667 | 1.75 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_DDSM_V2 | 15 | 45.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 14.3333 | 10.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_ESTN_TBSE_VE | 13.5 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
T-V-MNSP1 Import | V::N_ESTN_TBSE_O1 | 12.4167 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | VTBL_ROC | 11.8333 | 16.25 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Import | F_MAIN++NIL_BL_L6 | 10.5833 | 46.6667 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 10.3333 | 10.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T_BLINK_VT_BID | 9.4167 | 0 | Out = Nil, limit Basslink to 0 MW if Basslink bid zero. Constraint to swamp otherwise. | NIL
T-V-MNSP1 Import | V_T_NIL_BL1 | 9.4167 | 10.8333 | Out=Nil, Basslink no go zone limits Vic to Tas. Limit Basslink lower limit to -125 MW on 1st DI out of no go zone. i.e. BL >= -125 MW | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 9 | 22.4167 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 9 | 5.1667 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_APD_LD | 8.9167 | 8.75 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++94_96_TL_L60 | 8.6667 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 60 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_SETB_V2 | 8.4167 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 8 | 15.25 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_QNV++ML_L6_0400 | 7 | 0 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_X_SMSC_V | 6.75 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
T-V-MNSP1 Import | T_ROCOF_3 | 6.4167 | 0.41667 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL
T-V-MNSP1 Import | F_T++CSGO_TG_R5 | 5.9167 | 0.5 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S3 | 5.9167 | 0.91667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | V::N_HYSE_V2 | 5.9167 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SETB_V1 | 5.8333 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 5.6667 | 1.25 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_S2 | 5.3333 | 0.66667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_ESTN_TBSE_VB | 4.6667 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 2 | Outage
T-V-MNSP1 Import | V::N_ESTN_TBSE_VA | 4.25 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_MAIN++94_96_TL_L6 | 3.75 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 6 sec requirement for a Tomago Load Event, TL = Max two Potline load , Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_SMSC_SD | 3 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 2.8333 | 4.1667 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_HYSE_V1 | 2.75 | 1 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R6 | 2.5 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R60 | 2.5 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 2.3333 | 9.1667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_ESTN_TBSE_VD | 2.3333 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | T_BLINK_TV_NGZ | 2 | 4.0833 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | Outage
T-V-MNSP1 Import | F_MAIN++94_96_TL_L5 | 1.8333 | 0 | Out = Newcastle to Tomago (94) and Newcastle to Warath West (96), Lower 5 min requirement for a Tomago Load Event, TL = Max two Potline load, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | VT_000 | 1.8333 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | F_MAIN++TL_L60_0700 | 1.5833 | 0 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_SMSC_V1 | 1.5833 | 0 | Out = One South Morang 330 kV series capacitor bank, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_HYTR_O1 | 1.4167 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_JNWG_S1 | 1.1667 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R024930_002_RAMP_F | 1.0833 | 0 | Hard Ramping constraint for constraint VT_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
T-V-MNSP1 Import | V::N_ESTN_TBSE_V1 | 1.0833 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_ROSM_O1 | 1.0833 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_HYTR_O2 | 0.83333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | V::N_SMF2_O1 | 0.83333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | F_MAIN++BIP_ML_L6 | 0.75 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_HYTR_V1 | 0.66667 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | VT_050 | 0.66667 | 0 | Vic to Tas on Basslink upper limit of 50 MW | Outage
T-V-MNSP1 Import | V::N_HYSE_S1 | 0.58333 | 1.9167 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_LTWG_S1 | 0.58333 | 3.5833 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R025247_014_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025401_015_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ST2_ML_L6 | 0.5 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 6 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++ML_L60_0400 | 0.5 | 0 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | VT_100 | 0.5 | 0 | Vic to Tas on Basslink upper limit of 100 MW | Outage
T-V-MNSP1 Import | #R024887_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R025350_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025401_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025611_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026120_015_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026464_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB4_O1, Effective Date: 09/09/2022, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 0.41667 | 0.83333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_QNV++HYMO_L60 | 0.41667 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++LREG_0210 | 0.41667 | 0 | Qld, NSW and Vic Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | T_V_BL_GT_300_E | 0.41667 | 0 | Direction to greater than 300 MW for Basslink (Tas to Vic), for Predispatch | Outage
T-V-MNSP1 Import | #R024673_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R025241_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025247_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026120_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026138_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026173_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026173_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026177_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026302_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026451_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O1, Effective Date: 17/10/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026722_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L5_APD | 0.33333 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 0.33333 | 0.5 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_JNWG_SD | 0.33333 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_SETB_S1 | 0.33333 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R024569_026_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024845_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024845_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R025419_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025466_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026172_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #T-V-MNSP1_RAMP_E_F | 0.25 | 0.75 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other
T-V-MNSP1 Import | F_MAIN++BIP_ML_L60 | 0.25 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++TL_L5_0700 | 0.25 | 0 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 700, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | #R024681_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024887_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R025060_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025350_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025611_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025772_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V2, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026177_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026215_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++NIL_BL_L5 | 0.16667 | 0 | Mainland Lower 5 min Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | F_MAIN++ST2_ML_L5 | 0.16667 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++ML_L5_0400 | 0.16667 | 0 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.16667 | 2.9167 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_5F | 0.16667 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_HWCB_V2 | 0.16667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R024569_026_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024759_032_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_LTWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R025545_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R025615_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_SETB_V2, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026138_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026172_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026215_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026538_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 30/03/2022, Version: 1 | Other
T-V-MNSP1 Import | #R026705_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 07/12/2022, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++BIP_ML_L5 | 0.083333 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, for loss of the largest Boyne Island potline, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ST2_ML_L60 | 0.083333 | 0 | Out = 8889 or 8893 (S5 Western Downs to H78 Orana to H77 Columboola) 275kV line, Lower 60 sec Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++ST3_ML_L5 | 0.083333 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line, Lower 5 min Service Requirement for a Mainland Load Event-loss of Surat load on trip of remaining parallel feeder, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HYTR_L6 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 0.083333 | 2.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_6E | 0.083333 | 0 | Out = Nil, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_HWRO3_O1 | 0.083333 | 0 | Out = Hazelwood to Rowville No.3 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_HYMO_O1 | 0.083333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_HYTR_V2 | 0.083333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
T-V-MNSP1 Import | V::N_LTWG_V1 | 0.083333 | 3.0833 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_ROSM_V1 | 0.083333 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
T-V-MNSP1 Import | V::N_X_SMSC_Q1 | 0.083333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
T-V-MNSP1 Import | V_T_BL_ZERO_E | 0.083333 | 0 | Direction to zero for Basslink (Vic to Tas) for Dispatch and Predispatch and NOT PASA | Outage
V-S-MNSP1 Export | S>NIL_MHNW1_MHNW2 | 1465 | 1629.1667 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL
V-S-MNSP1 Export | S>NIL_NWRB2_NWRB1 | 211.6667 | 0 | Out= NIL, avoid O/L North West Bend-Roberstown #1 132kV line on trip of North West Bend-Robertstown #2 132kV line (this trips MWP1-3 SFs), Feedback | NIL
V-S-MNSP1 Export | V::N_DDSM_V1 | 158.0833 | 23.8333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>V_DDSM_1 | 124.6667 | 69.3333 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_25 | 93.6667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Export | V^^SML_NSWRB_2 | 78.5 | 58.3333 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL
V-S-MNSP1 Export | V>>N_NIL_65_66 | 75.9167 | 0 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | V::N_X_SMSC_O1 | 73.9167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V^^N_NIL_1 | 72.5833 | 169.4167 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
V-S-MNSP1 Export | VSML_ROC_80 | 72.5 | 81.8333 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | S>>RBTX_WEWT_RBTX | 70.4167 | 54.4167 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_X_SMSC_V1 | 52.3333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V::N_SMSC_S1 | 45.8333 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>BWMP_TWPA_TPRS | 42.0833 | 1.1667 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_X_SMSC_V2 | 35.1667 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | S>>MKRB_TWPA_TPRS | 33.5 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_22 | 33.4167 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo-Templers 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Export | V^^N_DTKV_1 | 30.3333 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 29.3333 | 60.0833 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | S>>X_RBTU+RBTX_14 | 24.4167 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_X_SMSC_O2 | 23.5 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WEWT | 23.3333 | 42.9167 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_DDSM_S1 | 21.8333 | 12.1667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_NILxxx | 21.75 | 25.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
V-S-MNSP1 Export | S>>CNRB_TWPA_TPRS | 21.3333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_16 | 20.0833 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Waterloo East-Waterloo 132 kV on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 19.8333 | 30.1667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-S-MNSP1 Export | F_S+ML_R5 | 19.6667 | 0 | Raise 5 min Service Requirement for SA island for loss of Murraylink | Outage
V-S-MNSP1 Export | V::N_ESTN_TBSE_VE | 19.0833 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
V-S-MNSP1 Export | V>>V_NIL_5 | 16.9167 | 0 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | V^SML_BUDP_3 | 16.5833 | 88.4167 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | S>>RBTX_TWPA_TPRS | 16.0833 | 0 | Out= one Robertstown 275/132kV transforme, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WTTP | 15.1667 | 20 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>CNRB+BRTW_03 | 14.9167 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Blyth West-Munno Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_RBPA_WEWT | 14.1667 | 0.083333 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SETB_S2 | 14.1667 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>NIL_TWPA_TPRS | 14.0833 | 2.5 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>X_RBTU+RBTX_13 | 13.8333 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_23 | 13.5833 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V3 | 13.5833 | 2 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_DDSM_V2 | 13.3333 | 38.6667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_ESTN_TBSE_O1 | 13 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WTTP | 12.75 | 0.16667 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>CNRB_BWPA_WTTP | 11.75 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+RBTX_10 | 11.4167 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line O/S, avoid O/L Templers- Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SETB_V2 | 8.4167 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | S-RBTX1+RBTX2_MLNK | 7.5 | 0 | Out= Robertstown 132/275kV TX1 + Robertstown 132/275kV TX2 O/S, limit import limit into SA on the Murraylink | Outage
V-S-MNSP1 Export | V::N_X_SMSC_V | 6.9167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
V-S-MNSP1 Export | VSML_165 | 6.1667 | 0 | Vic to SA on ML upper transfer limit of 165 MW | Outage
V-S-MNSP1 Export | V::N_DDSM_S2 | 5.9167 | 0.58333 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SETB_V1 | 5.75 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V>>N_NIL_65 | 5.6667 | 0 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 5.0833 | 4.1667 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 5 | 3.5833 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_ESTN_TBSE_VB | 5 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 2 | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_S3 | 4.6667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-S-MNSP1 Export | V::N_ESTN_TBSE_VA | 4.5 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V^^N_UTRV_1 | 3.75 | 0 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V::N_HYSE_V2 | 3.5 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>NWB6022_TX1 | 3.3333 | 0 | Out= North West Bend CB 6022 O/S, avoid O/L North West Bend 275/132kV TX1 on trip of North West Bend 275/132kV TX3, Feedback | Outage
V-S-MNSP1 Export | V::N_HYSE_V1 | 3.25 | 0.66667 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_ESTN_TBSE_VD | 3 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>>V_DDTX_C | 3 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage
V-S-MNSP1 Export | VSML_ZERO | 2.5833 | 20.9167 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | NRM_VIC1_SA1 | 2.4167 | 0.91667 | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | S>>CNRB_MKRB_BWMP | 2.1667 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Blyth West-Blyth Munno Para 275kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Export | V^SML_HOMR_3 | 2 | 0 | Out = Horsham to Murra Warra 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V::N_SMSC_V1 | 1.8333 | 0 | Out = One South Morang 330 kV series capacitor bank, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | S>>BWMP_BRTW_WTTP | 1.6667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage
V-S-MNSP1 Export | VSML_110 | 1.6667 | 0 | Vic to SA on ML upper transfer limit of 110 MW | Outage
V-S-MNSP1 Export | CA_BRIS_52460E76_1 | 1.5 | 0 | Constraint Automation, O/L XFMR T_1@R_TOWN@SA for CTG LS6W on trip of W_LOO - WATE_E 132KV 1 LINE. Generated by STNET[BNECR1] Host BNEREGEEMP1(EMPBRI) | Outage
V-S-MNSP1 Export | V::N_SMSC_SD | 1.5 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V>>N-NIL_HB | 1.5 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
V-S-MNSP1 Export | S>>CNRB+BRTW_01 | 1.4167 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown- Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+HUWT_10 | 1.4167 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 1.3333 | 2 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N-LTUT_G | 1.3333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_RBPA_WTTP | 1.0833 | 0.66667 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+HUWT_11 | 1.0833 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV lineon trip of Robertstown-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+RX+HUSN_14 | 1.0833 | 0 | Out= One Robertstown TX + Robertstown-Tungkillo 275kV line + Hummocks??Snowtown 132 kV line O/S, avoid O/L Waterloo East-Waterloo 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_ESTN_TBSE_V1 | 1.0833 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | VSML_195 | 1.0833 | 0 | Vic to SA on ML upper transfer limit of 195 MW | Outage
V-S-MNSP1 Export | S>>BRTX3_BWMP_WTTP | 1 | 0.91667 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>BWMP_RBTU_WTTP | 1 | 0.58333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_ROSM_O1 | 1 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | #R024613_014_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint S>>DVBG_RBTU_WTTP, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026207_022_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint S>>X_RBPA+RBTX2_22, Effective Date: 19/09/2022, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_RBPA_RBTU | 0.91667 | 0 | Out= Nil, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | #R026373_016_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+RX+HUSN_14, Effective Date: 14/10/2022, Version: 1 | Other
V-S-MNSP1 Export | V::N_JNWG_S1 | 0.83333 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_O1 | 0.83333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | #R025706_006_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R026120_015_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026681_020_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | #R026747_014_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | S>>BWMP_RBTU_RBPA | 0.66667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Robertstown-Para 275kV line on trip of Robertstown -Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>NIL_NWRB1_MWP3RB | 0.66667 | 0 | Out= NIL, avoid O/L Morgan Pipeline 3-Robertstown 132kV line on trip of North West Bend-Roberstown 132kV line, Feedback | NIL
V-S-MNSP1 Export | V>>V_NIL_26 | 0.66667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL
V-S-MNSP1 Export | #R025592_015_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | #R026734_021_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | F_S+ML_R6_2_LB_0 | 0.58333 | 0 | Raise 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage
V-S-MNSP1 Export | S>>X_RBTU+RX+HUSN_13 | 0.58333 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Waterloo-Templers 132 kV line on trip of Robertstown-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HYSE_S1 | 0.58333 | 1.5833 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_HYTR_O2 | 0.58333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | V::N_LTWG_S1 | 0.58333 | 3.5833 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N-NIL_HG | 0.58333 | 2.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | #R024588_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024673_010_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R025419_016_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025466_016_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025615_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_SETB_S2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026501_040_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024588_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024655_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024887_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R025350_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025401_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025611_008_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025611_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025912_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R026136_012_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S>>X_CNRB+RBTX_12, Effective Date: 17/08/2022, Version: 2 | Other
V-S-MNSP1 Export | #R026463_013_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S>>RBTU_RBPA_WEWT, Effective Date: 11/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026463_014_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 11/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026464_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB4_O1, Effective Date: 09/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026506_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R026775_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026775_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R026777_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_135, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_BWMP_TWPA | 0.41667 | 5.0833 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>PARB_RBTU_RBMWP4 | 0.41667 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SETB_S1 | 0.41667 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R024569_026_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024575_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_135, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024582_039_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024655_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VSML_165, Effective Date: 30/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024673_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R025203_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R025241_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025247_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025401_015_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025600_050_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R026120_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026136_020_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S>>X_CNRB+RBTX_22, Effective Date: 17/08/2022, Version: 2 | Other
V-S-MNSP1 Export | #R026138_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026173_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026173_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026192_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S-RBTX1+RBTX2_MLNK, Effective Date: 19/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026302_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026451_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 17/10/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026467_013_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+HUWT_11, Effective Date: 26/10/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026501_040_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R026535_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R026600_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HOMR_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R026722_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026747_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 04/11/2022, Version: 2 | Other
V-S-MNSP1 Export | N>>V_NIL_0X1_60 | 0.33333 | 0 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_HYTR_O1 | 0.33333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | #R024569_026_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024845_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024845_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R025419_016_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025466_016_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025706_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R025707_006_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R026044_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R026128_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>TPRS_BWPA_TWPA, Effective Date: 11/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026138_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026172_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026215_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026373_015_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+RX+HUSN_13, Effective Date: 14/10/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026467_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>X_RBTU+HUWT_10, Effective Date: 26/10/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026600_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_HOMR_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | S>>BRTX3_RBTU_WTTP | 0.25 | 0 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_TWPA_TPRS | 0.25 | 0.91667 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTX_BWPA_WTTP | 0.25 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N_NIL_66_65 | 0.25 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
V-S-MNSP1 Export | V^^N_DDSM_1 | 0.25 | 0 | Out = Dederang to South Morang 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | #R024582_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024622_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>DVBG_RBTU_WTTP, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024626_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>BRDV_BWPA_WTTP, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024626_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>BRDV_RBTU_WEWT, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024681_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024758_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024987_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R025060_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025067_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R025350_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025419_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025466_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025615_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SETB_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025772_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V2, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026027_020_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | #R026177_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026192_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S-RBTX1+RBTX2_MLNK, Effective Date: 19/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026207_022_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>>X_RBPA+RBTX2_22, Effective Date: 19/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026263_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_LTYS_1, Effective Date: 28/09/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026423_040_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R026463_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>RBTU_TWPA_TPRS, Effective Date: 11/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026467_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>>X_RBTU+HUWT_11, Effective Date: 26/10/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026538_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | S>>BRDV_RBTU_WEWT | 0.16667 | 1.75 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>MKRB_BWPA_BRTW | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_BWMP_WTTP | 0.16667 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>TPRS_RBPA_RBTU | 0.16667 | 0 | Out= Templers-Roseworthy 132kV line, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HWCB_V2 | 0.16667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_LTWG_V1 | 0.16667 | 3.0833 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_X_SMSC_Q1 | 0.16667 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-S-MNSP1 Export | V>>SML_NIL_7B | 0.16667 | 0 | Out = Nil, avoid O/L Buangor to Ararat 66kV line for loss of the Ararat to Crowlands 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL
V-S-MNSP1 Export | V>>V_NIL1A_R | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | V>SML_NSWRB_10 | 0.16667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Darlington Point to Balranald (X5) 220 kV line, feedback | NIL
V-S-MNSP1 Export | S>>MKRB_BRTW_WTTP | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>MKRB_BWMP_WTTP | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | #R024613_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>DVBG_BRTW_WTTP, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024622_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>DVBG_RBTU_WTTP, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024626_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>BRDV_RBTU_WTTP, Effective Date: 09/12/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024759_032_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_LTWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024887_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R025516_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025545_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R025707_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WEWT, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R025707_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R025829_022_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>CNRB_TWPA_TPRS, Effective Date: 01/02/2022, Version: 2 | Other
V-S-MNSP1 Export | #R025961_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_UTRV_1, Effective Date: 23/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026090_015_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>DVBL_TWPA_TPRS, Effective Date: 11/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026136_020_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>X_CNRB+RBTX_22, Effective Date: 17/08/2022, Version: 2 | Other
V-S-MNSP1 Export | #R026172_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026177_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026215_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026436_051_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R026463_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>RBTU_RBPA_WTTP, Effective Date: 11/08/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026705_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 07/12/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026722_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
V-S-MNSP1 Export | #R026725_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_O1, Effective Date: 07/12/2022, Version: 1 | Other
V-S-MNSP1 Export | #V-S-MNSP1_RAMP_E_F | 0.083333 | 0 | V-S-MNSP1 <= MAX(0, InitialFlow - 25) (Wt=35) | Other
V-S-MNSP1 Export | N>>V_DBUSS_4 | 0.083333 | 0 | Out = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage Schemes), avoid O/L Dederang H3 330/220kV transformer for loss of Dederang H1 or H2 330/220kV transformer, feedback | Outage
V-S-MNSP1 Export | S>>BRDV_RBTU_WTTP | 0.083333 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>CNRB_RBTU_WTTP | 0.083333 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_RBTX_RBTX_2 | 0.083333 | 0 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL
V-S-MNSP1 Export | S>>PARB_TWPA_TPRS | 0.083333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_05 | 0.083333 | 0 | Out= Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown-Morgan Whyalla 4 (1) on trip of Robertstown-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBPA+RBTX2_13 | 0.083333 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Templers-Roseworthy 132 kV on trip of Templers West-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTU+RX+HUSN_10 | 0.083333 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Templers-Roseworthy 132 kV on trip of Templers West-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_RBTX1_WTHU_02 | 0.083333 | 0 | Out= Robertstown 132/275kV TX1 + Waterloo-Hummocks 132kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage
V-S-MNSP1 Export | V::N_HWRO3_O1 | 0.083333 | 0 | Out = Hazelwood to Rowville No.3 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V::N_HYTR_V2 | 0.083333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-S-MNSP1 Export | V::N_ROSM_V1 | 0.083333 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-S-MNSP1 Export | V>>N-LTYS_CH | 0.083333 | 0.083333 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage
V-S-MNSP1 Export | VSML_VFRB_OFF | 0.083333 | 0 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL
V-S-MNSP1 Export | V^^SML_NIL_3 | 0.083333 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL
V-S-MNSP1 Import | N^^N_NIL_3 | 986.8333 | 709.5 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL
V-S-MNSP1 Import | SVML_ZERO | 543.5833 | 853.8333 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | V^^V_NIL_KGTS | 496.9167 | 153.1667 | Out= Nil, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | NIL
V-S-MNSP1 Import | SVML^NIL_MH-CAP_ON | 463.5 | 282.4167 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL
V-S-MNSP1 Import | V>>V_NIL_18 | 270.1667 | 125.3333 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 112.1667 | 0 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V>>V_NIL_7 | 101.8333 | 55.5 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_27 | 78.4167 | 0 | Out = Nil, avoid O/L Ararat to Waubra 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_9 | 77.3333 | 40.25 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | S>RBTX1_RBTX2_WEMWP4 | 75.4167 | 3.6667 | Out= Robertstown 275/132kV TX1, avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, | Outage
V-S-MNSP1 Import | SVML_ROC_80 | 74.0833 | 100.8333 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | V^^V_MLNK_KGTS | 61.5 | 105.5833 | Out= Murraylink, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | Outage
V-S-MNSP1 Import | S>>X_RBTU+RBTX_15 | 54.3333 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | S>>X_RBPA+RBTX2_06 | 43.6667 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown 275 kV-Tungkillo 275 kV line, Feedback | Outage
V-S-MNSP1 Import | N::N_NIL_63 | 38.8333 | 13 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL
V-S-MNSP1 Import | N>>99F_994_63 | 37 | 0 | Out= Uranquinty to Yanco (99F) 132kV line, avoid O/L Yanco to Wagga330 (994) on trip of Darlington Point to Wagga330 (63) 330kV line, (Note: Option C on OM521) | Outage
V-S-MNSP1 Import | N^^V_CNCW_1 | 36.1667 | 107.4167 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | F_S+ML_L5 | 34.25 | 0 | Lower 5 min Service Requirement for SA island for loss of Murraylink | Outage
V-S-MNSP1 Import | N>>N-DP_TIETX_D | 32.5833 | 0 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (220 KV to 330 kV) on Kerang-Bendigo trip; Feedback | Outage
V-S-MNSP1 Import | S>>CNRB+BRTW_02 | 26.9167 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Claire North 132 to Brinkworth 132 kV line on trip of Mokota-Robertstown 275kV line(this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | SVML_FLT_130 | 25.8333 | 19.1667 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | N^^V_DDSM1 | 18.8333 | 0 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
V-S-MNSP1 Import | N^^V_NIL_1 | 16.8333 | 100.4167 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
V-S-MNSP1 Import | S>NIL_RBMWP3_RBNW1 | 15.1667 | 0 | Out= Nil, avoid O/L Robertstown-North West Bend #1 132kV line on trip of Robertstown-Morgan Pipeline 3-Morgan Pipeline 2-Morgan Pipeline 1-North West Bend 132kV #2 line, Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_24 | 15 | 2.8333 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_23 | 12.1667 | 5.4167 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | V>>NIL_ELML_BAML2 | 11.0833 | 0 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL
V-S-MNSP1 Import | NRM_SA1_VIC1 | 9.75 | 0 | Negative Residue Management constraint for SA to VIC flow | NIL
V-S-MNSP1 Import | N>>994_99F_63 | 9.1667 | 0 | Out= Yanco to Wagga (994) 132kV line, avoid O/L Yanco to Uranquinty (99F) 132kV line on trip of Darlington Point to Wagga (63) 330kV line,[Note: assumed X5 trip scheme disarmed, Wagga-Darlington Pt 132kV Solid)] | Outage
V-S-MNSP1 Import | F_S+ML_L6_2_LB_0 | 7.9167 | 0 | Lower 6 sec Service Requirement for SA island for loss of Murraylink (FFR ZERO) | Outage
V-S-MNSP1 Import | S>>CNRB_MKRB_WEMWP4 | 7.6667 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | N>>V-LTYS_64_7_15M | 4.5 | 0 | Out= Lower Tumut to Yass(3), avoid O/L Lower Tumut to Upper Tumut (64), on trip of Lower Tumut to Canberra (7) ,Feedback | Outage
V-S-MNSP1 Import | S:VS_PA_SVC_570 | 4.25 | 6.3333 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-S-MNSP1 Import | N^^V_CNLT_1 | 4.1667 | 0 | Out = Canberra - Lower Tumut (07) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>>X_RBPA+RBTX2_07 | 3.75 | 0 | Out=Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV, avoid O/L Robertstown 275/132kV TX1 on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), Feedback | Outage
V-S-MNSP1 Import | V>>V_BABU_6 | 3.4167 | 0 | Out = Balranald to Buronga (X3) 220 kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | S>>CNRB+BRTW_04 | 3.25 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth-Templers West 275kV line, avoid O/L Morgan Whyalla 4 -Robertstown 132kV line on trip of Mokota-Robertstown 275kV line(this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | S>>X_RBTU+RBTX_16 | 3.1667 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S, avoid O/L of remaining Robertstown 275/132kV TX on trip of Waterloo East-MWP4-RB 132kV line (this trip MWP4 SF), | Outage
V-S-MNSP1 Import | S>>MKRB_CNRB_WEMWP4 | 3 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Morgan Whyalla 4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage
V-S-MNSP1 Import | S:VS_PA_SVC_620 | 2.75 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage
V-S-MNSP1 Import | N^^V_DPWG_X5_1 | 2.3333 | 4.0833 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | SVML_FLT_150 | 2.0833 | 9.25 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage
V-S-MNSP1 Import | N^^V_SMTXF2_1 | 1.9167 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | N^^V_X_SMF2_SMSC_1 | 1.6667 | 0 | Out = South Morang F2 500/330kV txfmr and both South Morang Series Capacitors, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | N^^V_CNYS_1 | 1.5833 | 0 | Out = Canberra - Yass (9), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>NIL_NWMH1_NWMH2 | 1.5833 | 0.083333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on trip of North West Bend-Monash #1 132kV line, Feedback | NIL
V-S-MNSP1 Import | N>>V_SMDD6 | 1.25 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
V-S-MNSP1 Import | F_S+ML_L60 | 1.1667 | 0 | Lower 60 sec Service Requirement for SA island for loss of Murraylink | Outage
V-S-MNSP1 Import | S:VS_PA_SVC_420 | 1.1667 | 1 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage
V-S-MNSP1 Import | N^^V_DPWG_X5_RVYS_1 | 1 | 0 | Out = Darlington Point to Wagga with line X5 open and Ravine to Yass (2+63) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>VMLMHNW2 | 0.91667 | 0.25 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage
V-S-MNSP1 Import | #R024708_008_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N^^V_CNLT_1, Effective Date: 30/04/2021, Version: 1 | Other
V-S-MNSP1 Import | CA_BRIS_5233A5C6_1 | 0.83333 | 0 | Constraint Automation, O/L XFMR 3H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage
V-S-MNSP1 Import | #R025112_013_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint N^^V_DPWG_X5_1, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Import | N^^V_JNWG_63_X5_1 | 0.75 | 0 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | #R025203_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R025539_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R026044_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 0.66667 | 0.33333 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | S>>X_RBTU+RX+HUSN_15 | 0.66667 | 0 | Out=One Robertstown 275/132kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275 kV line, Feedback | Outage
V-S-MNSP1 Import | #R026506_005_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V^^V_MLNK_KGTS, Effective Date: 16/11/2021, Version: 1 | Other
V-S-MNSP1 Import | N^^V_BADP_1 | 0.5 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>>V_NIL_NIL_RBMW3 | 0.5 | 1.4167 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | #R024987_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R025539_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R026566_021_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint SVML_FLT_130, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R026566_021_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_FLT_130, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | N^^V_LTYS_1 | 0.41667 | 6.3333 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | #R026506_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R026535_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | N>>NIL_DPTX_LV | 0.33333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
V-S-MNSP1 Import | S>V_RBNW_RBMWP3 | 0.33333 | 2.8333 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Import | #R025912_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R025912_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^V_MLNK_KGTS, Effective Date: 16/11/2021, Version: 1 | Other
V-S-MNSP1 Import | CA_SYDS_5233E05E_1 | 0.25 | 0 | Constraint Automation, O/L XFMR T_2@R_TOWN@SA for CTG LSIR on trip of R_TOWN - TUNKIL 275KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage
V-S-MNSP1 Import | N>>V_SMDD3 | 0.25 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the Eildon to Thomastown 220 kV line (flow to South) on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
V-S-MNSP1 Import | V>>V_NIL_14 | 0.25 | 26.75 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | #R025600_022_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DPWG_X5_RVYS_1, Effective Date: 05/07/2022, Version: 1 | Other
V-S-MNSP1 Import | #R025912_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^V_MLNK_KGTS, Effective Date: 16/11/2021, Version: 1 | Other
V-S-MNSP1 Import | #R026233_030_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
V-S-MNSP1 Import | #R026233_030_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
V-S-MNSP1 Import | CA_BRIS_52155A1A_2 | 0.16667 | 0 | Constraint Automation, O/L ELTS_MLTS_220:LMLT:Z:220@ELTS@VIC for CTG LVAI on trip of BATS-MLTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage
V-S-MNSP1 Import | SVML_FLT_125 | 0.16667 | 34.9167 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | V>>V_BUDP_6 | 0.16667 | 0 | Out = Balranald to Darlington Pt (X5) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | #R024569_025_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R024756_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>VMLMHNW2, Effective Date: 21/10/2019, Version: 1 | Other
V-S-MNSP1 Import | #R025975_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S:VS_PA_SVC_420, Effective Date: 07/08/2018, Version: 1 | Other
V-S-MNSP1 Import | N>>N-NIL_996_IN | 0.083333 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL
V-S-MNSP1 Import | S>>RBTX1_NIL_RBTX2 | 0.083333 | 0 | Out= Robertstown 275/132kV TX1, avoid O/L Robertstown 275/132kV TX2 on Nil trip, Feedback | NIL
V-S-MNSP1 Import | SVML_-020 | 0.083333 | 0 | SA to Vic on ML upper transfer limit of -20 MW | Outage
V-S-MNSP1 Import | V>>V_NIL_3_SIPS | 0.083333 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, 5 min line rating, feedback. Swamp if SIPS not available | NIL
V-SA Export | SA_TBSE1 | 138.6667 | 0 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS) Vic-SA Flow = South East Area Load - Local Generation | Outage
V-SA Export | V::N_X_SMSC_O1 | 90.6667 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_X_SMSC_V1 | 72.3333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V:S_600_HY_TEST | 64 | 46.9167 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | V_VS_LB_CAN_50 | 61.6667 | 96.75 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. Constraint swamp out when 2-4 syncons I/S | Outage
V-SA Export | V::S_SETB_TBSE_2 | 60.75 | 30.5833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 54.6667 | 18.1667 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_SMSC_S1 | 45 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_X_SMSC_V2 | 39.25 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 31.6667 | 18.9167 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | V::N_X_SMSC_O2 | 30.4167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | VS_050_DYN | 27.3333 | 11.25 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | V_S_HEYWOOD_UFLS | 23.25 | 110 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC. Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL
V-SA Export | V::S_2SE+PAVC_MAXG | 21.75 | 0.16667 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V_S_NIL_ROCOF | 20.6667 | 326.5833 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Export | V::N_NILxxx | 16 | 34.4167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
V-SA Export | V::N_SETB_S2 | 15.5833 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^S_HYCP | 14.5833 | 0 | Out = NIL, maintain adequate post contingent voltages for loss of a 500kV circuit between Heywood and Moorabool. | NIL
V-SA Export | V>S_460 | 14.4167 | 4.0833 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage
V-SA Export | V::N_BYPASS_HW_SY_V3 | 11.3333 | 2 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_ESTN_TBSE_VE | 8.1667 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
V-SA Export | V::N_SETB_V2 | 7.9167 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V::S_KNPW_MAXG | 7.8333 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA.. | Outage
V-SA Export | V::N_ESTN_TBSE_O1 | 7.5833 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_X_SMSC_V | 6.9167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
V-SA Export | V::N_BYPASS_HW_SY_S3 | 6.8333 | 1.0833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::S_PWSE_MAXG | 5.9167 | 0 | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage
V-SA Export | V::S_2SE+PAVC_SETB | 5.4167 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S(Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage
V-SA Export | V>S_460_DYN | 5.25 | 1 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Export | V::S_SEVC_MAXG | 4.8333 | 0 | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V^^S_SETB_TBSE_2 | 4.75 | 2.0833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::N_SETB_V1 | 4.25 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V_V_HYMO_1 | 4.1667 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line, Limit voltage unbalance at the APD 500 kV bus and Heywood 275 kV bus | Outage
V-SA Export | VS_250 | 4 | 7.8333 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage
V-SA Export | V^^S_SEVC1_SETB | 3.8333 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage
V-SA Export | V::N_HYSE_V2 | 3.5833 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_NIL_SETB_SECP_1 | 3.3333 | 0.16667 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | V::N_HYSE_V1 | 3.1667 | 0.66667 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | S>>NIL_TBTU_TBMO_1 | 3 | 2.6667 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | V::N_SMSC_SD | 3 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::S_SEVC1+PWSE_SETB | 3 | 0 | Out= Either one of the South East SVC+Penola West-South East 132kV (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage
V-SA Export | F_ESTN++HYTR_L60 | 2.75 | 0.083333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::S_BLKRG_MAXG_3 | 2.75 | 0 | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | Outage
V-SA Export | V::S_SEVC1+PWSE_MAXG | 2.75 | 0 | Out= Either one of the South East SVC+Penola West-South East 132kV (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V::S_NIL_TBSE_1 | 2.6667 | 0.33333 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | F_ESTN++HYTR_L6 | 2.5833 | 0.083333 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | V::N_ESTN_TBSE_VB | 2.5 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 2 | Outage
V-SA Export | VS_250_DYN | 2.5 | 6.0833 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | V::N_ESTN_TBSE_VA | 2.4167 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | F_ESTN++HYMO_L60 | 2 | 5.8333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_ESTN++HYMO_L6 | 1.9167 | 1.5833 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | V^^S_PAVC1_SETB | 1.9167 | 0 | Out= Para one SVC(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage
V-SA Export | V::N_SMSC_V1 | 1.8333 | 0 | Out = One South Morang 330 kV series capacitor bank, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | NRM_VIC1_SA1 | 1.75 | 1.3333 | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | V::N_ESTN_TBSE_VD | 1.75 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
V-SA Export | V^^S_2SE+PAVC_MAXG | 1.75 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S(Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V^^S_PAVC1_MAXG | 1.75 | 0.083333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V::N_HYTR_O1 | 1.6667 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::S_HYSE_MG_TPSB2 | 1.25 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (TIPSB2+ DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors I/S). Co-optimised eq TIPSB2 LHS. | Outage
V-SA Export | V^^S_NIL_MAXG_xxx | 1.1667 | 0 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_JNWG_S1 | 1.0833 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_ROSM_O1 | 1.0833 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::S_SEVC1_MAXG | 1 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | S>>TBTU_TBCG_TBMO | 0.91667 | 3 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V::N_SMF2_O1 | 0.91667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::S_HYSE_MG_PPGT1_2 | 0.91667 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors O/S). Co-optimised eq PPGT1 LHS | Outage
V-SA Export | V::S_SEVC1_SETB | 0.91667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage
V-SA Export | V>>S_MOTB_TBCG_TBTU | 0.91667 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V::N_HYTR_O2 | 0.83333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V::S_SETB_MAXG | 0.83333 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with one Black Range series capacitors I/S). | Outage
V-SA Export | #R026120_015_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | V::N_HYTR_V1 | 0.66667 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | #R025615_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_SETB_S2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | V::N_ESTN_TBSE_V1 | 0.58333 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_LTWG_S1 | 0.58333 | 3.5 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_HYSE_MAXG | 0.58333 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R025736_021_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R024742_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V:S_PA_SVC_550, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R025247_014_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R025358_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025611_008_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R025611_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R025930_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025939_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025951_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025957_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025982_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R026105_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::S_SEVC_MAXG, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R026464_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB4_O1, Effective Date: 09/09/2022, Version: 1 | Other
V-SA Export | V::S_HYSE_MG_PPGT1 | 0.41667 | 0 | Out=One Heywood-South East 275kV line O/S; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT1 + DPV trip) in SA (SE Cap Available). (NOTE: with both Black Range series capacitors I/S). Co-optimised eq PPGT1 LHS | Outage
V-SA Export | V^^S_SEVC1_MAXG | 0.41667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R024569_026_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024673_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R025241_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R025247_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R025266_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025589_031_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025589_031_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025710_021_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025710_021_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R026002_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R026120_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R026138_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R026160_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::S_SEVC_MAXG, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R026173_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R026173_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R026177_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R026193_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^S_SEVC1+PWSE_SETB, Effective Date: 21/09/2022, Version: 1 | Other
V-SA Export | #R026451_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O1, Effective Date: 17/10/2022, Version: 1 | Other
V-SA Export | #R026722_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
V-SA Export | F_QNV+HYMO_L6 | 0.33333 | 0.25 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+HYMO_L60 | 0.33333 | 0.33333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | S>>NIL_TBCG_TBTU_1 | 0.33333 | 0 | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL
V-SA Export | V::N_HYSE_S1 | 0.33333 | 1 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_SETB_S1 | 0.33333 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | VS_050 | 0.33333 | 0.5 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage
V-SA Export | #R025219_020_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025219_020_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025287_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025350_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R025545_020_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025545_020_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025736_021_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025742_021_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025742_021_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R026138_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R026172_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | F_QNV++HYTR_L6 | 0.25 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_JNWG_SD | 0.25 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::S_HYSE_MAXG_2 | 0.25 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R024673_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024673_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R024681_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R025350_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R025350_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R025615_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SETB_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R025756_022_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_V_HYMO_1, Effective Date: 01/09/2020, Version: 1 | Other
V-SA Export | #R025772_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V2, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R026177_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R026193_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::S_SEVC1+PWSE_MAXG, Effective Date: 21/09/2022, Version: 1 | Other
V-SA Export | #R026538_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Export | #R026722_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
V-SA Export | #R026725_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLSY_O1, Effective Date: 07/12/2022, Version: 1 | Other
V-SA Export | F_ESTN++HYMO_L5 | 0.16667 | 0.58333 | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | S>>CGTB1_TBTU_TBMO | 0.16667 | 21.1667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::N_HWCB_V2 | 0.16667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_LTWG_V1 | 0.16667 | 3.0833 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_SETB_MG_PPGT2 | 0.16667 | 0 | Out= one South East -Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block (Pelican Pt GT2 + DPV trip) in SA (SE Cap Available). (NOTE: with one Black Range series capacitors I/S. Co-optimised eq PPGT2 LHS | Outage
V-SA Export | #R024569_026_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024759_032_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_LTWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R025210_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R025247_020_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025247_020_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025392_022_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025392_022_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R025516_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R025710_022_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_V_HYMO_1, Effective Date: 01/09/2020, Version: 1 | Other
V-SA Export | #R026067_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R026160_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_SEVC_MAXG, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Export | #R026172_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
V-SA Export | #R026221_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>TBTU_TBCG_TBMO, Effective Date: 11/08/2022, Version: 1 | Other
V-SA Export | #R026221_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>TBTU_TBCG_TBMO, Effective Date: 11/08/2022, Version: 1 | Other
V-SA Export | #R026376_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R026705_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 07/12/2022, Version: 1 | Other
V-SA Export | #R026705_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | F_QNV++HYMO_L6 | 0.083333 | 0.083333 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | S>>MOTB_TBTU_TBCG | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::N_HWRO3_O1 | 0.083333 | 0 | Out = Hazelwood to Rowville No.3 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_HYMO_O1 | 0.083333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::N_HYTR_V2 | 0.083333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
V-SA Export | V::N_ROSM_V1 | 0.083333 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
V-SA Export | V::S_TBCP1_MAXG | 0.083333 | 0 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA | Outage
V-SA Export | V:S_570_OSC_AUTO | 0.083333 | 0 | Out = NIL (Note: with both Black Range series capacitors I/S), Upper transfer limit of 570 MW on VIC to SA on Heywood, Active only when I25 mode cannot be monitored. | NIL
V-SA Import | S:V_PA_SVC_470 | 217.6667 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 470 MW | Outage
V-SA Import | V::N_DDSM_V1 | 187.8333 | 55.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Import | SV_470_DYN | 132.5 | 0 | SA to Victoria on Heywood upper transfer limit of 470 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Import | F_S++HYSE_L60 | 121.75 | 104.25 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
V-SA Import | SV_420_DYN | 97.5833 | 188.4167 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Import | F_S++HYSE_L6_1 | 92.8333 | 17.6667 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | S::V_TBSE_TBSE | 92.25 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | S:V_PA_SVC_420 | 88.1667 | 175.6667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | S:V_PA_SVC_270 | 40.0833 | 45.0833 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage
V-SA Import | SA_TBSE1 | 31.1667 | 0 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS) Vic-SA Flow = South East Area Load - Local Generation | Outage
V-SA Import | S:V_XPAVC_310 | 26 | 54.8333 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 21.25 | 31.0833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-SA Import | V^^V_NIL_SWVIC | 19.1667 | 0 | Out = Nil, manage flow towards Moorabool across Haunted Gully to Moorabool and Mortlake to Moorabool 500kV lines to avoid voltage instability for the loss of Haunted Gully to Moorabool 500kV line and both APD potlines | NIL
V-SA Import | V::N_DDSM_V2 | 15.9167 | 55 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | NRM_SA1_VIC1 | 11.8333 | 0 | Negative Residue Management constraint for SA to VIC flow | NIL
V-SA Import | F_S++HYSE_L5 | 10.5 | 0.25 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
V-SA Import | S:VS_PA_SVC_420 | 8.8333 | 1.3333 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage
V-SA Import | S^^V_SETB_1 | 8.75 | 0 | Out= one South East to Tailem Bend 275kV line, voltage collapse equation Tailem Bend-Keith #2 132kV Line <=135 MW on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage
V-SA Import | #V-SA_RAMP_I_F | 8.1667 | 4.1667 | V-SA >= MIN(-85, InitialFlow + 50) (Wt=35) | Other
V-SA Import | S:VS_PA_SVC_620 | 6.6667 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murraylink upper transfer limit of 620 MW | Outage
V-SA Import | S:V_550_HY_TEST | 5.6667 | 29.1667 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | S:VS_PA_SVC_570 | 5.5 | 3 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-SA Import | S:V_550_HY_TEST_DYN | 4.5 | 13.8333 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | S>>TBTU_CGTB_MOTB | 2.25 | 0 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Mobilong-Tailem Bend 132kV line on trip of Cherry Gardens-Tailem Bend 275kV line, Feedback | Outage
V-SA Import | S>V_460 | 1.5 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW | Outage
V-SA Import | S>>SETB_TBSE_TBKH2_1 | 1.4167 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend-Keith #2 132kV Line on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage
V-SA Import | V>>V_ROTS_TX_2A_R | 1.4167 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Import | S::V_TBSE_TBSE_2 | 1.0833 | 11.9167 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | #R026363_001_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | S>>CGTB1_TUTB_MOTB | 0.91667 | 2.8333 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage
V-SA Import | #R024718_002_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R026653_002_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | S>V_460_DYN | 0.66667 | 0 | SA to VIC on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Import | SV_240_DYN | 0.66667 | 0 | SA to Victoria on Heywood upper transfer limit of 240 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Import | #R024687_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint S>>TBTU_CGTB_MOTB, Effective Date: 01/02/2022, Version: 2 | Other
V-SA Import | #R025401_015_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | S>>V_MOTB_TUTB_CGTB | 0.5 | 0 | Out=Mobilong - Tailem Bend 132kV line; avoid O/L Cherry Gardens -Tailem Bend 275kV on trip Tungkillo -Tailem Bend 275kV line, Feedback | Outage
V-SA Import | SV_240 | 0.5 | 0 | SA to Victoria on VicSA upper transfer limit of 240 MW | Outage
V-SA Import | #R024687_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>>TBTU_CGTB_MOTB, Effective Date: 01/02/2022, Version: 2 | Other
V-SA Import | #R025401_015_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R025825_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R026391_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R024694_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024694_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024700_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024887_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Import | #R026302_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R026586_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint S::V_TBSE_TBSE_2, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | S>>TPRS_RBPA_RBTU | 0.33333 | 0 | Out= Templers-Roseworthy 132kV line, avoid O/L Robertstown-Tungkillo 275kV line on trip of Robertstown-Para 275kV line, Feedback | Outage
V-SA Import | #R024680_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | #R024845_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Import | #R024845_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Import | #R025419_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R025423_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | #R025423_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | #R025466_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R025554_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R025615_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | #R026120_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R026215_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R026515_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | #R026653_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024680_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | #R025060_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R025615_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S::V_TBSE_TBSE, Effective Date: 09/12/2021, Version: 1 | Other
V-SA Import | #R026022_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | #R026238_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>V_460, Effective Date: 07/12/2015, Version: 1 | Other
V-SA Import | #R025335_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R025335_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R025969_008_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R025975_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S:VS_PA_SVC_420, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R026215_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
V-SA Import | #R026391_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | F_ESTN++HYTR_R60 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Raise 60 sec Requirement | Outage
V-SA Import | S>>SETB_TBSE_KHKN_1 | 0.083333 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith-Kincraig 132kV Line on trip of other Tailem Bend-South East 275kV line, (Note: with both SE series caps I/S or O/S) | Outage
VIC1-NSW1 Export | N^^N_NIL_3 | 1311.25 | 1117.5 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL
VIC1-NSW1 Export | V^^N_NIL_1 | 333.6667 | 826.5 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
VIC1-NSW1 Export | N::N_UTRV_2 | 241.1667 | 2.9167 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | V::N_DDSM_V1 | 157 | 52.5833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V^^N_DTKV_1 | 125.4167 | 0 | Out = Dapto - Kangaroo Valley (18) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>V_DDSM_1 | 117.0833 | 86.6667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
VIC1-NSW1 Export | V>>V_NIL_25 | 91.75 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
VIC1-NSW1 Export | V::N_X_SMSC_O1 | 84.0833 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V>>N_NIL_65_66 | 79.25 | 0 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | V::N_X_SMSC_V1 | 72.75 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | N::N_LTYS_2 | 62.0833 | 33.1667 | Out = Lower Tumut-Yass (03), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V^^N_DTMN_1 | 49.8333 | 5.1667 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N::N_RVYS_2 | 47.75 | 0 | Out = Ravine -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | V::N_SMSC_S1 | 43.75 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V^^N_LTYS_1 | 37.5833 | 95.5 | Out = Lower Tumut - Yass (3) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_X_SMSC_V2 | 37.4167 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HA | 34.0833 | 83.3333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | V^^N_DDSM_1 | 32.6667 | 0 | Out = Dederang to South Morang 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_X_SMSC_O2 | 24.8333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_S1 | 21.1667 | 14.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_NILxxx | 20.3333 | 41.6667 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | NIL
VIC1-NSW1 Export | V::N_ESTN_TBSE_VE | 20.25 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 19 | 27.6667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V3 | 18.5 | 1.3333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 17.3333 | 1 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | V::N_SETB_S2 | 16.9167 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V^^N_UTRV_1 | 16.5833 | 0.91667 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_ESTN_TBSE_O1 | 14.5 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | N::N_SDUT_2 | 14.1667 | 30.5 | Out = Upper Tumut-Stockdill (1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 12.4167 | 49.6667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SETB_V2 | 8.3333 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V^^N_DPWG_X5_1 | 7.3333 | 66.75 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S3 | 6.75 | 0.83333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V>>N_NIL_65 | 6 | 0 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V::N_DDSM_S2 | 5.9167 | 0.66667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HYSE_V2 | 5.9167 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | N::N_CNCW_2 | 5.5833 | 16.75 | Out = Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line | Outage
VIC1-NSW1 Export | V::N_X_SMSC_V | 5.3333 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. | Outage
VIC1-NSW1 Export | N>>N-NIL-YS-TX | 5.25 | 0 | Out= Nil, avoid O/L Either of Yass 132/330 Transformers on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | V::N_SETB_V1 | 5.25 | 0 | Out = one South East - Tailembend 275kV line (Black Range series caps I/S), prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_ESTN_TBSE_VA | 4.9167 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_ESTN_TBSE_VB | 4.75 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 2 | Outage
VIC1-NSW1 Export | N>>N-DTSS_20 | 4.5833 | 0 | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
VIC1-NSW1 Export | V^^N_BADP_1 | 4.4167 | 7.8333 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N>>N-NIL_998 | 3.6667 | 2.5 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | N>>AVMA-17_39_11 | 3.5833 | 0 | Out = Avon - Macarthur (17) 330kV line or Kemps Creek-Macarthur (37) 330kV line, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
VIC1-NSW1 Export | V::N_ESTN_TBSE_VD | 3.4167 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 3.3333 | 0.75 | Negative Residue Management constraint for VIC to NSW flow | NIL
VIC1-NSW1 Export | V::N_HYSE_V1 | 3.25 | 1.0833 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_SMSC_SD | 3.0833 | 0 | Out = one South Morang series capacitor, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V^^N_CNYS_1 | 2.6667 | 0.25 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | N>>V-LTYS_64_7_15M | 2.5833 | 0 | Out= Lower Tumut to Yass(3), avoid O/L Lower Tumut to Upper Tumut (64), on trip of Lower Tumut to Canberra (7) ,Feedback | Outage
VIC1-NSW1 Export | N^^N_NIL_1 | 1.6667 | 0 | Out= Nil, northerly flow on line 1,2,3 and 07 cut-set voltage stability limit, Feedback | NIL
VIC1-NSW1 Export | V>>N_051_66_65_R | 1.5 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line,(Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, 9R4 opened, and with 2 Yass Transformer in service - OM521) | Outage
VIC1-NSW1 Export | V^^N_SMF2_1 | 1.5 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>N-NIL_HG | 1.4167 | 3.75 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | N::N_CNSD_2 | 1.25 | 1.3333 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V::N_HYTR_O1 | 1.25 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_JNWG_S1 | 1.25 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | N>>N-DTKV_CTMN | 1.1667 | 0 | Out= Dapto- Kangaroo Valley (18), avoid O/L Crookwell to Bannaby (61) on trip Collector WF to Marulan (4) line, Feedback | Outage
VIC1-NSW1 Export | N>>X-WG5012+TX2_02_L | 1.1667 | 0 | Out = Wagga 330kV CB 5012 (Option 1) + Wagga 330/132kV TX2 O/S, avoid O/L one Yass 132/330kV TX on trip of other Yass 132/330kV TX , Feedback | Outage
VIC1-NSW1 Export | V::N_ESTN_TBSE_V1 | 1.0833 | 0 | SA / ESTN separation between Tailem Bend and South East Sub, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_ROSM_O1 | 1.0833 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_SMSC_V1 | 1.0833 | 0 | Out = One South Morang 330 kV series capacitor bank, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V>>N-LTUT_G | 1.0833 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_2A_R | 1.0833 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | CA_BRIS_5233A5C6_1 | 1 | 0 | Constraint Automation, O/L XFMR 3H@DARL_PT@NSW for CTG LVDL on trip of BETS-KGTS 220KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage
VIC1-NSW1 Export | N>>N-DTMN_39_16 | 1 | 0 | Out = Dapto-Marulan(8), avoid O/L Bannaby to Sydney West (39) on trip of Marulan to Avon (16) line, Feedback | Outage
VIC1-NSW1 Export | #R024610_009_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_68 | 0.91667 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) on trip of Collector to Marulan (4) line, Feedback | NIL
VIC1-NSW1 Export | N>>N-NIL__A_15M | 0.91667 | 0.25 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Stockdill (1) line, Feedback | NIL
VIC1-NSW1 Export | N>>N-NIL__H_15M | 0.91667 | 2.4167 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL
VIC1-NSW1 Export | N>>X-17+76_39_11 | 0.91667 | 0 | Out= Avon to Macarthur (17) and Sydney South to Wallerawang (76), avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | Outage
VIC1-NSW1 Export | N>>NIL_998 | 0.83333 | 0 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | #R024618_009_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R026120_015_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | N>>N-DTMN_08 | 0.75 | 0 | Out = Dapto-Marulan(8), avoid O/L Marulan to Avon (16) on trip of Dapto to Kangaroo Valley (18) line, Feedback | Outage
VIC1-NSW1 Export | V::N_HYTR_O2 | 0.75 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V>>N-LTMS_1 | 0.75 | 1.5833 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Export | V>>N_NIL_66_65 | 0.66667 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
VIC1-NSW1 Export | CA_BRIS_51934522_1 | 0.58333 | 0 | Constraint Automation, O/L BATS_BETS_220:LBET:I:220@BATS@VIC for CTG LVK1 on trip of KMTS - RCTS 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Export | V::N_HYSE_S1 | 0.58333 | 2.3333 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_O1 | 0.58333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | #R024673_010_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025247_014_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025419_016_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025466_016_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025615_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_SETB_S2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | N::N_GRYS_2 | 0.5 | 0 | Out = Gullen Range to Yass (3J), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage
VIC1-NSW1 Export | V::N_HYTR_V1 | 0.5 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_LTWG_S1 | 0.5 | 3 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_26 | 0.5 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL
VIC1-NSW1 Export | #R024887_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025267_021_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025350_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025611_008_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025611_008_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026464_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_HWCB4_O1, Effective Date: 09/09/2022, Version: 1 | Other
VIC1-NSW1 Export | CA_SYDS_51A7040E_1 | 0.41667 | 0 | Constraint Automation, O/L 61:LN61:Z:330@CROOKWF@NSW for CTG LNQT on trip of COLLECWF-MARULAN 4 330KV LINE. Generated by STNET[NORCR1] Host NORREGEEMP4(EMPSYD) | Outage
VIC1-NSW1 Export | V::N_SETB_S1 | 0.41667 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HB | 0.41667 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | NIL
VIC1-NSW1 Export | #R024673_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025241_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025247_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025401_015_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025466_016_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025541_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N::N_SDUT_2, Effective Date: 06/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025787_015_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^N_CNYS_1, Effective Date: 17/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R026120_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V2, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026138_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026173_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026173_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026177_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026302_015_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026722_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
VIC1-NSW1 Export | N>>NIL_DPTX_LV | 0.33333 | 0 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
VIC1-NSW1 Export | V::N_JNWG_SD | 0.33333 | 0 | Out = Jindera to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | #R024569_026_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024845_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024845_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025019_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N::N_SDUT_2, Effective Date: 06/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025280_021_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^N_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025401_015_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025419_016_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025518_015_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^N_CNYS_1, Effective Date: 17/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025615_010_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SETB_V2, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025700_016_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 04/02/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025787_015_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^N_CNYS_1, Effective Date: 17/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R026138_014_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026172_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026451_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_O1, Effective Date: 17/10/2022, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_67 | 0.25 | 1.9167 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | V>>V_NIL1A_R | 0.25 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | #R024569_026_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024569_046_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_JNWG_1, Effective Date: 08/12/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024582_040_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024681_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HWCB_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024887_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025060_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025280_021_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025393_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 04/02/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025401_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 11/05/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025419_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025457_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DTMN_1, Effective Date: 09/12/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025457_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DTMN_1, Effective Date: 09/12/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025772_015_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYMO_V2, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026121_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 11/05/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026177_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026215_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026263_015_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_LTYS_1, Effective Date: 28/09/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026538_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_64 | 0.16667 | 0.33333 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
VIC1-NSW1 Export | N>>NIL_4 | 0.16667 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | V::N_HWCB_V2 | 0.16667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_LTWG_V1 | 0.16667 | 2.5 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_X_SMSC_Q1 | 0.16667 | 0 | Out = both South Morang 330 kV series capacitor banks, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
VIC1-NSW1 Export | V>>N-LTMS_4 | 0.16667 | 0 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L(15m rating) on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | #R024618_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024629_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::N_SDUT_2, Effective Date: 06/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024629_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024759_032_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_LTWG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025073_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_CNLT_1, Effective Date: 03/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025350_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025393_015_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 04/02/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025466_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDSM_S1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025488_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025498_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::N_SDUT_2, Effective Date: 06/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025513_016_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 04/02/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025513_016_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_DTKV_1, Effective Date: 04/02/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025516_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R025518_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_CNYS_1, Effective Date: 17/08/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025541_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R025545_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HYTR_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026172_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V1, Effective Date: 27/04/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026215_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 30/03/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026215_017_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_DDSM_1, Effective Date: 11/02/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026349_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>X-WG5012+TX2_02_L, Effective Date: 04/10/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026451_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 17/10/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026705_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 07/12/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026714_015_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_LTYS_1, Effective Date: 28/09/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026722_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWRO3_O1, Effective Date: 07/12/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026725_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_O1, Effective Date: 07/12/2022, Version: 1 | Other
VIC1-NSW1 Export | #R026754_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::N_UTRV_2, Effective Date: 05/12/2022, Version: 1 | Other
VIC1-NSW1 Export | N>>UTRV-6X_64_1 | 0.083333 | 0 | Out = Ravine-Yass (2) 330kV line outage or Upper Tumut to Ravine (6X) 330kV line O/S, avoid O/L Lower Tumut to Upper Tumut (64) on trip of Upper Tumut to Stockdill (1) line, Feedback | Outage
VIC1-NSW1 Export | V::N_HWRO3_O1 | 0.083333 | 0 | Out = Hazelwood to Rowville No.3 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_HYMO_O1 | 0.083333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, Other than VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V::N_HYTR_V2 | 0.083333 | 0 | Out = Heywood to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 500kV. | Outage
VIC1-NSW1 Export | V::N_ROSM_V1 | 0.083333 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV. | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_3A_R | 0.083333 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V^^N_SDUT_1 | 0.083333 | 27.5833 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Import | N^^V_SM_SCAP_R & N^^V_SM_SCAP_P | 122.6667 | 0 | Out = both South Morang 330 kV series capacitor banks, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 80.25 | 23.75 | Negative Residue Management constraint for NSW to VIC flow | NIL
VIC1-NSW1 Import | N^^V_CNCW_1 | 40 | 113.3333 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W) or Dapto-Kangaroo Valley (18), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_NIL_ARWBBA | 30.6667 | 21.6667 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL
VIC1-NSW1 Import | V>>NIL_ELML_BAML2 | 26 | 0 | Out= Nil, avoid O/L Elaine to Moorabool 220kV line on trip of Ballarat to Moorabool No.2 220kV line, Feedback | NIL
VIC1-NSW1 Import | N^^V_DDSM1 | 22.5833 | 72.4167 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 17.75 | 114.8333 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
VIC1-NSW1 Import | N^^V_CNLT_1 | 5.25 | 0 | Out = Canberra - Lower Tumut (07) 330kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_BADP_1 | 4.75 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N::V_DDSM_MSDD | 3.6667 | 0.91667 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
VIC1-NSW1 Import | N>>V_NIL_0X1_60 | 3.25 | 0 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL
VIC1-NSW1 Import | V>>V_DDTX_C | 2.9167 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage
VIC1-NSW1 Import | N^^V_SMTXF2_1 | 2.4167 | 0.83333 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DPWG_X5_1 | 2.3333 | 4.0833 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_LTWG_1 | 2.25 | 3.6667 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_CNYS_1 | 1.9167 | 0 | Out = Canberra - Yass (9), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_X_SMF2_SMSC_1 | 1.6667 | 0 | Out = South Morang F2 500/330kV txfmr and both South Morang Series Capacitors, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N_V_HV1100 | 1.5 | 0 | Discretionary constraint on transfer from NSW to VIC of 1100 MW on DDTS-NSW cutset | Outage
VIC1-NSW1 Import | N>>V_SMDD6 | 1.4167 | 5.6667 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
VIC1-NSW1 Import | N^^V_MLNK_ARWBBA | 1.3333 | 0 | Out = Murraylink, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | Outage
VIC1-NSW1 Import | N^^V_DPWG_X5_RVYS_1 | 1.1667 | 0 | Out = Darlington Point to Wagga with line X5 open and Ravine to Yass (2+63) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | #R024708_008_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N^^V_CNLT_1, Effective Date: 30/04/2021, Version: 1 | Other
VIC1-NSW1 Import | #R025112_013_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint N^^V_DPWG_X5_1, Effective Date: 20/04/2021, Version: 1 | Other
VIC1-NSW1 Import | N^^V_JNWG_63_X5_1 | 0.75 | 0 | Out = Jindera to Wagga(62) 330kV line, 63 + X5 open, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_MLNK_1 | 0.66667 | 0 | Out = Murraylink, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N::V_DTKV_MSDD | 0.58333 | 0 | Out=Dapto - Kangaroo Valley (18), NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
VIC1-NSW1 Import | N:V_DDSM_BWRG | 0.58333 | 0.083333 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage
VIC1-NSW1 Import | N>>V_SMDD3 | 0.58333 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the Eildon to Thomastown 220 kV line (flow to South) on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
VIC1-NSW1 Import | N>>V-NIL_0X1_60 | 0.5 | 0 | Out= Nil, avoid O/L Buronga to Redcliff (OX1) 220kV line on trip of Jindera to Wodonga(60) 330kV line, Feedback | NIL
VIC1-NSW1 Import | CA_BRIS_52155A1A_2 | 0.41667 | 0 | Constraint Automation, O/L ELTS_MLTS_220:LMLT:Z:220@ELTS@VIC for CTG LVAI on trip of BATS-MLTS1 220KV LINE. Generated by STNET[NORCR2] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Import | N::V_DDSM_UTMS | 0.41667 | 0 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit for trip of Upper Tumut - Murray (65) line | Outage
VIC1-NSW1 Import | N^^V_LTYS_1 | 0.41667 | 9.3333 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N_V_HV1500 | 0.33333 | 0 | Discretionary constraint on transfer from NSW to VIC of 1500 MW on DDTS-NSW cutset | Outage
VIC1-NSW1 Import | V::V_1900 | 0.25 | 0.33333 | Out=Nil, upper limit into Vic of 1900 MW | NIL
VIC1-NSW1 Import | #R025600_022_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DPWG_X5_RVYS_1, Effective Date: 05/07/2022, Version: 1 | Other
VIC1-NSW1 Import | #R026233_030_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
VIC1-NSW1 Import | #R026233_030_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_BADP_1, Effective Date: 16/08/2022, Version: 1 | Other
VIC1-NSW1 Import | #R026424_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_LTWG_1, Effective Date: 16/08/2022, Version: 1 | Other
VIC1-NSW1 Import | CA_BRIS_5120191F_1 | 0.16667 | 0 | Constraint Automation, O/L 0X1:L0X1:I:220@BURONGA@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORVM1] Host BNEREGEEMP1(EMPBRI) | Outage
VIC1-NSW1 Import | CA_BRIS_51201D29_1 | 0.16667 | 0 | Constraint Automation, O/L 0X1:L0X1:I:220@BURONGA@NSW for CTG LXPF on trip of WOTS-JINDERA 060 330KV LINE. Generated by STNET[NORVM1] Host BNEREGEEMP1(EMPBRI) | Outage
VIC1-NSW1 Import | N>>V-NIL_0X1 | 0.16667 | 0.5 | Out= NIL, avoid O/L Buronga to Red cliffs (OX1) on Nil trip, Feedback | NIL
VIC1-NSW1 Import | N::V_NIL_MSDD | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | NIL
VIC1-NSW1 Import | N:V_NIL_BWRG | 0.083333 | 0 | Out=Nil, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | NIL
VIC1-NSW1 Import | N>>N-NIL_996_IN | 0.083333 | 0 | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL
VIC1-NSW1 Import | N>>V_NIL_65_66 | 0.083333 | 0 | Out = Nil, avoid Upper Tumut to Murray(65) using 15 mins rating O/L on Lower Tumut to Murray(66) trip; (Note: constraint is swamped out if TL 64 is O/S) | NIL
VIC1-NSW1 Import | N>>V_NIL_66_65 | 0.083333 | 0 | Out = Nil, avoid Lower Tumut to Murray(66) using 15 mins rating O/L on Upper Tumut to Murray(65) trip; (Note: Swamped when TL 64 is O/S) | NIL
VIC1-NSW1 Import | N_V_HV1150 | 0.083333 | 0 | Discretionary constraint on transfer from NSW to VIC of 1150 MW on DDTS-NSW cutset | Outage

## Outages
Constraint Set ID | 2022 Days | 2021 Days | Description
N-LS_VC1 | 330.0208 | 9.2431 | Out= Lismore SVC
S-PA_VC1 | 323.0764 | 305.9444 | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
V-X_SMSC | 304.7674 | 0 | Outage = Both South Morang 330kV series capacitors
N-MBTE_1 | 153.1424 | 146.9965 | Out= one Directlink cable
Q-KEP-HYB_25MW | 122.5972 | 0 | Kennedy Energy Park upper limit of 25MW
V-MOORBWF_150_0SWT | 116.6146 | 365 | Moorabool Wind Farm upper limit of 150 MW. Limit Moorabool wind farm to 0 MW if any turbine online from the Moorabool wind farm - South (Cluster 2)
V-KIAMAL_SC_220CB | 110.4132 | 0.41319 | Outage = Kiamal Syncon, 7422B and RC2A open
I-QN_1200_TEST | 107.5799 | 0 | Qld to NSW on QNI limited to 1200 MW for testing QNI minor augmentation
V-X_HWRO_12_R | 107.5694 | 201.6007 | Out = Hazelwood to Rowville No. 1 and No. 2 220 kV lines, radial mode
N-BANYS_9GM | 90.6424 | 13.2049 | Out = Bango 999 WF to Yass 132kV line(9GM)
N-LDNC_81 | 84.8924 | 6.5 | Out= Liddell to Newcastle (81)
V-KIAMAL_SC | 75.9236 | 0.61806 | Outage = Kiamal Syncon, 7422B and RC2A closed
Q-KEP-HYB_20MW | 75.7812 | 0 | Kennedy Energy Park upper limit of 20MW
S-SE_VC1 | 71.7986 | 4.6076 | Out= Either one of South East SVC O/S (Note: with both Black Range series caps I/S)
N-RVYS_2 | 70.434 | 0.33333 | Out= Ravine to Yass (2) 330kV line
Q-810_PARALLEL_CLOSE | 70.2118 | 29.9549 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV network intact
Q-NE_275BUS_CB | 67.6042 | 0.80208 | Out = one 275kV bus or one or more CB (8342,8222) at H11 Nebo
N-BANCO_999 | 66.2292 | 30.4722 | Out= Bango 999 WF to Cowra 132kV line (999)
I-NQ_600_TEST | 59.9965 | 0 | NSW to QLD on QNI limited to 600 MW for testing QNI minor augmentation
Q-TRSP_832 | 59.4896 | 0 | Out= 832 H18 Tarong to H2 South Pine 275 kV feeder
V-DBUSS_T | 59.1597 | 56.1458 | Outage = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage schemes)
N-TARALGAWF_ZERO | 54.1597 | 1.5035 | Taralga WF upper limit of 0 MW
V-DDSM | 52.2708 | 41.8715 | Out = Dederang to South Morang (DDTS-SMTS) 330 kV line
F-TAS_NTH_STH_RISK | 48.7743 | 0 | Credible risk of TAS North / South separation between Palmerston and Liapootah/Waddamana. Ensures a distribution of TAS dispatched FCAS between Nth and Sth TAS
I-NQ_700_TEST | 47.5764 | 0 | NSW to QLD on QNI limited to 700 MW for testing QNI minor augmentation
F-T_STH_NYR_RECLASS | 44.125 | 0 | TAS South local FCAS requirement for loss of all Nyrstar load - 20 MW reclassified as a credible contingency. See market notice 102360
T-X_LIPM | 43.8924 | 0 | Out = Both Palmerston to Waddamana (tee) to Liapootah 220kV lines. Both lines must ben open at least at Palmerston.
N-AVMA_17 | 42.0278 | 3.9236 | Out = Avon to Macarthur (17) 330kV line
Q-CHWR | 39.0382 | 0 | Out= 877(H32 Chalumbin to H39 Woree) 275kV line or Woree (H39) 275/132kV 1T Transformer
N-BANGOWF2_ZERO | 38.0868 | 13.1458 | Bango 999 wind farm upper limit of 0 MW
S-PA_VC1_BC-2CP | 37.6979 | 30.2743 | Out= One Para SVC (Note: with both Black Range series caps O/S)
T-BLINK_NGZ | 37.6667 | 50.6424 | Manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. DS only
Q-NESTM | 37.5972 | 0 | Out = One H11 Nebo to H35 Strathmore 275KV line (822 / 878 / 8845)
S-SECB6611_10 | 33.8194 | 0.53125 | Out= Either one of South East CB 6611 Or 6605 Or 6610 Or 6604 O/S (Note: with both Black Range series caps I/S)
Q-MIMR_9907_9908 | 27.5278 | 0 | Out= 9907 or 9908 R4 Millmerran to H14 Middle Ridge 330kV feeder, or H14 Middle Ridge 330/275 kV #4 or #5 transformer
N-WLTX | 26.5764 | 0 | Out = one of the Wellington 132/330kV Transformers
I-MURRAYLINK | 25.7396 | 0 | Out = Murraylink, (NOTE: ONLY INVOKE when MLK is O/S on both SA & VIC ends OR when MLK is open on either ends)
S-SE_VC1_BC-2CP | 25.1528 | 0 | Out= One South East SVC (Note: with both Black Range series caps O/S)
Q-BCST | 24.2847 | 9.5625 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line
V-BRYBWF_ZERO | 24.1632 | 0.57986 | Berrybank Wind Farm upper limit of 0 MW
I-VS_050 | 23.1667 | 13.7639 | Victoria to SA on VicSA upper transfer limit of 50 MW
N-LTYS_03 | 22.7917 | 19.316 | Out= Lower Tumut - Yass (03) 330kV line
S-RB_TX1 | 22.6424 | 7.6493 | Out =Robertstown #1 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
F-T-BBGT | 21.4479 | 0 | Out=One Bell Bay - Georgetown 110 kV line, all four Bell Bay GTs on remaining 110 kV line, FCAS requirements
Q-BLUEGSF1_ZERO | 20.3819 | 0 | Bluegrass Solar Farm upper limit of 0 MW
Q-HACL | 20.25 | 0.045139 | Out= 8810 or 8811 H24 Calvale to S2 Halys 275 kV feeder
N-MNTX3 | 19.934 | 0 | Out = Marulan 132/330kV TX3
Q-CPWO_813 | 19.5729 | 15.4167 | Out = H67 Calliope River to H5 Woolooga 275kV line (813) feeder Tee Gin Gin (section 1 or 2 or both)
N-X_MBTE_3 | 18.9271 | 13.8021 | Out= all three Directlink cables
Q-H13RS_SVC | 17.8924 | 0.58681 | Out= H13 Ross 275 kV SVC
F-T-GTTE | 17.3993 | 21.5694 | Out = one George Town to Temco 110kV line OR loss of both Georgetown to Temco 110 kV lines or all Temco load declared credible
S-CNHL_HAL | 16.4167 | 0 | Out = Canowie Hallett 275kV line
S-X_BWMP+MPPA | 15.7049 | 7.3646 | Out = Blyth West- Munno Para 275kV line and Munno Para-Para 275kV (i.e. with Blyth West CB8002 OPEN & Blyth West tripping scheme I/S)
Q-WUBI | 15.1806 | 32.4236 | Out= 865 or 866 H40 Wurdong to H8 Boyne Island 275kV feeder, CQ-SQ voltage stability limit, 2008/2009 implementation
S-BC_CP | 15.0139 | 5.3472 | Out = either one of Black Range series capacitors bypassed,
S-PLN_CB6210 | 15.0035 | 3.4062 | Out=Port Lincoln CB6210
Q-X_BSNE_BC | 14.9618 | 0 | Out = 8846/8847/834 (H20 Broadsound to H11 Nebo)+ H10 Bouldercombe / H20 Broadsound bus
Q-KEP-HYB_30MW | 14.7847 | 0 | Kennedy Energy Park upper limit of 30MW
V-HYTX_M12 | 14.691 | 22.1736 | Out = Heywood (HYTS) M1 or M2 500/275 kV txfmr
V-SMSC | 14.2049 | 0.03125 | Outage = one South Morang 330kV series capacitor
S-CNRB | 13.9062 | 0 | Out = Canowie-Robertstown 275kV line (i.e. Line ONLY O/S, with associated line CBs I/S), (Note: both Black Range series capacitors I/S)
S-MKRB | 13.8924 | 2.375 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps I/S)
S-HALWF2_0 | 13.4618 | 2.4965 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW
Q-KEP-HYB_ZERO | 13.3646 | 0 | Kennedy Energy Park upper limit of 0MW
I-MUTE_758 | 12.9444 | 0.125 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line
V-HY_500BUS | 12.5243 | 3.816 | Out = Heywood (HYTS) No. 1 or No. 2 500 kV bus.
Q-X_BSNE_CHWR_BC | 12.066 | 0 | Out = 8846/8847/834 (H20 Broadsound to H11 Nebo)+ 877 or 8902 (H32 Chalumbin to H39 Woree to H60 Walkamin)+ with or without H10 Bouldercombe/H20 Boradsound bus
T-WIND_NTH_100 | 12.066 | 0 | Discretionary 100 MW upper limit on TAS North Wind Generation
S-DVTX | 12.0278 | 9.3819 | Out= One Davenport 275/132kV TX O/S
T-CTHLWF_100 | 11.9132 | 0 | Wild Cattle Hill Wind Farm upper limit of 100 MW
N-MORBOR | 11.7917 | 0 | Out= Any one 132kV feeder between Moree to Boggabri East (96M,9UH,9UJ) 132kV line. Applicable with or without 96M offloaded during 9UH or 9UJ outage.
V-HYTX_M3 | 11.3264 | 0.13542 | Out = Heywood (HYTS) M3 500/275 kV txfmr
N-ARTW_85 | 11.2917 | 4.5938 | Out = Armidale to Tamworth (85) line
S-TBSE | 11.2604 | 0.40972 | Out - one South East-Tailembend 275kV line (Note: with one Black Range series caps I/S)
S-X_RBPA+RBTX2 | 11.2361 | 0 | Out= Robertstown-Para 275 kV line + Robertstown TX2 275/132 kV (Note: with both Black Range series caps I/S)
Q-BCRG_811 | 11.2222 | 0 | Out = 811 (H10 Bouldercombe to H73 Raglan) 275kV line
Q-X_CPST_BC_NE | 10.9549 | 0 | Out = 812+ 848 (H67 Calliope River - H29 Stanwell) 275kV line + one or both of (H11 Nebo bus + H10 Bouldercombe bus)
T-FARC1 | 10.7049 | 0.83681 | Out=Farrell-Reece 1 220KV line
I-MUTE_757 | 10.6319 | 0.069444 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line
S-X_SEVC2+PAVC | 10.1875 | 1.5382 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S, (Note: with both Black Range series caps I/S)
T-CSGO | 9.9826 | 4.0347 | Out = One Chapel St to Gordon 220kV line
F-T-CSGO | 9.9826 | 4.0347 | Out = one Chapel St to Gordon 220kV line, FCAS Requirements
S-ACMA | 9.9132 | 0 | Out= Angas Creek-Mannum 132kV line(Note: With/Without associated line CBs I/S); (NOTE: with both Black Range series capacitors I/S); (Note: This offloads Mannum-Adelaide Pumping Station PVs 2 & 3)
N-MORIV | 9.7882 | 0 | Out= Moree to Inverell (9U2) 132kV line
S-X_RBTU+RBTX2 | 9.6875 | 0 | Out= One Robertstown TX 275/132 kV + Robertstown-Tungkillo 275kV line O/S; (Note: with both Black Range Series caps I/S)
N-YNWG_994_C | 9.1979 | 4.0382 | Out= Yanco to Wagga (994) 132kV line; X5 trip scheme Disarmed, 132kV parallel Solid. Option C on OM521
N-WLWO_79 | 9.0382 | 4.2326 | Out = Wellington to Wollar (79) 330kV line
Q-BSLV | 8.9826 | 0 | Out = 833 or 850 H20 Broadsound - H15 Lilyvale 275kV line
N-DP_TIETX | 8.9375 | 2.5139 | Out= DarlingtonPt 330/220/33 kV tie Tx (#3 or #4)
N-URYC_99F_C | 8.7986 | 0 | Out= Uranquinty to Yanco (99F) 132kV line; X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
N-BU-SCON1 | 8.6944 | 6.3403 | Out= Buronga Syncon 1, SCON1 is associated with Finley SF
S-X_PLN_02 | 8.6076 | 0 | Out = Yadnarie to Port Lincoln line, Port Lincoln PS islanded
N-TAPM_964 | 8.5451 | 1.8229 | Out = Taree to Port Macquarie (964) 132kV line
Q-KEP-HYB_27MW | 8.4931 | 0 | Kennedy Energy Park upper limit of 27MW
N-MOON_94T | 8.4271 | 0 | Out = Molong to Orange North (94T) 132kV line
V-ELAINEWF_ZERO | 8.2569 | 99.1806 | Elaine Wind Farm upper limit of 0 MW
S-LFTI | 8.1354 | 0.91319 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S)
S-SE_132KV_BUS | 7.9132 | 41.9514 | Out = ONLY One South East 132 kV bus (i.e. either East or West 132kV bus WITH/WITHOUT associated CBs)
Q-X_NEVC_BCNE_RSWR | 7.3611 | 0 | Out = Nebo SVC+ 821 (H10 Bouldercombe - H11 Nebo) 275kV line + 858 or 857 or two series feeders between H13 Ross and H39 Woree
Q-EMLV_6067 | 7.3125 | 1.5729 | Out= 6067 Emerald to Lilyvale 66kV line with Emerald SF offloaded
T-WIND_100 | 7.2222 | 0 | Discretionary 100 MW upper limit on TAS Wind Generation. NOTE - Direction may also be required to manage this limit, if constraint violates
N-CG2_ZERO_E | 7.1215 | 0 | Direction to zero for Colongra #2 for Dispatch and Predispatch and NOT PASA
N-CG4_ZERO_E | 7.1215 | 0 | Direction to zero for Colongra #4 for Dispatch and Predispatch and NOT PASA
N-CG3_ZERO_E | 7.1215 | 0 | Direction to zero for Colongra #3 for Dispatch and Predispatch and NOT PASA
N-URANQ13_ZERO_E | 7.0764 | 0 | Direction to zero for Uranquinty #3 for Dispatch and Predispatch and NOT PASA
N-URANQ12_ZERO_E | 7.0764 | 0 | Direction to zero for Uranquinty #2 for Dispatch and Predispatch and NOT PASA
N-URANQ14_ZERO_E | 7.0764 | 0 | Direction to zero for Uranquinty #4 for Dispatch and Predispatch and NOT PASA
N-URANQ11_ZERO_E | 7.0764 | 0 | Direction to zero for Uranquinty #1 for Dispatch and Predispatch and NOT PASA
F-SA_ESTN_ISLE_REG | 7.0729 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS) - Regulation FCAS Requirements
SA_ESTN_LG_ISLE | 7.0729 | 0 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS)
N-SITHE01_ZERO_E | 6.8924 | 0 | Direction to zero for Sithe for Dispatch and Predispatch and NOT PASA
SA_ISLE_LB_FFR_ZERO | 6.8785 | 0 | SA / Eastern separation with Lake Bonney battery and MOPS NOT CONNECTED to SA island (i.e. Lake Bonney battery remains connected to VIC region) - To provide FFR outside of 4 hours contract
S-TORRB3_ZERO_E | 6.8715 | 0 | Direction to zero for Torrens Island B #3 for Dispatch and Predispatch and NOT PASA
S-TORRB2_ZERO_E | 6.8715 | 0 | Direction to zero for Torrens Island B #2 for Dispatch and Predispatch and NOT PASA
Q-WR_VC | 6.8576 | 3.4201 | Out= H39 Woree 132 kV SVC
N-CG1_ZERO_E | 6.7847 | 0 | Direction to zero for Colongra #1 for Dispatch and Predispatch and NOT PASA
Q-STBS | 6.5903 | 0.23958 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
V-NPS_ZERO_E | 6.5174 | 0 | Direction to zero for Newport for Dispatch and Predispatch and NOT PASA
V-JLA02_ZERO_E | 6.4688 | 0 | Direction to zero for Jeeralang A2 for Dispatch and Predispatch and NOT PASA
V-JLA04_ZERO_E | 6.4688 | 0 | Direction to zero for Jeeralang A4 for Dispatch and Predispatch and NOT PASA
V-JLA01_ZERO_E | 6.4514 | 0 | Direction to zero for Jeeralang A1 for Dispatch and Predispatch and NOT PASA
N-SHGEN_ZERO_E | 6.4236 | 0 | Direction to zero for Shoalhaven for Dispatch and Predispatch and NOT PASA
V-JLB01_ZERO_E | 6.3715 | 0 | Direction to zero for Jeeralang B1 for Dispatch and Predispatch and NOT PASA
V-JLB02_ZERO_E | 6.3715 | 0 | Direction to zero for Jeeralang B2 for Dispatch and Predispatch and NOT PASA
V-JLB03_ZERO_E | 6.3715 | 0 | Direction to zero for Jeeralang B3 for Dispatch and Predispatch and NOT PASA
S-KNPW | 6.3021 | 3.434 | Kincraig to Penola West 132kV O/S, (Note: with both Black Range series caps I/S)
V-MCKAY1_ZERO_E | 6.2118 | 0 | Direction to zero for McKay Creek for Dispatch and Predispatch and NOT PASA
V-DARTM1_ZERO_E | 6.1458 | 0 | Direction to zero for Dartmouth for Dispatch and Predispatch and NOT PASA
I-T_V_BL_ZERO_E | 6.1424 | 0 | Direction to zero for Basslink (Tas to Vic) for Dispatch and Predispatch and NOT PASA
Q-X_BCBS_CHWR_BC | 5.9965 | 0 | Out = 820 (H20 Broadsound to H10 Bouldercombe)+ 877 or 8902(H32 Chalumbin to H39 Woree to H60 Walkamin)+ with or without H10 Bouldercombe/H20 Boradsound bus
S-X_PAVC2+SEVC | 5.9306 | 0.086806 | Out = Para SVC 1 and 2 & one South East SVC (Note: with both Black Range series caps I/S)
S-PWSE | 5.7951 | 1.3229 | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S)
N-WNMR_991 | 5.75 | 0 | Out = Wagga North to Murrumburrah (991) 132kV line
Q-PWSP_808 | 5.7326 | 1.2014 | Out= 808 (H2 South Pine to H9 Palmwoods) 275 kV feeder (132 and 110 kV parallel between South Pine and Woolooga closed)
I-HYSE | 5.691 | 1.0938 | Outage = Heywood to South East 275kV line (NOTE: with both Black Range series caps I/S)
V-STOCKYH_ZERO | 5.6806 | 16.9479 | Stockyard Hill wind farm upper limit of 0 MW
S-PPCCGT_ZERO_E | 5.6806 | 0 | Direction to zero for Pelican Point for Dispatch and Predispatch and NOT PASA
S-X-RBTX1+6616+6573 | 5.6701 | 0.26736 | Out =Robertstown North 275kV Bus (this offloads Robertstown TX1) O/S, (NOTE:with RBTX1 132kV CBs 6005 & 6188 I/S)
Q-WARWARSF1 | 5.566 | 0.28819 | Out = 33kV feeder from T58 Warwick to Warwick SF1
Q-COLTX | 5.4028 | 10.3021 | Out = Collinsville North T1 or T2 132/33 kV transformer
Q-RSCH | 5.316 | 0.020833 | Out= 857 or 858 (H13 Ross to H32 Chalumbin) 275kV line with 132 kV network between Ross and Woree NOT split
Q-X_RSWR_BC_NE | 5.2847 | 0 | Out = 858 or 857 or two series feeders between H13 Ross and H39 Woree + one or both of (H11 Nebo bus + H10 Bouldercombe bus)
S-BRTX3 | 5.2153 | 3.5174 | Out= Brinkworth 275/132kV TX3 transformer (with/without associated CBs 6530 & 6528& 6093 & 6068 OPEN).
Q-SMSPL | 5.0764 | 0.26042 | Out = 7457 (H35 Strathmore to T242 Springlands) 132kV line O/S
S-PATW | 5.0625 | 0.72222 | Out = Para - Templers West 275kV line
T-X_LIPM_WACB | 5.0486 | 0 | Out = Both Palmerston to Waddamana (tee) to Liapootah 220kV lines, with associated 220kV CB at WA O/S
F-I_ML_APD | 5.0382 | 8.9375 | Out=Nil, Dymanic FCAS for APD Load Event
Q-810_PARALLEL_OPEN | 5.0035 | 0 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV and 110kV network open
V-KM_TX_220CB | 4.9965 | 0.30208 | Outage of one Kiamal 220/33 kV Transformer, associated 220kV CB open
V-LNGS1_ZERO_E | 4.9757 | 0 | Direction to zero for Laverton North #1 for Dispatch and Predispatch and NOT PASA
V-LNGS2_ZERO_E | 4.9757 | 0 | Direction to zero for Laverton North #2 for Dispatch and Predispatch and NOT PASA
V-VPGS5_ZERO_E | 4.8299 | 0 | Direction to zero for Valley Power GT #5 for Dispatch and Predispatch and NOT PASA
V-VPGS2_ZERO_E | 4.8299 | 0 | Direction to zero for Valley Power GT #2 for Dispatch and Predispatch and NOT PASA
V-VPGS3_ZERO_E | 4.8299 | 0 | Direction to zero for Valley Power GT #3 for Dispatch and Predispatch and NOT PASA
V-VPGS6_ZERO_E | 4.8299 | 0 | Direction to zero for Valley Power GT #6 for Dispatch and Predispatch and NOT PASA
S-MKRB_BC-2CP | 4.8056 | 0 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps O/S)
N-SHPUMP_ZERO_E | 4.7361 | 0 | Direction to zero for Shoalhaven Pump for Dispatch and Predispatch and NOT PASA
N-BANGOWF1_ZERO | 4.6528 | 0 | Bango 973 wind farm upper limit of 0 MW
N-LDTM_82_OPEN | 4.5625 | 2.1667 | Out= Liddell to Tomago (82), Redbank to Kurri 132kV loop opened
V-VPGS4_ZERO_E | 4.5243 | 0 | Direction to zero for Valley Power GT #4 for Dispatch and Predispatch and NOT PASA
S-X_SEVC1+PWSE | 4.5243 | 0 | Out= Either one of the South East SVC O/S+Penola West-South East 132kV O/S (NOTE: With both Black Range series capacitors I/S)
N-WALGR_BAT_L_ZERO | 4.5069 | 0.23611 | Wallgrove Battery (Load Component) upper limit of 0 MW
N-WALGR_BAT_G_ZERO | 4.5069 | 0.23611 | Wallgrove Battery (Generation Component) upper limit of 0 MW
N-TUMUT3_ZERO_E | 4.4965 | 0 | Direction to zero for Tumut 3 for Dispatch and Predispatch and NOT PASA
N-SNOWYP_ZERO_E | 4.4514 | 0 | Direction to zero for Snowy Pumps for Dispatch and Predispatch and NOT PASA
S-MOTB | 4.434 | 0 | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S)
V-ROSM | 4.4236 | 0.60764 | Outage = Rowville to South Morang 500kV line
S-X_CNRB+BRTW | 4.4062 | 0 | Out= Canowie-Robertstown 275kV line + Brinkworth- Templers West 275kV line
N-X_AVMA_SSWW | 4.3438 | 0 | Out= Avon to Macarthur (17) and Sydney South to Wallerawang (76) 330kV lines
S-MY_BUS | 4.3299 | 0 | Outage = Mayura 132kV Bus outage (Note: this offloads both Mayura 33/132kV TX1 and TX2)
S-RBPA | 4.3125 | 16.3507 | Out= Robertstown - Para 275 kV line (Note: with both Black Range series caps I/S)
Q-X_BCBS_BSNE_CHWR | 4.3021 | 0 | Out = 820 (H20 Broadsound to H10 Bouldercombe)+ 8846/8847/834 (H20 Broadsound to H11 Nebo)+ 877 or 8902(H32 Chalumbin to H39 Woree to H60 Walkamin)
Q-X_NESTM+BCST | 4.2569 | 0 | Out = One H11 Nebo to H35 Strathmore 275KV line (822 / 878 / 8845) and 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275 kV line
I-BL_ZERO | 4.1667 | 3.1042 | Limit Basslink to zero in either direction
V-DDTX2 | 3.9306 | 0 | Outage = Dederang No.2 330/220kV transformer
V-MORTLK12_ZERO_E | 3.9028 | 0 | Direction to zero for Mortlake #2 for Dispatch and Predispatch and NOT PASA
V-MORTLK11_ZERO_E | 3.9028 | 0 | Direction to zero for Mortlake #1 for Dispatch and Predispatch and NOT PASA
S-RBTU | 3.8854 | 2.125 | Out= Robertstown - Tungkillo 275 kV line (Note: Line ONLY O/S with associated line CBs I/S); (NOTE: with both Black Range series caps I/S)
N-FLUR-99A-A | 3.6875 | 15.6424 | Out = Finley to Uranquinty (99A), X5 trip scheme armed and Wagga - Darlington point parallel solid, option a on OM521
Q-MARYRSF1_10MW | 3.6354 | 0 | Maryrorough Solar Farm upper limit of 10 MW
S-MTM_0 | 3.6111 | 0 | Discretionary upper limit for Mt Millar windfarm generation of 0 MW
Q-YARANSF1_37MW | 3.5868 | 0 | Yarranlea Solar Farm upper limit of 37 MW
V-HYTR | 3.4896 | 0.11806 | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line
N-WRWSF_ZERO | 3.3924 | 2.5972 | Upper limit of zero MW on total generation of White Rock wind and solar farms
I-VS_250 | 3.3333 | 8.1875 | Victoria to SA on VicSA upper transfer limit of 250 MW
N-DEFI_9R3_C | 3.3194 | 4.7222 | Out= Finley to Deniliquin (9R3); X5 Trip Scheme Disarmed, 132 kV parallel Solid, option c OM521
S-QPS5_ZERO_E | 3.2743 | 0 | Direction to zero for Quarantine #5 for Dispatch and Predispatch and NOT PASA
N-X_LTYS_MNYS | 3.2535 | 0 | Out = 3 (Lower Tumut to Yass) 330kV line and 5 (Marulan to Yass) 330kV line
Q-X_WOPW_CPWO2_CL | 3.2222 | 0 | Out = 810 (H5 Woolooga to H9 Palmwoods) 275kV line+ 813 (H67 Calliope River to H5 Woolooga) 275kV lines with 132kV and 110kV network between Woolooga to Palmwoods network closed
N-BANYS_9GL | 3.1424 | 0.28819 | Out = Bango973 WF to Yass 132kV line(9GL)
N-DTSS_11 | 3.0174 | 2.5764 | Out = Dapto to Sydney South (11) 330kV line
S-HUWT | 2.9479 | 2.3194 | Out= Hummocks-Waterloo 132kV line
Q-RRSF1_ZERO | 2.9306 | 1.2118 | Ross River solar farm upper limit of 0 MW
N-TWNR_968 | 2.9201 | 0 | Out= 968 (Tamworth to Narrabri) 132 kV Line
V-HYMO | 2.9062 | 2.4375 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line
S-OSB-AG_ZERO_E | 2.8472 | 0 | Direction to zero for Osborne for Dispatch and Predispatch and NOT PASA
Q-BRAEMAR2_ZERO_E | 2.7118 | 0 | Direction to zero for Braemar #2 for Dispatch and Predispatch and NOT PASA
N-GOONSF1_ZERO_INV | 2.6667 | 0 | Goonumbla solar farm upper limit of 0 MW and 0 Inverter
Q-BRAEMAR3_ZERO_E | 2.6562 | 0 | Direction to zero for Braemar #3 for Dispatch and Predispatch and NOT PASA
N-CNYS_9 | 2.625 | 0.44792 | Out = Canberra - Yass (9)
Q-BRAEMAR6_ZERO_E | 2.566 | 0 | Direction to zero for Braemar #6 for Dispatch and Predispatch and NOT PASA
Q-BSNE | 2.5312 | 12.25 | Out = 8846 or 8847 (H20 Broadsound -H11 Nebo) 275kV feeder
N-SDUT_1 | 2.5243 | 13.4097 | Out = Stockdill to Upper Tumut (1) 330kV line
T-CTHLWF_ZERO | 2.5 | 1.8403 | Wild Cattle Hill Wind Farm upper limit of 0 MW
Q-STR_KBWF_60 | 2.4167 | 0 | Limit Kaban to 60MW for system strength requirement
N-DPWG_63_X5 | 2.4062 | 10.9653 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
S-WP_0 | 2.3924 | 0 | Discretionary upper limit for Wattle Point windfarm generation of 0 MW
N-BABU | 2.2535 | 5.1076 | Out = Balranald to Buronga (X3) 220kV line
N-PKWL_94K | 2.2396 | 57.9861 | Out = Parkes to Wellington (94K) 132kV line (Note: Entire line segment between Parkes-Suntop T-Wellington O/S)
N-X-AR-LS_VC1 | 2.1736 | 0 | Out = Armidale SVC and Lismore SVC
Q-BRAEMAR7_ZERO_E | 2.1319 | 0 | Direction to zero for Braemar #7 for Dispatch and Predispatch and NOT PASA
Q-WIV1_ZERO_E | 2.1146 | 0 | Direction to zero for Wivenhoe #1 for Dispatch and Predispatch and NOT PASA
Q-WIV2_ZERO_E | 2.1146 | 0 | Direction to zero for Wivenhoe #2 for Dispatch and Predispatch and NOT PASA
Q-BARCALDN_ZERO_E | 2.0139 | 0 | Direction to zero for Barcaldine for Dispatch and Predispatch and NOT PASA
Q-CLWU | 1.9826 | 6.9931 | Out = 871 H24 Calvale to H40 Wurdong 275kV line
Q-MSTUART1_ZERO_E | 1.9792 | 0 | Direction to zero for Mt Stuart #1 for Dispatch and Predispatch and NOT PASA
Q-MSTUART2_ZERO_E | 1.9792 | 0 | Direction to zero for Mt Stuart #2 for Dispatch and Predispatch and NOT PASA
Q-YABULU_ZERO_E | 1.9757 | 0 | Direction to zero for Yabulu for Dispatch and Predispatch and NOT PASA
F-I_ML_APD_LOAD | 1.8958 | 5.3299 | Out=Nil, Dynamic FCAS for APD Load Event, excluding Portland WF
I-HYSE_BC-2CP | 1.8819 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with one/both Black Range series caps O/S)
S-BLBF | 1.8472 | 0.41667 | Out = Belalie - Bluff 275kV line (i.e. Bluff WF <=0 MW)
S-DRYCGT3_ZERO_E | 1.8229 | 0 | Direction to zero for Dry Creek #3 for Dispatch and Predispatch and NOT PASA
N-FINLYSF1_ZERO_INV | 1.809 | 0.43056 | Finley solar farm upper limit of 0 MW and 0 Inverter
S-DRYCGT2_ZERO_E | 1.7812 | 0 | Direction to zero for Dry Creek #2 for Dispatch and Predispatch and NOT PASA
S-DRYCGT1_ZERO_E | 1.7431 | 0 | Direction to zero for Dry Creek #1 for Dispatch and Predispatch and NOT PASA
Q-NQ_SEMI_RAMP_ZERO | 1.7257 | 0 | Ramp North Qld semi-scheduled generators to zero and hold at zero.
Q-LVMIDSF | 1.6875 | 0.43403 | Out = 6065 (H15 Lilyvale to Middlemount SF) 66kV feeder
S-BARKIPS1_ZERO_E | 1.6458 | 0 | Direction to zero for Barker Inlet for Dispatch and Predispatch and NOT PASA
N-X_MBTE_2 | 1.6146 | 10.066 | Out= two Directlink cables
Q-KWF1_ZERO | 1.5903 | 0 | Kaban Wind Farm upper limit of 0 MW
N-ARTW_86 | 1.5868 | 13.1528 | Out = Armidale to Tamworth (86) line
N-ARSR_8E | 1.5833 | 1 | Out= Armidale Sapphire (8E) line
N-DMSR_8J | 1.5799 | 4.441 | Out= Dumaresq to Sapphire (8J) line
N-CRWF1_ZERO | 1.5764 | 1.8333 | Crudine Ridge wind farm upper limit of 0 MW
T-HA_TX | 1.559 | 0 | Out = one Hadspen 220/110kV transformer
N-LTWG_RADIAL | 1.5382 | 5.1424 | Out= Lower Tumut - Wagga (051) line, (Note: Assumed Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service)
T-LIPM | 1.5312 | 0.77083 | Out = Liapootah to Waddamana to Palmerston 220kV line, with associated 220kV CB I/S at Waddamana
S-NWRB | 1.5139 | 10.4375 | Out= Robertstown-North West Bend #1 132kV line
S-DVBL | 1.5035 | 0 | Out = Davenport - Belalie 275kV line (Note: with both Black Range series caps I/S)
Q-NQ_275BUS_CB | 1.5 | 0.53819 | Out = one 275kV Bus or one or more 275kV CB at north of Calvale and Calliope River resulting loss of two 275kV feeders in the next contingency.
V-DDMB | 1.4861 | 138.9097 | Out=Dederang to Mount Beauty 220kV line
N-CNSD_3C | 1.4826 | 4.559 | Out= Canberra to Stockdill (3C) line
S-X_RBTX1+WTHU | 1.4792 | 0 | Out= Robertstown 132/275kV TX1 + Waterloo-Hummocks 132kV line
N-X_TW_330_BUS3-5 | 1.4792 | 0.36111 | Out= Tamworth No.3 and No.5 330kV bus
V-ROTX_R | 1.4722 | 19.0312 | Outage = Rowville 500/220kV (A) transformer, Radial
S-BLNBH_0 | 1.441 | 0.41667 | Out = Belalie - North Brown Hill 275kV line O/S (i.e. North Brown Hill WF <= 0 MW)
N-ARIV_96N | 1.4201 | 1.8819 | Out = Armidale to Inverell (96N) 132kV line
Q-CLBWS_8891_8892 | 1.4201 | 0 | Out = 8891 or 8892 (H77 Columboola to H76 Wandoan South) 275kV line
Q-ISHW_M022 | 1.4167 | 0 | Out = M022 (T131 Isis to Howard Tee Childer SF) 66kV feeder
N-WELLSF1_ZERO | 1.3785 | 6.3229 | Wellington solar farm upper limit of 0 MW
S-MHNW_2 | 1.3576 | 3.9236 | Out = Monash to North West Bend line 2, (Note: Murraylink runback scheme can be I/S or O/S)
S-AGLHAL_P_ZERO_E | 1.3264 | 0 | Direction to zero for Hallett GT for Dispatch and Predispatch and NOT PASA
N-X_94_96 | 1.3194 | 0 | Out= Newcastle to Tomago (94) and Newcastle to Warith West (96)
S-SNUG1_ZERO_E | 1.3194 | 0 | Direction to zero for Snuggery for Dispatch and Predispatch and NOT PASA
S-POR01_ZERO_E | 1.2986 | 0 | Direction to zero for Port Lincoln #1 and #2 for Dispatch and Predispatch and NOT PASA
S-POR03_ZERO_E | 1.2986 | 0 | Direction to zero for Port Lincoln #3 for Dispatch and Predispatch and NOT PASA
S-X_PA_VC_2 | 1.2847 | 15.2639 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S)
S-QPS4_ZERO_E | 1.2569 | 0 | Direction to zero for Quarantine #4 for Dispatch and Predispatch and NOT PASA
S-QPS1_ZERO_E | 1.2569 | 0 | Direction to zero for Quarantine #1 for Dispatch and Predispatch and NOT PASA
S-QPS3_ZERO_E | 1.2569 | 0 | Direction to zero for Quarantine #3 for Dispatch and Predispatch and NOT PASA
S-QPS2_ZERO_E | 1.2569 | 0 | Direction to zero for Quarantine #2 for Dispatch and Predispatch and NOT PASA
V-SMTS_BYPASS_HW_SY | 1.2361 | 0.79514 | Outage = SMTS 500kV bus or CB outages or SMTS bus bypass that creates risk of HWTS-SMTS and SMTS-SYTS combined line trip, Radial or Parallel
N-CROOKWF2_ZERO | 1.2361 | 0 | Crookwell wind farm upper limit of 0 MW
N-AR_TX | 1.2292 | 15.0312 | Out= Armidale No.3 or 6 330/132kV transformer
N-BADP | 1.2049 | 5.1146 | Out = Balranald to Darlington Point (X5) 220kV line
V-X_SMTXF2_SMSC_R | 1.1875 | 0 | Out = South Morang F2 500/330kV txfmr and both South Morang Series Capacitors, radial mode
N-ARDM_8C | 1.1597 | 4.3542 | Out= Armidale to Dumaresq (8C) line
N-X_LS_VC1_967_96L | 1.1597 | 0 | Multiple outage of Lismore SVC and 967 (Koolkhan to Lismore) and 96L(Lismore to Tenterfield) 132kV lines. Lismore load radial on TL 89
Q-X_CPST_BC_NE_RSWR | 1.1562 | 0 | Out = 812+ 848 (H67 Calliope River - H29 Stanwell) 275kV line + 858 or 857 or two series feeders between H13 Ross and H39 Woree+ H11 Nebo bus and/or H10 Bouldercombe bus
Q-KMBG_7184 | 1.1285 | 27.6979 | Out= 7184 Kamerunga Barron Gorge PS 132kV line
S-DC_CBG3 | 1.1285 | 0.15278 | Outage of Dry Creek 66kV CB G3, DRYCGT3<=0
N-X_TWNR_MORNR | 1.125 | 0 | Out= 968 (Tamworth to Narrabri) and 96M(Narrabri to Moree) 132kV line
S-RBPA_BC-2CP | 1.1076 | 0.92361 | Out= Robertstown - Para 275 kV line (Note: both Black Range series caps O/S)
Q-X_BCST_NE | 1.0556 | 0 | Out = 848 or 849 (H10 Bouldercombe - H29 Stanwell) 275kV line + Nebo SVC
S-CNRB_BC-2CP | 1.0521 | 0 | Out = Canowie-Robertstown 275kV line (i.e. Line ONLY O/S, with associated line CBs I/S), (Note: both Black Range series capacitors O/S)
V-MLSY_NOEMTT_R | 1.0417 | 3.5903 | Out = One Moorabool to Sydenham 500 kV line, EMTT scheme not armed, Radial mode
Q-X_BCNE_BC_NE_CHWR | 1.0382 | 0 | Out = 821 (H10 Bouldercombe to H11 Nebo) 275kV line + 877 or 8902(H32 Chalumbin to H39 Woree to H60 Walkamin)+ Nebo SVC/SVC CB + with or without H10 Bouldercombe bus
Q-LVDS_2 | 1.0069 | 0 | Out =7150/2 (H15 Lilyvale to T35 Dysart tee Norwich Park) 132kV line section 2 open at Dysart end
N-CNLT_07 | 1.0035 | 0.22222 | Out = Canberra - Lower Tumut (07) 330kV line
S-SNAPPER1_ZERO_E | 0.95833 | 0 | Direction to zero for Snapper Point for Dispatch and Predispatch and NOT PASA
Q-KEP-HYB_15MW | 0.93403 | 0 | Kennedy Energy Park upper limit of 15MW
N-LDTW_84 | 0.89236 | 20.316 | Out = Liddell to Tamworth (84) 330kV line
N-TW_330_BUS1 | 0.89236 | 3.1389 | Out= Tamworth No.1 330kV bus
Q-X_CLWU+BCST | 0.87847 | 0 | Out= 871 (H24 Calvale to H40 Wurdong) 275kV line and 848 or 849 (H10 Bouldercombe to H29 Stanwell) 275kV line
Q-LV_275_BUS_TX | 0.83333 | 0 | Out = Lilyvale (H15) 275kV Bus no 1 or no 2 and/or Lilyvale 275/132 kV transformer T1 or T2
N-GITN_96R | 0.75694 | 2.8715 | Out= Glen Innes to Tenterfield (96R) line
S-DLN_BUS | 0.67361 | 0.54167 | Out = Dalrymple North 33kV Bus or Dalrymple-Dalrymple North 33kV line
S-X_LFPP+PGTX | 0.65972 | 0 | Out = Pelican Point to Lefevre 275kV line(Note: with both Black Range series capacitors I/S)+one Parafield Gardens West 66/275kV TX , trip of Pelican Point - Parafield Gardens West 275kV line resulting in loss of Pelican & Snapper PT PS a credible event.
I-LTMS | 0.65972 | 1.5799 | Out= Lower Tumut - Murray (66) line
Q-YARANSF1_ZERO | 0.65625 | 0.28125 | Yarranlea Solar Farm upper limit of 0 MW
N-WLMP_72 | 0.64583 | 0 | Out = Mt_Piper to Wellington (72) 330 kV line
Q-EMERASF1_ZERO | 0.63889 | 0.33681 | Emerald Solar Farm upper limit of 0 MW
V-HYCB_204_205 | 0.63194 | 0.41319 | Out = Heywood (HYTS) 500 kV CB 204 or 205
S-LADBROK1_ZERO_E | 0.62153 | 0 | Direction to zero for Ladbroke Grove #1 for Dispatch and Predispatch and NOT PASA
S-TORRB4_ZERO_E | 0.62153 | 0 | Direction to zero for Torrens Island B #4 for Dispatch and Predispatch and NOT PASA
N-X_ARKK_CH_CB892A | 0.61806 | 11.8924 | 966 (Armidale to Koolkhan) 132kV line O/S and Coffs Harbour CB 892A opened - Arrangement 1 - see OM521
SA_LG_ISLE_FFR0_70M | 0.60417 | 0 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS) - 70 MW Metro Option - No FFR
Q-X_NQ_275_FDR_SVC | 0.60417 | 0 | Out = one 275 kV feeder between Calvale /Calliope River and Ross and Ross SVC or Woree SVC
F-T-GO_CB_C752 | 0.60069 | 0.35417 | Out= Gordon CB C752, FCAS Requirements
Q-KENSF1_ZERO | 0.59722 | 0 | Kennedy Solar Farm upper limit of 0MW
Q-KENWF1_ZERO | 0.59722 | 0 | Kennedy Wind Farm upper limit of 0MW
V-HWCB4 | 0.59375 | 0.038194 | Outage = Hazelwood to Cranbourne No.4 500kV line
S-IBR_1800 | 0.58681 | 0 | Discretionary upper limit of 1800 MW for SA non-synchronous generation
N-ARGI_96T | 0.57986 | 2.2743 | Out= Armidale to Glen Innes (96T) line
S-DLBAT-G_0 | 0.56597 | 0.055556 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW
S-DLBAT-L_0 | 0.56597 | 0.055556 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW
V-EL_BUS2 | 0.54861 | 0.52083 | Out = Elaine No.2 220kV bus
V-HOTS_SVC | 0.54514 | 0.72569 | Out = Horsham 220kV SVC
Q-HASMME_RAMP_ZERO | 0.52431 | 0 | Ramp Haughton, Sun Metals, Kaban and Mt Emerald generators to zero and hold at zero.
Q-SMHAU | 0.52083 | 1.1701 | Out = 879 (H35 Strathmore to H91 Haughton) 275kV line
N-KKLS_967 | 0.51389 | 0.61458 | Out= Koolkhan to Lismore (967) 132kV line
V-HWRO3 | 0.50694 | 0 | Outage = Hazelwood to Rowville No.3 500kV line
S_DV-RB2_070 | 0.47569 | 0 | Discretionary upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 70 MW
Q-COL_CBEB05Q00 | 0.47222 | 0 | Out = Collinsville North 33kV bus coupler CB EB05Q00
Q-ORNCLB_8893 | 0.42708 | 0 | Out = 8893 (H78 Orana to H77 Columboola) 275kV line
N-WRWF1_ZERO | 0.41667 | 0.26736 | White Rock WF upper limit of 0 MW
N-X_MMSW+RGSW | 0.40278 | 0 | Out= Munmorah-Sydney West (26) and Regentville-Sydney West (38) 330kV lines
S-X_RBTU+RBTX2+HUSN | 0.39931 | 0 | Out=One Robertstown 275/132 kV TX + Robertstown-Tungkillo 275kV line + Hummocks-Snowtown 132 kV line O/S, (Note: with both Black Range Series caps I/S)
N-MOLNGSF1_ZERO | 0.39931 | 0 | Molong solar farm upper limit of 0 MW
V-KGTS_SVC | 0.39583 | 3.4201 | Out = Kerang 220kV SVC
V-X_WETS_BTX | 0.39236 | 0.45139 | Out = Wemen 220/66kV B1 and B2 txfmr
V-NV_HV1500 | 0.38542 | 0 | Discretionary constraint on transfer from NSW to VIC of 1500 MW on DDTS-NSW cutset
V-KG_WE_RC | 0.38542 | 3.9167 | Outage = Kerang to Wemen to Red Cliffs 220 kV line section, entire line section
S-BRDV | 0.37847 | 2.8368 | Out = Brinkworth - Davenport 275 kV line
F-TAS_NTH_STH_ISLE | 0.37847 | 0 | TAS North / South separation between Palmerston and Liapootah/Waddamana
N-JNWG_RADIAL | 0.375 | 0 | Outage = Jindera - Wagga (62) line, Wagga-Yass 132kV network Split, X5 opened, 63 open, and with 2 Yass Transformer in service
S-BRTW | 0.375 | 2.2951 | Out= Brinkworth- Templers West 275kV line
N-MPWW_ONE | 0.37153 | 5.0104 | Outage of Mt. Piper to Wallerawang (70 or 71) 330kV line
I-BCDM_ONE | 0.36458 | 4.9028 | Out = one Bulli Creek to Dumaresq (8L or 8M) line
S-DC_CBG2 | 0.35069 | 0.27083 | Outage of Dry Creek 66kV CB G2, DRYCGT2<=0
F-S_LBBAT-G_ZERO | 0.34722 | 0 | Lake Bonney Battery (Generation Component) FCAS <= 0MW
F-S_LBBAT-L_ZERO | 0.34722 | 0 | Lake Bonney Battery (Load Component) FCAS <= 0MW
Q-CHCR | 0.34722 | 0 | Out = Charters Towers to Cape River 66kV line
S-X_WTP+DALR_ISLAND | 0.34375 | 0 | Out= Yorke Peninsula 132kV network islanded (i.e. island formed between Hummocks-Androssan West- Dalrymple 132kV network) and disconnected from rest of SA network,(Note:Wattle Point Wind Farm and Dalrymple Battery operating in islanded mode)
F-S_LG1_ZERO | 0.34375 | 0 | Ladbroke Grove Unit1 FCAS <= 0MW
F-S_LG2_ZERO | 0.34375 | 0 | Ladbroke Grove Unit2 FCAS <= 0MW
Q-WDCLB_8890 | 0.33681 | 0 | Out = 8890 (S5 Western Downs to H77 Columboola) 275kV line
S-SNPT_0 | 0.31944 | 0 | Out = Snapper Pt PS = 0MW
F-I_TL_0700 | 0.31944 | 0 | FCAS Lower Requirements for a NEM Network Event, TL = 700
S-DVEM | 0.31597 | 0.37153 | Out = Davenport - Emeroo #1 132kV line (Note: With/Without associated line CBs)
S-X_RBTX1+RBTX2 | 0.3125 | 0 | Out= Robertstown 132/275kV TX1 + Robertstown 132/275kV TX2 O/S
S-X_RBTU+HUWT | 0.30903 | 0 | Out= Robertstown-Tungkillo 275kV line + Hummocks-Waterloo 132 kV line O/S (NOTE: with both Black Range series caps I/S)
Q-ROMA_8_ZERO_E | 0.29861 | 0 | Direction to zero for Roma #8 for Dispatch and Predispatch and NOT PASA
Q-WDORN_8889 | 0.29861 | 0 | Out = 8889 (S5 Western Downs to H78 Orana) 275kV line
Q-ROMA_7_ZERO_E | 0.29514 | 0 | Direction to zero for Roma #7 for Dispatch and Predispatch and NOT PASA
N-PK_TX | 0.28819 | 3.059 | Out = One Parkes 132/66kV Transformer
N-LTUT_64_15M | 0.28125 | 1.6354 | Out= Lower to UpperTumut (64), 15/30_min ratings for 65, 66 lines auto-switch on prior loading
Q-OKYTX4 | 0.27778 | 0.20486 | Out= Oakey 110/33kV transformer (T4)
S-LK_CB8020_CB8018 | 0.27778 | 0 | Out = Mt Lock 275 kV CB8020 or CB8018 (Note:both Black Range series capacitors I/S)
I-CTRL_ISSUE_ML | 0.27431 | 0.16667 | DC Link Control Issue Constraint for Murraylink
Q-KIDKIDSF_7455 | 0.26736 | 0.069444 | Out = 7455 (T77 Kidston to Kidston SF) 132 kV Feeder
S-TBTU | 0.26736 | 0.26389 | Out= Tailem Bend - Tungkillo 275kV line (Note: WITH/WITHOUT associated line CBs I/S), (NOTE: with both Black Range series caps I/S)
N-FINLYSF1_ZERO | 0.26389 | 15.8229 | Finley solar farm upper limit of 0 MW
N-X_MOON_WLTX | 0.26042 | 0 | Out = 94T (Molong to Orange North) 132kV line and one of the Wellington 123/330kV Transformer
I-CTRL_ISSUE_TE | 0.26042 | 0.083333 | DC Link Control Issue Constraint for Terranora
Q-RGBYRSF1_ZERO | 0.24653 | 0.28819 | Rugby Run Solar Farm upper limit of 0 MW
Q-LVCM | 0.24653 | 0.74653 | Out =7153 (H15 Lilyvale to T71 Clermont) 132kV line
T-LIPM_PMWA_N-3 | 0.24306 | 0 | Out = Nil, simultaneous loss of all 220 and 110 kV transmission lines between Palmerston and Waddamana declared credible
Q-KEP-HYB_01MW | 0.23958 | 0 | Kennedy Energy Park upper limit of 1MW
S-CRK_20 | 0.23264 | 0 | Discretionary upper limit for Cathedral Rocks windfarm generation of 20 MW
N-AR_330_BS5 | 0.23264 | 1 | Out= Armidale No.5 330kV bus
Q-ISTX | 0.22222 | 1.2465 | Out = Isis T2 132/66 kV transformer
Q-OKYTX3 | 0.21181 | 3.3056 | Out= Oakey 110/33kV transformer (T3)
I-SV_240 | 0.20833 | 0 | SA to Victoria on VicSA upper transfer limit of 240 MW
N-GIWR-9UG | 0.20139 | 0.61458 | Out = Glen Innes to White Rock (9UG) 132kV line
S-CGTB1 | 0.20139 | 1.7049 | Cherry Gardens to Tailem Bend 275kV line O/S (NOTE: with both Black Range series caps I/S)
N-WG-CB5012+WGTX2 | 0.18056 | 0 | Out = Wagga 330kV CB 5012 (Option 1) + Wagga 330/132kV TX2 O/S, (Note: 132kV network between Darlington Pt and Wagga assumed intact)
S-RB_TX2 | 0.17361 | 11.4618 | Out = Robertstown #2 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
Q-KEP-HYB_11MW | 0.15972 | 0 | Kennedy Energy Park upper limit of 11MW
S-TBCP1 | 0.15625 | 5.3299 | Out = Tailem Bend 275kV capacitor bank (Note: with both Black Range series Caps I/S);
S-NWB_CB6022 | 0.15278 | 0.072917 | North West Bend CB6022 ONLY O/S, Murraylink runback scheme I/S or O/S, Murraylink sever scheme I/S or O/S (NOTE: DO NOT INVOKE if Murraylink Interconnector is O/S)
T-CTHLWF_020 | 0.15278 | 0 | Wild Cattle Hill Wind Farm upper limit of 20 MW
S_DV-RB2_DYNAMIC | 0.14931 | 0 | Discretionary DYNAMIC upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= MAXG SA(i.e.function X_SA_MAXG_ST_DS)
T-FARC2 | 0.14583 | 0 | Out=Farrell-Reece 2 220KV line
Q-LVTX | 0.14236 | 0.19444 | Out = Lilyvale 275/132 kV transformer T1 or T2
N-WRWSF1_ZERO_INV_WT | 0.13542 | 0 | White Rock wind and solar farm upper limit of 0 MW, 0 Inverter, 0 wind turbine
Q-WIVPUMP1_ZERO_E | 0.13542 | 0 | Direction to zero for Wivenhoe Pump #1 for Dispatch and Predispatch and NOT PASA
Q-WIVPUMP2_ZERO_E | 0.13542 | 0 | Direction to zero for Wivenhoe Pump #2 for Dispatch and Predispatch and NOT PASA
I-ML_ZERO | 0.13542 | 42.8299 | Limit Murraylink to 0 MW in either direction (Note: assumed Murraylink remains I/S and capable of Var support on BOTH ends of the interconnector)
S-NWCB6022+6023 | 0.13194 | 0 | Out = North West Bend 132 kV circuit breakers CB6022 and CB6023(Note: this takes out North West Bend-Monash #2 132kV line).(Note: for Murraylink runback scheme I/S or O/S and Sever scheme I/S or O/S)
Q-BRAEMAR5_ZERO_E | 0.13194 | 0 | Direction to zero for Braemar #5 for Dispatch and Predispatch and NOT PASA
F-I_MG_0850 | 0.125 | 0 | FCAS Raise Requirements for a Generation Event, MG = 850
Q-COLNVSF1_ZERO | 0.12153 | 0.14931 | Collinsville solar farm upper limit of 0 MW
S-SNOW_N+S_210 | 0.11458 | 0 | Discretionary upper limit for Snowtown North and South Windfarms 210 MW
Q-NQ_SEMI_ZERO | 0.10764 | 0 | Limit all Northern Qld semi-scheduled generators to zero
Q-DDPS1_ZERO_E | 0.10417 | 0 | Direction to zero for Darling Downs GT for Dispatch and Predispatch and NOT PASA
I-VT_100 | 0.10069 | 0 | Vic to Tas on Basslink upper limit of 100 MW
S-NWRB2 | 0.097222 | 2.0069 | Out = North West Bend to Robertstown No.2 132kV line O/S
S-X_DVLK_LKCN_BC-2CP | 0.097222 | 0 | Out = Davenport-Mt Lock-Canowie 275kV line (Note:both Black Range series capacitors O/S)
V-BUHO | 0.097222 | 0 | Out = Bulgana to Horsham 220kV line
T-NWSD | 0.086806 | 0.37847 | Out= Norwood - Scottsdale 110kV direct line OR Scottsdale 110kV CB A752
V-HOMR | 0.079861 | 0 | Out = Horsham to Murra Warra 220kV line
I-VT_000 | 0.076389 | 0 | Vic to Tas on Basslink upper limit of 0 MW
F-N_LIDDELL_REG_ZERO | 0.076389 | 0 | Liddell (all units) raise and lower regulation <=0 MW
F-N_MTPIPER_REG_ZERO | 0.072917 | 0 | Mt Piper (all units) raise and lower regulation <=0 MW
F-N_BAYSWTR_REG_ZERO | 0.072917 | 0 | Bayswater (all units) raise and lower regulation <=0 MW
Q-WARWSF2_16 | 0.069444 | 0 | Warwick Solar Farm 2 upper limit of 16 MW
S-SA_DVRB_GEN_0300 | 0.069444 | 0 | Discretionary upper limit for SA generation connected at Davenport and between Davenport-Robertstown 275kV lines of 300 MW.
F-N_ERARING_REG_ZERO | 0.069444 | 0 | Eraring (all units) raise and lower regulation <=0 MW
N-X_63_X5_RVYS | 0.069444 | 0 | Out = Darlington Point to Wagga (63) 330kV line (Note: with line X5 open) and Ravine to Yass (2) 330kV line
V-NV_HV1100 | 0.059028 | 0 | Discretionary constraint on transfer from NSW to VIC of 1100 MW on DDTS-NSW cutset
S-TBSE_BC-2CP | 0.055556 | 2.4688 | Out - one South East-Tailembend 275kV line (Note: with both Black Range series caps O/S)
N-WRSF1_ZERO | 0.055556 | 0 | White Rock solar farm upper limit of 0 MW
Q-BSNE_834 | 0.052083 | 0 | Out = 834 (H20 Broadsound -H11 Nebo) 275kV feeder
N-WR_TTS | 0.048611 | 0.29167 | Out = White Rock Generation Transfer Trip Scheme
Q-KSP1_ZERO | 0.048611 | 1.9549 | Kidston solar farm upper limit of 0 MW
S-LB2_0 | 0.045139 | 0 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW
Q-CRCRE_6383 | 0.045139 | 0 | Out = Cape River to Cape River East 66kV line
S-LB3_0 | 0.045139 | 0 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW
N-MOREESF1_ZERO_INV | 0.041667 | 0.26389 | Moree Solar Farm upper limit of 0 MW and 0 Inverter
Q-WOOLGSF1_ZERO | 0.041667 | 0 | Woolooga Solar Farm upper limit of 0 MW
Q-BCNE_821 | 0.038194 | 0.31597 | Out = 821 275kV fdr H10 Bouldercombe - H11 Nebo
N-FLML_9R4_DISARMED | 0.038194 | 0 | Out = Finley to Mulwala (9R4) or Mulwala to Corowa(997/2) or Corowa to Albury (997/1) And Finley Transfer Trip Scheme Disarmed
V-BA_EL_ML | 0.034722 | 0.27431 | Out = Ballarat to Elaine to Moorabool 220kV line
S_DV-RB2_050 | 0.034722 | 0 | Discretionary upper limit on for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 50 MW
I-SVML_-020 | 0.03125 | 0 | SA to Vic on ML upper transfer limit of -20 MW
S-TPRS | 0.03125 | 0.27083 | Out= Templers-Roseworthy 132kV line
I-VT_050 | 0.024306 | 0 | Vic to Tas on Basslink upper limit of 50 MW
S-X_CNRB+RBTX1 | 0.017361 | 0 | Out=Canowie-Robertstown 275kV line + Robertstown 275/132kV #1 TX O/S;(Note:with both Black Range series cap I/S)
S-SNOW_N+S_130 | 0.017361 | 0 | Discretionary upper limit for Snowtown North and South Windfarms 130 MW
S-SNOW_N+S_190 | 0.017361 | 0 | Discretionary upper limit for Snowtown North and South Windfarms 190 MW
N-IVWR-9U4 | 0.017361 | 0.73611 | Out = Inverell to White Rock (9U4) 132kV line
Q-MEWF1_ZERO | 0.013889 | 0.19792 | Mt Emerald Wind Farm upper limit of 0 MW
S-IBR_LB_600 | 0.013889 | 0 | Discretionary upper limit of 600 MW for SA non-synchronous generation excluding Lake Bonney 1,2,3 and Canunda
I-T_V_BL_GT_300_E | 0.013889 | 0 | Direction to greater than 300 MW for Basslink (Tas to Vic), for Predispatch
Q-KA_1TX | 0.010417 | 7.0312 | Out=Kareeya Power Station 1 132/11/11kV transformer
T-CTHLWF_080 | 0.0069444 | 0 | Wild Cattle Hill Wind Farm upper limit of 80 MW
Q-YARRAN_RTU | 0.0069444 | 0.21528 | Out = Yarranlea or Yarranlea North RTU, limit Maryrorough SF to 10 MW and Yarranlea SF to 37MW
I-V_T_BL_ZERO_E | 0.0034722 | 0 | Direction to zero for Basslink (Vic to Tas) for Dispatch and Predispatch and NOT PASA
V-NV_HV1150 | 0 | 0 | Discretionary constraint on transfer from NSW to VIC of 1150 MW on DDTS-NSW cutset

## Outage stats
NSP / Year | Unplanned | Short Notice | ≤ 30 days | ≤ 3 months | ≤ 6 months | ≤ 9 months | > 9 months
APT 2018 | 21 | 74 | 15 | 2 | 0 | 1 | 0
2019 | 17 | 58 | 24 | 1 | 0 | 0 | 0
2020 | 13 | 23 | 13 | 2 | 0 | 0 | 0
2021 | 11 | 31 | 28 | 5 | 1 | 0 | 0
2022 | 15 | 37 | 21 | 6 | 2 | 0 | 2
ElectraNet 2018 | 417 | 863 | 973 | 765 | 31 | 8 | 0
2019 | 352 | 852 | 1077 | 687 | 142 | 6 | 0
2020 | 269 | 654 | 958 | 599 | 219 | 21 | 0
2021 | 338 | 645 | 1108 | 651 | 164 | 20 | 1
2022 | 432 | 901 | 1295 | 155 | 44 | 77 | 0
Essential E 2018 | 8 | 5 | 29 | 0 | 0 | 0 | 0
2019 | 4 | 17 | 39 | 0 | 0 | 0 | 0
2020 | 3 | 22 | 62 | 1 | 0 | 0 | 0
2021 | 4 | 30 | 58 | 0 | 0 | 0 | 0
2022 | 17 | 28 | 35 | 3 | 0 | 0 | 0
Powerlink 2018 | 2020 | 5841 | 13383 | 222 | 0 | 0 | 0
2019 | 2040 | 5250 | 8042 | 2154 | 180 | 0 | 0
2020 | 1897 | 6642 | 8078 | 3903 | 247 | 51 | 44
2021 | 1951 | 6022 | 6947 | 5002 | 756 | 39 | 6
2022 | 1986 | 6345 | 7511 | 5241 | 1248 | 148 | 60
AusNet 2018 | 304 | 1467 | 970 | 54 | 0 | 0 | 0
2019 | 364 | 1387 | 1588 | 69 | 0 | 0 | 0
2020 | 370 | 1128 | 1689 | 67 | 10 | 1 | 0
2021 | 280 | 1039 | 2047 | 71 | 0 | 0 | 0
2022 | 190 | 627 | 1881 | 49 | 0 | 0 | 0
TasNetworks 2018 | 171 | 577 | 637 | 109 | 47 | 19 | 63
2019 | 198 | 500 | 1069 | 223 | 47 | 0 | 70
2020 | 108 | 1231 | 890 | 321 | 60 | 31 | 26
2021 | 143 | 604 | 906 | 227 | 97 | 39 | 111
2022 | 104 | 428 | 469 | 203 | 66 | 8 | 19
TransGrid 2018 | 326 | 820 | 1730 | 502 | 19 | 1 | 0
2019 | 327 | 1066 | 1868 | 827 | 10 | 0 | 0
2020 | 411 | 1061 | 1635 | 811 | 30 | 2 | 0
2021 | 384 | 877 | 1676 | 580 | 37 | 0 | 1
2022 | 302 | 849 | 1613 | 358 | 9 | 2 | 0

## NEM Changes
PROJECT | DATE | REGION | NOTES
Murray Bridge - Onkaparinga Pipeline Pumping Station 2 Solar Farm | 11 January 2022 | SA | New Generator
H5 Woolooga - T258 Widgee Creek No. 7471 132 kV line | 2022-01-13 | Qld
St Leonards Scheduled Load | 25 January 2022 | Tasmania | New Load
Bluegrass Solar Farm | 1 February 2022 | Qld | New Generator
Starfish Hill Wf (Mw) | 1 February 2022 | SA | Change of registration - dispatch obligations on existing plant
Cathedral Rocks Wf (Mw) | 1 February 2022 | SA | Change of registration - dispatch obligations on existing plant
Mt Millar Wf (Mw) | 1 February 2022 | SA | Change of registration - dispatch obligations on existing plant
Murra Warra 2 Wind Farm | 15 February 2022 | Victoria | New Generator
Demand Response – Enel X Vic 17 | 22 February 2022 | Victoria | New Wholesale Demand Response
Demand Response – Enel X NSW 3 | 1 March 2022 | NSW | New Wholesale Demand Response
Demand Response – Enel X SA 2 | 1 March 2022 | SA | New Wholesale Demand Response
Demand Response – Enel X Vic 24 | 1 March 2022 | Victoria | New Wholesale Demand Response
Demand Response – Enel X Vic 12 | 1 March 2022 | Victoria | New Wholesale Demand Response
Port Augusta Renewable Energy Park 210 Mw Wind Farm (Mw) | 8 March 2022 | SA | New Generator
Hunter GT (2 Aggregated Units) | 15 March 2022 | NSW | Deregistered Generator
Tamworth #2 120 MVAr cap bank | 23 March 2022 | NSW | Part of QNI minor project
Metz Solar Farm | 29 March 2022 | NSW | New Generator
Demand Response – Enel X NSW 34 | 29 March 2022 | NSW | New Wholesale Demand Response
Demand Response – Enel X NSW 33 | 29 March 2022 | NSW | New Wholesale Demand Response
Demand Response – Enel X NSW 31 | 29 March 2022 | NSW | New Wholesale Demand Response
Beaconsfield South to Rookwood Road 330 kV line | 31 March 2022 | NSW | New transmission line
Liddell Unit 3 | 2 April 2022 | NSW | Deregistered Generator
Mannum Adelaide Pumping Station No 3 | 12 April 2022 | SA | New Generator
Happy Valley Solar Farm | 20 April 2022 | SA | New Generator
Happy Valley Battery (Load Compnent) | 20 April 2022 | SA | New Battery
Happy Valley Battery (Generation Component) | 20 April 2022 | SA | New Battery
Temporary Generation South (Tgs) Lonsdale | 1 May 2022 | SA | Deregistered Generator
Demand Response – Enel X NSW 36 | 17 May 2022 | NSW | New Wholesale Demand Response
Woolooga Solar Farm | 24 May 2022 | Qld | New Generator
Columboola Solar Farm | 14 June 2022 | Qld | New Generator
Queanbeyan BESS | 5 July 2022 | NSW | New Battery
Christie Beach Battery | 12 July 2022 | SA | New Battery
Moorabool No. 3 100 Mvar 220 kV Reactor | 20 July 2022 | Victoria
Moorabool No. 2 100 Mvar 220 kV Reactor | 13 August 2022 | Victoria
Uralla 330kV Terminal Station | 2022-08-19 | NSW | Uralla substation cut into the existing Armidale to Tamworth (85) 330kV line to form Tamworth to Uralla (8U) and Armidale to Uralla (85)
Tamworth 330kV SVC | 2022-09-13 | NSW | Part of QNI minor project
Dumaresq 330kV SVC | 2022-09-13 | NSW | Part of QNI minor project
Kaban Wind Farm 1 | 26 September 2022 | Qld | New Generator
West Wyalong Solar Farm | 27 September 2022 | NSW | New Generator
St Leonards Schedule Load | 28 September 2022 | Tasmania | Deregistered Generator
Torrens Island A Unit 3 | 30 September 2022 | SA | Deregistered Generator
Tumoulin 275kV Terminal Station | 2022-10-06 | Qld | Tumoulin cut in between Chalumbin and Woree 275 kV terminal stations
Moura Solar Farm | 18 October 2022 | Qld | New Generator
Narrandera Substation | 2022-11-27 | NSW | Narrandera substation has been cut into the existing Yanco – Uranquinty (99F) 132kV line.
Bolivar Power Station | 29 November 2022 | SA | New Generator
Berrybank 2 Wind Farm | 29 November 2022 | Victoria | New Generator
Edenvale Solar Farm | 20 December 2022 | Qld | New Generator
New England Solar Farm #1 | 20 December 2022 | NSW | New Generator
New England Solar Farm #2 | 20 December 2022 | NSW | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.