Status Report prepared under clause 7.12 of the Market Rules by System Management
1 April 2016 – 30 June 2016

Table of Contents

1	Introduction	3

1.1	System Management	3

1.2	Status Report	3

2	Issuance of Dispatch and Operating Instructions.	3

3	Non-compliance with Dispatch and Operating Instructions	5

4	Issuance of Dispatch Instructions to Balancing Facilities Out of Merit Order.	7

4.1	Out of Merit instances reported to the IMO	7

4.2	Other instances of Out of Merit dispatch	7

5	Transmission constraints	7

6	Operating States, Shortfalls in Ancillary Services and Involuntary Curtailment of Load	8

6.1	High Risk Operating State	8

6.2	Emergency Operating State	10

6.3	Shortfalls in Ancillary Services	11

6.4	Involuntary curtailment of load	11

7	LFAS Facilities out of Merit Order	11

Introduction

## System Management

On 1 July 2016 Australia Energy Market Operator (AEMO) assumed accountability of System Managements functions under the Wholesale Electrical Market Rules.

Coinciding with this, the Economic Regulation Authority (ERA) has also taken accountability of compliance functions from the Independent Market Operator (IMO) as of 1 July 2016.

This report provides information on events occurring prior to 1 July 2016 and in this context references to System Management, AEMO and IMO made in this report are to be read as referring to the obligations associated with these entities prior to 1 July 2016.

## Status Report

Clause 7.12 requires System Management to provide a quarterly report on the performance of the market with respect to the dispatch process. The report must include details of:

- the incidence and extent of issuance of Operating Instructions and Dispatch Instructions;

- the incidence and extent of non-compliance with Operating Instructions and Dispatch Instructions;

- the incidence and reasons for the issuance of Dispatch Instructions to Balancing Facilities Out of Merit, including for the purposes of this clause, issuing Dispatch Orders to the Verve Energy Balancing Portfolio in accordance with clause 7.6.2;

- the incidence and extent of transmission constraints;

- the incidence and extent of shortfalls in Ancillary Services, involuntary curtailment of load, High Risk Operating States and Emergency Operating States;

- the incidence and reasons for the selection and use of LFAS Facilities under clause 7B.3.8.

System Management has prepared this report pursuant to its obligations under clause 7.12 of the Market Rules, for the period 1 April 2016 to 30 June 2016.

Unless otherwise specified, data contained within this report refers to trading dates and not calendar dates.

Issuance of Dispatch and Operating Instructions.

System Management issued a total of 9,386 Dispatch Instructions to Market Participants during the current reporting period.

Figure 1 below shows the number of Dispatch instructions issued by month since 
1 January 2015.

Figure 1: Dispatch Instructions per month

During the current reporting period, System Management issued a total of 39 Operating Instructions.

Under the Market Rules an Operating Instruction is required for Commissioning and Reserve Capacity Testing.

Figure 2 below shows the number of Operating Instructions issued by month since 1 January 2015.

Figure 2: Operating Instructions per month

Non-compliance with Dispatch and Operating Instructions

In the current reporting period, System Management reported 313 instances of non-compliance with Dispatch Instructions by a Market Participant at the end of their scheduled interval taking into account the Tolerance Range where applicable.

System Management issued 12,130 one minute non-compliance notifications to Market Participants for non-compliance with Dispatch Instructions during the reporting period taking into account the Tolerance Range where applicable.

There were a total of 189 failures by a Market Participant to acknowledge a Dispatch Instruction through the Market Participant Interface.

There were no instances of failure by a Market Participant to acknowledge an Operating Instruction during the current reporting period.

Figure 3 below provides historical non-compliance data since 1 January 2015.

Figure 3: 	Dispatch Instruction non-compliance notifications (end of interval) and non-acknowledged Dispatch Instructions

Issuance of Dispatch Instructions to Balancing Facilities Out of Merit Order.

## Out of Merit instances reported to the IMO

During the reporting period there were no self-reported occasions of potential non-compliant Out of Merit dispatch to the IMO that may have been in breach of the Market Rules.

## Other instances of Out of Merit dispatch

Section 5 of this report contains information pertaining to facilities that have been impacted by transmission constraints. Where a transmission constraint reported in section 5 has resulted in a facility/ies being dispatched to a position that differs from the applicable Balancing Merit Order then these instances will constitute Out of Merit dispatch. Dispatch Advisory notifications are released for these transmission constraint related instances.

Section 6 of this report describes occasions of High Risk and Emergency Operating States that have occurred during the reporting period. During elevated Operating States there may be a need to dispatch facilities Out of Merit to return the power system to a Normal Operating State where indicated in the information provided in section 6.

Transmission constraints

A “transmission constraint” refers to the configuration of the transmission network that has an effect or potential effect of constraining or otherwise varying the output of a generator.  The resultant situation has a generation Facility either decrease output or increase output as required by the circumstances of the constraint.

System Management has identified the following transmission constraints during the period.

- On 10 April 2016 commencing Interval 11:2 and ending Interval 18:2 a planned Western Power Networks Outage on the MU330, MU BTT3 H and MU951.4 lines required the following facilities to be constrained  during the period (refer to Dispatch Advisory 16029);

  - INVESTEC_COLLGAR_WF constrained to 70MW for 3 Intervals

  - MUJA_G2 constrained on to 27.5MW for 11 intervals

- On 15 April 2016 commencing Interval 15:2 until 19 April 2016 ending Interval 11:1, a planned Western Power Networks outage in the Bunbury region resulted in MUJA_G4 being constrained on to 27.5MW for 146 Intervals. (Refer to Dispatch Advisories 16078 and 16085)

- On 15 May 2016, commencing Interval 15:1 until 17 May 2016 ending Interval 2:1 due to upgrades to the SCADA systems and ongoing commissioning of the SCADA systems the following facilities were required to be constrained during the period. (Refer Dispatch Advisories 16327, 16372, 16375, 16376, 16377, 16382, 16385, 16386, 16389, and 16391).

  - INVESTEC_COLLGAR_WF1 constrained between 0MW and 30 MW for 74 Intervals

  - ALINTA_WWF constrained between 0MW and 30MW for 57 Intervals

  - EDWFMAN_WF1 constrained between 0MW and 30MW for 74 Intervals

  - MWF_MUMBIDA_WF1 constrained between 0MW and 30MW for 57 Intervals

- On 21 May 2016 commencing Interval 11:1 and ending 23 May 2016 Interval 14:1 severe storms and lightning strikes in the North Country region tripped the MBA_TS81 and MGA_TS81 lines. This resulted in the following facilities being constrained. (Refer to Dispatch Advisories 16400, 16401, 16402 and 16404).

  - ALINTA_WWF constrained to 0MW for 62 Intervals

  - GREENOUGH_RIVER_PV1 constrained to 0MW for 58 Intervals

  - MWF_MUMBIDA_WF1 constrained between 0MW and 25MW for 108 Intervals

- On 15 June 2016 commencing Interval 7:1 and ending 16 June 2016 Interval 10:2 a Planned Western Power Networks outage on the TS_MBA81 transmission line resulted in the facility ALINTA_WWF being constrained to 0MW for 56 Intervals. (Refer Dispatch Advisories 16464, 16465 and 16466).

Operating States, Shortfalls in Ancillary Services and Involuntary Curtailment of Load

## High Risk Operating State

Six instances of a High Risk Operating States occurred during the report period.

| Date and Interval/s | 14 May 2016 Interval 8:1 to 15 May 2016 Interval 16:1 |
| --- | --- |
| DA Number | 16375 |
| Details | A scheduled SCADA system outage and upgrade was affecting Participant communications and control systems in the SWIS. ABC and AGC control were not available for the duration of the upgrade. Western Power Networks constraints were in place for the following windfarms: ALINTA_WWF; INVESTEC_COLLGAR_WF1; MWF_MUMBIDA_WF1 EDWFMAN_WF1; ALBANY_WF1; GRASMERE_WF1. |
| System Management action | Monitor System Security and provide regular updates. |

| Date and Interval/s | 15 May 2016 Interval 16:2 to 16 May 2016 Interval 10:1 |
| --- | --- |
| DA Number | 16385 |
| Details | Issues resulting from the commissioning of the new SCADA System upgrade required the SWIS to remain in a High Risk State overnight. |
| System Management action | SM continued to monitor Power System Security and Reliability, this included the curtailing of the following windfarms to limit frequency deviations: ALINTA_WWF; INVESTEC_COLLGAR_WF1; MWF_MUMBIDA_WF1 and EDWFMAN_WF1 |

| Date and Interval/s | 16 May 2016 Interval 10:2 to 17 May 2016 Interval 06:1 |
| --- | --- |
| DA Number | 16389 |
| Details | Issues resulting from the commissioning of the new SCADA System upgrade required the SWIS to remain in a High Risk State. |
| System Management action | SM continued to monitor Power System Security and Reliability, this included verbally communicating constraints directly with the following windfarms to limit frequency deviations: ALINTA_WWF; INVESTEC_COLLGAR_WF1; MWF_MUMBIDA_WF1 and EDWFMAN_WF1 |

| Date and Interval/s | 17 May 2016 Interval 06:1 Interval 15:2 |
| --- | --- |
| DA Number | 16391 |
| Details | Ongoing issues with the commissioning of the SCADA System upgrade required the SWIS to remain in a High Risk State |
| System Management action | System Management continued to Dispatch as per the latest Balancing Merit Order |

| Date and Interval/s | 21 May 2016 Interval 10:3 to 23 May 2016 Interval 14:1 |
| --- | --- |
| DA Number | 16400 |
| Details | The MBA - TS 81 line tripped at 14:41 due to storms and lightning strikes in the North Country region which resulted in the North Country islanding. Storm activity in the metro region was also affecting transmission lines. |
| System Management action | MWF_MUMBIDA_WF1, ALINTA_WWF and GREENOUGH_RIVER_PV1 were curtailed between 0 to 25MW and MUNGARRA_GT units were dispatched Out of Merit to ensure Power System Security and Reliability. |

| Date and Interval/s | 22 June 2016 Interval 13:1 |
| --- | --- |
| DA Number | 16484 |
| Details | At 13:04hrs the facility ALINTA_WGP_U2 tripped from approximately 170MW resulting in a frequency deviation to approximately 49.64Hz. |
| System Management action | System Management continued to Dispatch as per the latest Balancing Merit Order |

## Emergency Operating State

During the reporting period, one Emergency Operating State was issued.

| Date and Interval/s | 14 May 2016 Interval 12:1 to 14 May 2016 Interval 13:1 |
| --- | --- |
| DA Number | 16376 |
| Details | The SCADA system upgrade resulted in the SCADA system being completely unavailable. |
| System Management action | Facilities were issued with verbal Dispatch Instructions as per the latest Balancing Merit Order |

Figure 4 below provides historical data for High Risk and Emergency Operating States that have occurred since 1 January 2015.

Figure 4: Number of High Risk and Emergency Operating States

## Shortfalls in Ancillary Services

There were no instances of shortfalls in Ancillary Services for the period.

## Involuntary curtailment of load

There were no instances of involuntary curtailment of load.

# LFAS Facilities out of Merit Order

During the current reporting period there were no incidents where System Management was required to use LFAS Facilities outside of the LFAS Merit Order to operate the SWIS in a reliable and safe manner as per MR7B.3.8.

# Footnotes

Note clause 7.6.1D of the Market Rules provides for Out of Merit Dispatch to avoid a High Risk Operating State or an Emergency Operating State or if the SWIS is in a High Risk Operating State or an Emergency Operating State.