## New South Wales Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer at:
http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Data presented is current as at 16 March 2018
New South Wales Summary
Changes since last update
None to report.
Generation withdrawals
Withdrawn
None to report.
Announced withdrawals (i.e. Mothballed, Seasonal Shut down etc.)
Liddell Power Station: AGL Energy Limited advises that Liddell C Power Station (2000 MW) is to shut down in 2022.
Committed projects
Coal: Bayswater (25 MW) increase each Winter from 2019 to 2022.
CCGT, OCGT, Gas other, Water, Biomass, Geo-thermal, Other : None to report.
Solar: Griffith Solar Farm (29.9 MW), Gullen Range Solar Farm (10 MW), Manildra Photovoltaic Solar Farm (50 MW), Parkes Solar Farm (55 MW), White Rock Solar Farm (20 MW)
Wind: Bodangora Wind Farm (113 MW), Crookwell 2 Wind Farm (91 MW), Sapphire Wind Farm Phase 1 and 2 (270 MW), Silverton Wind Farm (198.94 MW).
Diesel: Hunter Economic Zone (28.8 MW).
Proposed projects
Please refer to information presented in the worksheet titled 'New Developments'.
Plant limitations
AEMO has not been advised of any plant limitations for this region.
New South Wales existing and potential new developments by generation type (MW)
Status | Coal | CCGT | OCGT | Gas other | Solar* | Wind | Water | Biomass | Other | Total
Existing | 10160 | 528.9 | 1530 | 147 | 267.4117 | 839.5 | 2706 | 130.659 | 9.13 | 16318.6007
Announced Withdrawal | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000
Existing less Announced Withdrawal | 8160 | 528.9 | 1530 | 147 | 267.4117 | 839.5 | 2706 | 130.659 | 9.13 | 14318.6007
Committed | 100 | 0 | 0 | 0 | 169.9424 | 673.2 | 0 | 0 | 28.8 | 971.9424
Proposed | 0 | 0 | 0 | 975 | 5642.3074 | 5106.5 | 2000 | 316.6 | 16.1 | 14056.5074
Withdrawn | 0 | -62** | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -62
Note: Existing includes Announced Withdrawal
* Excludes rooftop PV installations
**Visy Power Generation advises that Smithfield Energy Facility, which closed in July 2017, has been brought back into service with up to 109 MW of capacity available, with a further 62 MW available on recall with lead time to be determined.

## Change Log
New South Wales Change Log
Lists all updates to new development projects and existing generation information since the 2012 ESOO published 9 August 2012.
Publication date: | 2012-12-20
Eraring Power Station: Eraring Energy advises that the upgrade of unit 4 was completed in November 2012.
Publication date: | 2013-02-22
Wallerawang Power Station: Energy Australia advises that the Wallerawang plant has revised its available capacity from 1,000 MW to 500 MW (-500 MW) for summer 2013–14 and winter 2013, due to the unit with DUID (dispatchable unit ID) WW7 being unavailable and only being brought back into service under extreme weather conditions.
Colongra Power Station: Delta Electricity advises that the Colongra plant available capacity has been revised from 668 MW to 724 MW (+56 MW) in summer, based on operating with distillate fuel.
Publication date: | 2013-06-30
Wallerawang Power Station: Energy Australia advises that the Wallerawang plant available capacity has been revised from 500 MW to 1,000 MW (+500 MW) in summer 2013–14, where both units are available dependant on demand.
Liddell Power Station: Energy Australia advises that the Liddell plant available capacity has been revised from 2,060 MW to 2,020 MW (-40 MW) in summer and winter due to a reassessment of plant capacity.
Tallawarra Power Station: Energy Australia advises that the Tallawarra plant's available capacity has been revised from 435 MW to 440 MW (+5 MW) in winter.
Gullen Range Wind Farm: Gullen Range Wind Farm Pty Ltd advises that this is a committed project. Construction at the site has commenced and commissioning is planned for July 2014.
Capital East Solar Farm P1: Infigen's Capital East Solar Farm demonstration facility is a committed project. Construction at site has commenced.
Publication date: | 2013-08-13
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that this is a committed project. Construction of the first phase of 113 MW at the site has commenced and commissioning is planned for December 2014.
Taralga Wind Farm: CBD Energy/Banco Santander advises that this 106.7 MW Wind Farm is a committed project. Construction at the site has commenced and commissioning is planned for October 2014.
Publication date: | 2013-11-15
Capital East Solar Farm P1: Infigen's Capital East Solar Farm (0.13 MW) demonstration facility project is was completed in June 2013.
Broken Hill: AGL Energy Limited advises that both the Broken Hill (53 MW) large-scale solar photovoltaic (PV) project is set to proceed after achieving financial close. Construction of the Broken Hill project is expected to commence in July 2014, and is scheduled to be completed around November 2015.
Nyngan: AGL Energy Limited advises that both the Nyngan (102 MW) large-scale solar photovoltaic (PV) projects is set to proceed after achieving financial close. Construction of the Nyngan project is expected to commence in February 2014, with completion scheduled by mid 2015.
Royalla Solar Farm: Royalla Asset Pty Ltd ATF Royalla Asset Trust advises that Royalla Solar Farm (20 MW) in ACT is now classified as a committed project, and construction at the site has commenced, with full commissioning planned for August 2014.
Onesun Capital Solar Farm: Elementus Energy Pty Ltd advises that Onesun Capital Solar Farm (7 MW) in ACT expects construction to commence in June 2014, with full commissioning planned for April 2015.
Mugga Lane Solar Facility: Zhenfa Canberra Solar Farm One Pty Ltd advises that Mugga Lane Solar Facility (13 MW) in ACT expects construction to commence in June 2014, with full commissioning planned for Q4 2014.
Publication date: | 2014-02-28
Nyngan Solar Plant: AGL Engergy Limited advises the Nyngan Solar Plant (102 MW solar) is now classified as a committed project. Construction has commenced, and full commissioning is planned for July 2015.
Jupiter Wind Farm Project: EPYC Pty Ltd has announced the Jupiter Wind Farm Project (up to 100 wind turbines). If approved, construction and commissioning of the wind farm near Tarago would be completed by the end of 2016. The capacity of the project is yet to be advised.
Wallerawang C: EnergyAustralia advises that Wallerawang C unit 7 (500 MW black coal) has been removed from service in January 2014. Unit 8 (500 MW) will remain available until the end of March 2014, and will then be placed on a three-month recall should market conditions change.
Publication date: | 2014-05-30
Bayswater Power Station: Macquarie Generation advises that the Bayswater Power Station available capacity has been revised from 2,720 MW to 2,700 MW (-20 MW) in summer and winter due to a reassessment of plant capacity.
Guthega Power Station: Snowy Hydro Ltd advises that Guthega's available capacity has been revised from 68 MW to 34 MW (-34 MW) for summer 2022–23, due to major refurbishment of unit 1; and 68 MW to 34 MW (-34 MW) for summer 2023–24, due to major refurbishment of unit 2.
Broken Hill Solar Plant: AGL PV Solar Development Pty Limited advises that Broken Hill Solar Plant (53 MW) is a committed project. Construction of the 53 MW at the site is to commence in July 2014 and commissioning is planned for August 2015.
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that Boco Rock Wind Farm (113 MW) is a committed project. Construction of the first phase at the site has commenced and commissioning is planned for March 2015.
Publication date: | 2014-08-07
Moree Solar Farm: Moree Solar Farm advises that Moree Soalr Farm (56 MW) is a committed project. Construction is to commence in July 2014 and commissioning is planned for February 2016.
OneSun Capital: Elementus Energy Pty Ltd advises that OneSun Capital (10 MW) construction is to commence in October 2014 and commissioning is planned for April 2015.
Publication date: | 2014-12-10
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that Boco Rock Wind Farm (113 MW) is a committed project. Construction of the first phase at the site has commenced and commissioning is planned for January 2015.
Taralga Wind Farm: CBD Energy/Banco Santander advises that Taralga Wind Farm (106.7 MW) is a committed project. Construction at the site has commenced and commissioning is planned for May 2015.
Royalla Solar Farm: Royalla Asset Pty Ltd ATF Royalla Asset Trust advises that Royalla Solar Farm (20 MW) is a committed project. Construction has commenced, and full commissioning is planned for February 2015.
Moree Solar Farm: Moree Solar Farm advises that Moree Soalr Farm (56 MW) is a committed project. Construction commenced in November 2014 and commissioning is planned for February 2016.
Wallerawang C Power Station: EnergyAustralia advises that Wallerawang C Power Station (1000 MW black coal) has been removed from service in January 2014 (Unit 8 500 MW) and March 2014 (Unit 7 500 MW), and will permanently closed and decommissioned.
Redbank Power Station: Redbank Energy Ltd advises that Redbank Power Station (143.8 MW black coal) has been removed from service from August 2014 and shut down. There are no future plans at this stage for Redbank to return to service.
Gullen Range Wind Farm: Gullen Range Wind Farm Pty Ltd advises that Gullen Range Wind Farm (165.5 MW) project has been completed and in full commercial operation since November 2014.
Wilga Park Power Station B: Santos advises the Wilga Park Power Station B (6 MW) project has been completed and in full commercial operation since Sepetember 2014.
Publication date: | 2015-04-15
Taralga Wind Farm: CBD Energy/Banco Santander advises that Taralga Wind Farm (106.7 MW) is under construction and full commercial operation is planned for May 2015.
Moree Solar Farm: Moree Solar Farm advises that Moree Solar Farm (56 MW) is under construction since November 2014 and full commercial operation is planned for the end of March 2016.
Boco Rock Wind Farm: Boco Rock Wind Farm Pty Ltd advises that Boco Rock Wind Farm (113 MW) has been completed and in full commercial operation since March 2015.
Royalla Solar Farm: Royalla Asset Pty Ltd ATF Royalla Asset Trust advises that Royalla Solar Farm (20 MW) has been completed and in full commercial operation since February 2015.
Wilga Park Power Station B: Santos advises the Wilga Park Power Station B (6 MW) project has been completed and in full commercial operation since January 2015.
Gullen Range Solar Project: Goldwind Australia Pty Ltd advises has announced plans to add a solar plant at the Gullen Range wind farm site.
Publication date: | 2015-08-13
Taralga Wind Farm: CBD Energy/Banco Santander advises that Taralga Wind Farm (106.7 MW) has been completed and in full commercial operation since May 2015.
Nyngan Solar Plant: AGL Engergy Limited advises the Nyngan Solar Plant (102 MW) has been completed and in full commercial operation since July 2015.
Wallerawang C Power Station: EnergyAustralia advises that Wallerawang C Power Station (1000 MW black coal) has permanently closed in November 2014.
Liddell Power Station: AGL Energy Limited advises that Liddell C Power Station (2000 MW) is to shut down in 2022.
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to retire in 2017.
Redbank Power Station: Redbank Energy Ltd advises that Redbank Power Station (143.8 MW black coal) has been removed from service from August 2014 and shut down. There are no future plans at this stage for Redbank to return to service.
Publication date: | 2015-10-23
Broken Hill Solar Plant: AGL PV Solar Development Pty Limited advises that Broken Hill Solar Plant (53 MW) has been in full commercial operation since October 2015.
Publication date: | 2016-03-03
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to close on 31 July 2017.
Moree Solar Farm: Moree Solar Farm advises that Moree Solar Farm (56 MW) full commercial operation is planned for the end of March 2016.
New Development: Gidginbung Solar Farm, White Rock Solar Farm, Manildra Solar Farm, Capital Solar Farm, Parkes Solar Farm, Griffith Solar Farm, Dubbo Solar Hub, Griffith Solar Farm.
Publication date: | 2016-04-15
SmithField Energy Facility: Smithfield Power Partnership advises that SmithField Energy Facility 170.9 MW) is to close on 31 July 2017.
Moree Solar Farm: Moree Solar Farm advises that Moree Solar Farm (56 MW) full commercial operation is planned for the end of March 2016.
New Development: Gidginbung Solar Farm, White Rock Solar Farm, Manildra Solar Farm, Capital Solar Farm, Parkes Solar Farm, Griffith Solar Farm, Dubbo Solar Hub, Griffith Solar Farm.
Publication date: | 2016-08-11
Moree Solar Farm: Moree Solar Farm Pty Ltd advises that Moree Solar Farm (56 MW) has been completed and is in full commercial operation since late March 2016.
White Rock Wind Farm: Goldwind Australia advises that White Rock Wind Farm (175 MW) is a committed project.
Williamsdale Solar Farm: Elementus Energy Ptd Ltd. advises that Williamsdale Solar Farm (10MW) is a committed project.
Mugga Lane Solar Park: Zhenfa Canberra Solar Farm One advises that Mugga Lane Solar Park (13MW) is a committed project.
New Development: Gullen Solar Project, Narromine Solar Farm, South Keswick Solar Farm, Boco Rock Wind Farm (expansion), Woodlan Bioreactor Energy Generation (expansion).
Publication date: | 2016-11-18
Eraring GT: AEMO has corrected the entry on the worksheet titled 'Existing NS Generation' to show OCGT for the Technology Type. This also updates the capacity totals shown below, moving 42 MW of Existing/Existing less announced withdrawal capacity from the "Other" category to the "OCGT" category.
Publication date: | 2017-02-27
Griffith Solar Farm: Griffith Solar Farm Pty Ltd advises that Griffith Solar Farm (29 MW) is now a committed project.
Parkes Solar Farm: Parkes Solar Farm Pty Ltd advises that Parkes Solar Farm (55 MW) is now a committed project.
Williamsdale Solar Farm: OneSun advises that Williamsdale Solar Farm (10MW) is now completed and is undergoing commissioning tests with full commercial operation expected in March 2017.
Woodlawn Bioreactor Energy Generation (expansion): AEMO has corrected the capacity totals shown below to include this existing new development (7.455 MW) in the Biomass (Proposed) category.
Publication date: | 2017-06-05
Manildra Photovoltaic Solar Farm: Manildra Prop Pty Ltd as trustee for the Manildra Asset Trust advises that Manildra Photovoltaic Solar Farm (50 MW) is now a committed project.
Gullen Range Solar Farm: New Gullen Range Wind Farm Pty Ltd advises that Gullen Range Solar Farm (10 MW) is now a committed project.
Mugga Lane Solar Park: Mugga Lane Solar Park Pty Ltd advises that Mugga Lane Solar Park (13 MW) is now an existing generator with full commercial operation having commenced in 2017.
Publication date: | 2017-12-22
Smithfield Energy Facility: Visy Power Generation advises that Smithfield Energy Facility, which closed in July 2017, has been brought back into service with up to 109 MW of capacity available, with a further 62 MW available on recall with lead time to be determined.
Bodangora Wind Farm: Bodangora Wind Farm (113 MW) is now reported as committed since Infigen Energy has advised construction has commenced.
Silverton Wind Farm: PARF Company Pty Ltd as trustee for the Silverton Project Trust advises that Silverton Wind Farm (198.94 MW) is now a committed project.
White Rock Solar Farm: White Rock Solar Farm (20 MW) is now reported as committed since White Rock Wind Farm Pty Ltd has advised construction has commenced.
Sapphire Wind Farm Phase 1 and 2: Sapphire Wind Farm Pty Ltd advises that Sapphire Wind Farm Phase 1 and 2 (270 MW) is now committed.
Hunter Economic Zone Diesel: Hunter Economic Zone Diesels (28.8 MW) is now reported at committed as Snowy Hydro Ltd advises construction has commenced.
Crookwell 2 Wind Farm: Crookwell 2 Wind Farm (91 MW) is reported as committed as Crookwell Development Pty Ltd has advised construction has commenced.
Bayswater: AGL has advised Bayswater Power Station will increase capacity by 25 MW each Winter from 2019 to 2022
Publication date: | 2017-03-16
None to report.

## Existing S & SS Generation
Existing scheduled and semi-scheduled generation
Power Station | Owner | Unit Number and Nameplate Capacity (MW) | Installed Capacity (MW) | Technology Type | Fuel Type | Dispatch Type | Service Status
Bayswater | AGL Energy | 4 x 660 | 2640 | Steam Sub Critical | Black Coal | S | In Service
Blowering | Snowy Hydro Ltd | 1 x 80 | 80 | Hydro - Gravity | Water | S | In Service
Boco Rock Wind Farm | Boco Rock Wind Farm Pty Ltd | 9 x 1.6 58 x 1.7 | 113 | Wind - Onshore | Wind | SS | In Service
Broken Hill Solar Plant | AGL PV Solar Development Pty Limited | 40 x 1.325 | 53 | PV panels | Solar | SS | In Service
Colongra | Snowy Hydro Ltd | 4 x 181 | 724 | OCGT | Natural Gas Pipeline | S | In Service
Eraring | Origin Energy Eraring Pty Ltd | 4 x 720 | 2880 | Steam Sub Critical | Black Coal | S | In Service
Gullen Range Solar Farm | New Gullen Range Wind Farm Pty Ltd | 4x2.5 | 10 | PV panels | Solar | SS | In Service
Gullen Range Wind Farm | New Gullen Range Wind Farm Pty Ltd | 17 x 1.5 56 x 2.5 | 165.5 | Wind - Onshore | Wind | SS | In Service
Gunning Wind Farm | Gunning Wind Energy Developments | 31 x 1.5 | 46.5 | Wind - Onshore | Wind | SS | In Service
Guthega | Snowy Hydro Ltd | 2 x 30 | 60 | Hydro - Gravity | Water | S | In Service
Hume NSW | Green State Power Pty Ltd | 1 x 29 | 29 | Hydro - Gravity | Water | S | In Service
Hunter Valley GT | AGL Energy | 2 x 25 | 50 | OCGT | Fuel Oil | S | In Service
Liddell | AGL Energy | 4 x 500 | 2000 | Steam Sub Critical | Black Coal | S | Announced Withdrawal
Moree Solar Farm | Moree Solar Farm Pty Ltd | 56 x 1 | 56 | PV panels | Solar | SS | In Service
Mt Piper | EnergyAustralia | 2 x 660 | 1320 | Steam Sub Critical | Black Coal | S | In Service
Nyngan Solar Plant | AGL PV Solar Developments Pty Limited | 77 x 1.325 | 102 | PV panels | Solar | SS | In Service
Shoalhaven | Origin Energy Eraring Pty Ltd | 2 x 40 2 x 80 | 240 | Pump Storage | Water | S | In Service
Smithfield Energy Facility | Visy Power Generation | 3 x 36.3 1 x 62 | 170.9* | CCGT | Natural Gas Pipeline | S | In Service
Tallawarra | EnergyAustralia | 1 x 420 | 420 | CCGT | Natural Gas Pipeline | S | In Service
Taralga Wind Farm | Banco Santander / BlueNRGY Group Limited | 9 x 3 21 x 1.8 21 x 2 | 106.7 | Wind - Onshore | Wind | SS | In Service
Tumut 3 | Snowy Hydro Ltd | 6 x 250 | 1500 | Hydro - Gravity | Water | S | In Service
Upper Tumut | Snowy Hydro Ltd | 4 x 72 4 x 82 | 616 | Hydro - Gravity | Water | S | In Service
Uranquinty | Origin Energy Uranquinty Power Pty Ltd | 4 x 166 | 664 | OCGT | Natural Gas Pipeline | S | In Service
Vales Point B | Delta Electricity | 2 x 660 | 1320 | Steam Sub Critical | Black Coal | S | In Service
Woodlawn Wind Farm | Woodlawn Wind Pty Ltd | 23 x 2.1 | 48.3 | Wind - Onshore | Wind | SS | In Service
White Rock Wind Farm | White Rock Wind Farm Pty Ltd | 1-70 | 172.5 | Wind - Onshore | Wind | SS | In Service
Total |  |  | 15416.5
*Visy Power Generation advises that Smithfield Energy Facility, which closed in July 2017, has been brought back into service with up to 109 MW of capacity available, with a further 62 MW available on recall with lead time to be determined.

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation
Power Station | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | Dispatch Type
Bayswater | 2520 | 2520 | 2545 | 2570 | 2595 | 2620 | 2620 | 2620 | 2620 | 2620 | S
Beryl Solar Farm | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Boco Rock Wind Farm | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | SS
Bodangora Wind Farm | 0 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Colongra | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | S
Crookwell 2 Wind Farm | 0 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | SS
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Gullen Range Solar Farm | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | SS
Gullen Range Wind Farm | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning Wind Farm | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Guthega | 68 | 68 | 68 | 34 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Hunter Economic Zone | 0 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Hunter Valley GT | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | S
Liddell | 1800 | 1800 | 1800 | 1800 | 1800 | 0 | 0 | 0 | 0 | 0 | S
Manildra Photovoltaic Solar Farm | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | SS
Moree Solar Farm | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | SS
Mt Piper | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | S
Nyngan Solar Plant | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Parkes Solar Farm | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | SS
Sapphire Wind Farm Phase 1 and 2 | 0 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Silverton Wind Farm | 0 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | SS
Smithfield Energy Facility | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | S
Tallawarra | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | S
Taralga Wind Farm | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | SS
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
White Rock Wind Farm | 173 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | SS
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Total | 15396.1 | 16147.6 | 16272.6 | 16263.6 | 16322.6 | 14547.6 | 14547.6 | 14547.6 | 14547.6 | 14547.6
The table above lists the latest Summer capacities for New South Wales generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 6.7% of the installed capacity during summer, and 3.7% during winter, based on AEMO's analysis of historical wind output over summer 2012-13 to 2016-17, and winter 2013 to 2017.
Due to the intermittent nature of sunlight, solar generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. However, AEMO has not yet calculated contribution factors for solar, due to there being insufficient historical data to analyse for semi-scheduled solar generation in the New South Wales. Thus the Firm Solar Capacity values in the table below are shown as NA, and do not contribute to the total capacity in that table.
The two tables below have been included to better represent the supply availability in New South Wales, by taking into account the firm contribution by semi-scheduled generation. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the Summer period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the Summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation
Power Station | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | Dispatch Type
Bayswater | 2520 | 2520 | 2545 | 2570 | 2595 | 2620 | 2620 | 2620 | 2620 | 2620 | S
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Colongra | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | S
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Guthega | 68 | 68 | 68 | 34 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Hunter Economic Zone | 0 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Hunter Valley GT | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | S
Liddell | 1800 | 1800 | 1800 | 1800 | 1800 | 0 | 0 | 0 | 0 | 0 | S
Mt Piper | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | S
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Smithfield Energy Facility | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | S
Tallawarra | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | S
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
Firm Wind Capacity | 43.7242 | 88.8286 | 88.8286 | 88.8286 | 88.8286 | 88.8286 | 88.8286 | 88.8286 | 88.8286 | 88.8286 | SS
Firm Solar Capacity | [10 empty] | SS | bar: 2017-18 to 2026-27
Total | 14510.7242 | 14584.6286 | 14609.6286 | 14600.6286 | 14659.6286 | 12884.6286 | 12884.6286 | 12884.6286 | 12884.6286 | 12884.6286
Summer aggregate available semi-scheduled generation
Power Station | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | Dispatch Type
Beryl Solar Farm | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Boco Rock Wind Farm | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | SS
Bodangora Wind Farm | 0 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Crookwell 2 Wind Farm | 0 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | SS
Gullen Range Solar Farm | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | SS
Gullen Range Wind Farm | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning Wind Farm | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Manildra Photovoltaic Solar Farm | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | SS
Moree Solar Farm | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | SS
Nyngan Solar Plant | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Parkes Solar Farm | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | SS
Sapphire Wind Farm Phase 1 and 2 | 0 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Silverton Wind Farm | 0 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | SS
Taralga Wind Farm | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | SS
White Rock Wind Farm | 173 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | SS
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Total (Wind) | 652.6 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8
Total (Solar) | 276 | 326 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation
Power Station | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Dispatch Type
Bayswater | 2640 | 2665 | 2690 | 2715 | 2740 | 2740 | 2740 | 2740 | 2740 | 2740 | S
Beryl Solar Farm | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Boco Rock Wind Farm | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | SS
Bodangora Wind Farm | 0 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Colongra | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | S
Crookwell 2 Wind Farm | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | SS
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Gullen Range Solar Farm | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | SS
Gullen Range Wind Farm | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning Wind Farm | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Guthega | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hunter Economic Zone | 0 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Hunter Valley GT | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Liddell | 1800 | 1800 | 1800 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | S
Manildra Photovoltaic Solar Farm | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | SS
Moree Solar Farm | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | SS
Mt Piper | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Nyngan Solar Plant | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Parkes Solar Farm | 54 | 53.8 | 53.5 | 53.2 | 52.9 | 52.7 | 52.5 | 52.3 | 52.1 | 51.9 | SS
Sapphire Wind Farm Phase 1 and 2 | 0 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Silverton Wind Farm | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | SS
Smithfield Energy Facility | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | S
Tallawarra | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | S
Taralga Wind Farm | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | SS
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 534 | 534 | 534 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 688 | 688 | 688 | 688 | 688 | 688 | 688 | 688 | 688 | 688 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
White Rock Wind Farm | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | SS
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Total | 16029.6 | 16566.4 | 16591.1 | 16697.8 | 14922.5 | 14922.3 | 14922.1 | 14921.9 | 14921.7 | 14921.5
The table above lists the latest Winter capacities for New South Wales generation. Winter conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 6.7% of the installed capacity during summer, and 3.7% during winter, based on AEMO's analysis of historical wind output over summer 2012-13 to 2016-17, and winter 2013 to 2017.
Due to the intermittent nature of sunlight, solar generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. However, AEMO has not yet calculated contribution factors for solar, due to there being insufficient historical data to analyse for semi-scheduled solar generation in New South Wales. Thus the Firm Solar Capacity values in the table below are shown as NA, and do not contribute to the total capacity in that table.
The two tables below have been included to better represent the supply availability in New South Wales, by taking into account the firm contribution by semi-scheduled generation. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the Winter period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the Winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation
Power Station | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Dispatch Type
Bayswater | 2640 | 2665 | 2690 | 2715 | 2740 | 2740 | 2740 | 2740 | 2740 | 2740 | S
Blowering | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | S
Colongra | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | 724 | S
Eraring | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | 2880 | S
Guthega | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Hume NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Hunter Economic Zone | 0 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Hunter Valley GT | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | S
Liddell | 1800 | 1800 | 1800 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | S
Mt Piper | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Shoalhaven | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | S
Smithfield Energy Facility | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | S
Tallawarra | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | S
Tumut 3 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | S
Upper Tumut | 534 | 534 | 534 | 616 | 616 | 616 | 616 | 616 | 616 | 616 | S
Uranquinty | 688 | 688 | 688 | 688 | 688 | 688 | 688 | 688 | 688 | 688 | S
Vales Point B | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | 1320 | S
Firm Wind Capacity | 44.8662 | 49.0546 | 49.0546 | 49.0546 | 49.0546 | 49.0546 | 49.0546 | 49.0546 | 49.0546 | 49.0546 | SS
Firm Solar Capacity | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | SS
Total | 14817.8662 | 14875.8546 | 14900.8546 | 15007.8546 | 13232.8546 | 13232.8546 | 13232.8546 | 13232.8546 | 13232.8546 | 13232.8546
Winter aggregate available semi-scheduled generation
Power Station | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Dispatch Type
Beryl Solar Farm | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | SS
Boco Rock Wind Farm | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | SS
Bodangora Wind Farm | 0 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | 113.2 | SS
Broken Hill Solar Plant | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | SS
Crookwell 2 Wind Farm | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | SS
Gullen Range Solar Farm | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | SS
Gullen Range Wind Farm | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | SS
Gunning Wind Farm | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | SS
Manildra Photovoltaic Solar Farm | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | SS
Moree Solar Farm | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | SS
Nyngan Solar Plant | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | SS
Parkes Solar Farm | 54 | 53.8 | 53.5 | 53.2 | 52.9 | 52.7 | 52.5 | 52.3 | 52.1 | 51.9 | SS
Sapphire Wind Farm Phase 1 and 2 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | SS
Silverton Wind Farm | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | SS
Taralga Wind Farm | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | SS
White Rock Wind Farm | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | 172.5 | SS
Woodlawn Wind Farm | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | SS
Total (Wind) | 1212.6 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8 | 1325.8
Total (Solar) | 314 | 413.8 | 413.5 | 413.2 | 412.9 | 412.7 | 412.5 | 412.3 | 412.1 | 411.9

## Existing NS Generation
Existing non-scheduled generation
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type | Service Status
101 Miller Street | Cogent Energy Pty Ltd | 2.3 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
133 Castlereagh St | Cogent Energy Pty Ltd | 0.772 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
20 Bond St | Cogent Energy Pty Ltd | 0.6 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
275 Kent St | Cogent Energy Pty Ltd | 1.2 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
40 Mount St | Cogent Energy Pty Ltd | 0.8 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
8 Chifley Place | Cogent Energy Pty Ltd | 0.4 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
Broadwater and Condong Co-generation plants | Cape Byron Management | 68 | Steam Sub Critical | Bagasse | In service
Appin | EDL CSM NSW Pty Ltd | 55.62 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
Lucas Heights 2 | EDL LFG NSW Pty Ltd | 17.25 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Bankstown Sports Club | Bankstown Sports Club | 2.14 | Compression Reciprocating Engine | Diesel | In service
Eastern Creek 2 Gas Utilisation Facility | LMS Energy Pty Ltd | 7.861 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Woodlawn Bioreactor Energy Generation | Veolia Environmental Services Aust P/L | 6.39 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Woodlawn Bioreactor Energy Generation (expansion) | Veolia Environmental Services Aust P/L | 7.455 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Blackmores | Cogent Energy Pty Ltd | 0.772 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
Blayney | Blaney and Crookwell WindFarm Pty Ltd | 9.9 | Wind - Onshore | Wind | In service
Lucas Heights I | EDL LFG NSW Pty Ltd | 5.39 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Broken Hill GT | Essential Energy | 50 | OCGT | Diesel | In service
Brown Mountain Hydro Power Station | Cochrane Dam Pty Ltd | 4.95 | Hydro - Gravity | Water | In service
Burrendong | AGL | 19 | Hydro - Gravity | Water | In service
Burrinjuck | Green State Power Pty Ltd | 27.2 | Hydro - Gravity | Water | In service
Capital East Solar Farm P1 | Infigen Energy | 0.13 | PV panels | Solar | In service
Capital Wind Farm | Renewable Power Ventures Pty Ltd | 140.7 | Wind - Onshore | Wind | In service
Charlestown Square Cogeneration | GPT RE Limited | 2.808 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline | In service
Copeton | AGL | 20 | Hydro - Gravity | Water | In service
Crookwell | Blaney and Crookwell WindFarm Pty Ltd | 4.8 | Wind - Onshore | Wind | In service
Cullerin Range Wind Farm | Cullerin Range Wind Farm Pty Ltd | 30 | Wind - Onshore | Wind | In service
Eastern Creek | EDL LFG NSW Pty Ltd | 5.06 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Earthpower Technologies Sydney | Earthpower Technologies Sydney | 3.9 | Spark Ignition Reciprocating Engine | Biogas - Sludge captured for combustion methane only | In service
Mugga Lane | EDL LFG ACT Pty Ltd | 3.45 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Eraring GT | Origin Energy Eraring Pty Ltd | 42 | OCGT | Diesel | In service
Erskine Park | Cogent Energy Pty Ltd | 0.386 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
Glenbawn | AGL | 5 | Hydro - Gravity | Water | In service
Glennies Creek | EDL OCI Pty Ltd | 13 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
Jacks Gully | EDL LFG NSW Pty Ltd | 2.3 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Summer Hill | LMS Energy Pty Ltd | 2.246 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Jindabyne | Snowy Hydro Ltd | 1.1 | Hydro - Gravity | Water | In service
Jounama | Snowy Hydro Ltd | 14.4 | Hydro - Gravity | Water | In service
Keepit | Green State Power Pty Ltd | 7.2 | Hydro - Gravity | Water | In service
Wyong | LMS ENERGY Pty Ltd | 2.246 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Grange Avenue | EDL LFG NSW Pty Ltd | 1.26 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Mount Majura | Mount Majura Solar Holdings Pty Ltd | 2.3 | PV panels | Solar | In service
Albury Renewable Energy Facility | LMS Energy Pty Ltd | 1.123 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Mugga Lane Solar Park | Mugga Lane Solar Park Pty Ltd | 12.85 | PV panels | Solar | In service
Nine Network Willoughby | Nine Network | 3.2 | Compression Reciprocating Engine | Diesel | In service
Pindari | AGL | 5.7 | Hydro - Gravity | Water | In service
Royalla Solar Farm | Royalla Asset Pty Ltd ATF Royalla Asset Trust | 20 | PV panels | Solar | In service
St George Leagues Club | St George Leagues Club | 1.48 | Compression Reciprocating Engine | Diesel | In service
Awaba | LMS Energy Pty Ltd | 1.123 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Tahmoor | EDL TT Pty Ltd | 7.3 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
Teralba | Envirogen Pty Ltd | 3.11 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
The Drop | Pacific Hydro Investments Pty Ltd | 2.5 | Hydro - Gravity | Water | In service
Tower | EDL CSM NSW Pty Ltd | 41.2 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas | In service
UNSW C25 | Cogent Energy Pty Ltd | 0.772 | Compression Reciprocating Engine | Natural Gas Pipeline | In service
Warragamba HEPS | Water NSW | 50 | Hydro - Gravity | Water | In service
West Illawarra Leagues Club | Wests Illawarra Leagues Club | 0.99 | Compression Reciprocating Engine | Diesel | In service
Belconnen | EDL LFG ACT Pty Ltd | 1.03 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Western Suburbs League Club Campbelltown | Western Suburbs League Club Campbelltown | 1.32 | Compression Reciprocating Engine | Diesel | In service
Wilga Park Power Station A | Santos | 10 | Spark Ignition Reciprocating Engine | Coal Seam Methane | In service
Wilga Park Power Station B | Santos | 6 | Spark Ignition Reciprocating Engine | Coal Seam Methane | In service
Williamsdale Solar Farm | OneSun Capital 10MW Operting Pty Ltd | 7.566 | PV panels | Solar | In service
Belrose | EDL LFG NSW Pty Ltd | 1.03 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Wyangala A | Hydro Power Pty Ltd | 20 | Hydro - Gravity | Water | In service
Wyangala B | AGL | 4 | Hydro - Gravity | Water | In service
West Nowra Landfill Gas Power Generation Facility | AGL | 1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Jemalong STEG Plant Phase 1 | Vast Solar | 1.1 | PV Tracking flat panel | Solar | In service
Bakers Maison | TBA | 0.2246 | PV Panels | Solar | In service
Chillamurra | TBA | 4.77 | PV Tracking flat panel | Solar | In service
De Bortoli Wines | TBA | 0.23 | PV Panels | Solar | In service
DHL6 Solar Horsley Park | TBA | 0.1 | PV Panels | Solar | In service
Drayton's Family Wines Solar | TBA | 0.2 | PV Panels | Solar | In service
LMCC - Works Depot Power Station | TBA | 0.0788 | PV Panels | Solar | In service
Parkes Shire Council STP | TBA | 0.1074 | PV Panels | Solar | In service
Parkes Shire Council WTP | TBA | 0.1074 | PV Panels | Solar | In service
Penrith RSL Solar | TBA | 0.1999 | PV Panels | Solar | In service
Proten - Farm 74 | TBA | 0.2499 | PV Panels | Solar | In service
Stockland Development Wetherill Park | TBA | 0.9248 | PV Panels | Solar | In service
Taronga Western Plains Zoo | TBA | 0.9976 | PV Panels | Solar | In service
Todae Solar CSU | TBA | 1.7691 | PV Panels | Solar | In service
Todae Solar PE - Llandilo | TBA | 0.795 | PV Panels | Solar | In service
Todae Solar- PF Minchinbury | TBA | 0.3204 | PV Panels | Solar | In service
Todae Solar SV - Mater Clinic | TBA | 0.1302 | PV Panels | Solar | In service
Todae Solar SV - Mater Hospital | TBA | 0.2801 | PV Panels | Solar | In service
Proten - Farm 60 | TBA | 0.3588 | PV Panels | Solar | In service
Proten - Farm 61 | TBA | 0.3567 | PV Panels | Solar | In service
Proten - Farm 75 - 79 | TBA | 1.211 | PV Panels | Solar | In service
Total |  | 810.0917

## New Developments
Projects under development
Project | Owner | Unit ID | Technology Type | Fuel Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Full Commercial Use Date | Source
Balranald Solar Farm | Maoneng Solar Asset Holdings Limited |  | PV Panels | Solar | [5 empty] | Pub An | 200 | SS
Bango Wind Farm | Bango Wind Farm Pty Ltd | 1 - 90 | Wind - Onshore | Wind | [5 empty] | Pub An | 200 | SS |  | http://bangowindfarm.com.au/facts_figures
Ben Lomond | AGL Energy Limited | 1-67 | Wind - Onshore | Wind | [5 empty] | Pub An | 200 | SS
Beryl Solar Farm | Manildra Prop Pty Ltd as trustee for the Manildra Asset Trust | 1-6 | PV - single axis tracking | Solar | ü |  |  |  | ü | Pub An | 100 | SS
Biala Wind Farm | Newtricity |  | Wind - Onshore | Wind | [5 empty] | Pub An | 109 | SS
Bindaree Beef Biodigestor Pant | Yolarno |  | Biogas | Biogas | [5 empty] | Pub An | 12 | NS
BluesScope Cogeneration Plant | BlueScope |  | Co-generation | Natural Gas | [5 empty] | Pub An | 225 | S
Boco Rock Wind Farm (expansion) | Boco Rock Wind Farm Pty Ltd | 68-122 | Wind - Onshore | Wind | [5 empty] | Pub An | TBC | SS
Bodangora Wind Farm | Infigen Energy | Units 1-33 | Wind - Onshore | Wind | ü | ü |  | ü | ü | Com* | 113.2 | SS | Aug-18 | https://www.infigenenergy.com/investors/asxreleases/infigen-to-proceed-to-construction-of-113-mw-bodangora-wind-farm/
Bogan River | Infigen Energy | Solar Panels | PV Panels | Solar | ü |  |  |  | ü | Pub An | 12 | NS |  | https://www.infigenenergy.com/our-business/development-pipeline/solar-energy-projects/
Bomen Solar Farm | Renew Estate |  | PV Panels | Solar | [5 empty] | Pub An | 120 | SS
Brewongle Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 131 | SS |  | http://www.photonenergy.com.au/current-projects/brewongle-solar-farm/
Broadwater Bioenergy Plant | Cape Byron Power |  | Biomass | Biomass | [5 empty] | Pub An | 38 | S
Brocklehurst Solar Farm | TBA |  | PV Panels | Solar | [5 empty] | Pub An | 29 | NS
Capital 2 Wind Farm | Infigen Energy | Units 1-33 | Wind - Onshore | Wind |  |  | ü |  |  | Pub An | 100 | SS | Oct-19 | https://www.infigenenergy.com/capital-precinct/capital-2-wind-farm/
Capital Solar Farm | Infigen Energy | Inverters 1 - 34 | PV Panels | Solar | [5 empty] | Pub An | 50 | SS
Carrick Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 138 | SS |  | http://www.photonenergy.com.au/current-projects/carrick-solar-farm/
Chipping Norton Waste to Energy | Benedict Industries PL | 1 | Steam Sub Critical | Biomass | ü |  |  |  |  | Pub An | 8 | NS
Coleambally Solar Farm | Neoen | 88 | PV - single axis tracking | Solar | [5 empty] | Pub An | 150 | SS
Collector | Ratch Australia Corporation | 1-55 | Wind - Onshore | Wind | ü | ü |  |  |  | Pub An | 187 | SS | Sep-19
Condong Bioenergy Plant | Cape Byron Power |  | Biomass | Biomass | [5 empty] | Pub An | 30 | S
Conroy's Gap Wind Farm | EPURON Pty Ltd |  | Wind - Onshore | Wind | [5 empty] | Pub An | 30 | SS
Coppabella Wind Farm | Goldwind Australia Pty Ltd |  | Wind - Onshore | Wind | [5 empty] | Pub An | 285 | SS
Crookwell 2 Wind Farm | Crookwell Development Pty Ltd | Units 1-28 | Wind - Onshore | Wind | ü | ü |  | ü | ü | Com* | 91 | SS | Aug-2018 | http://www.unionfenosa.com.au/portfolio/nsw-crookwell-2/
Crookwell 3 Wind Farm | Crookwell Development Pty Ltd | Units 1-23 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 76 | SS
CRS Canberra | Benedict Industries PL | 1 | Waste to Energy | Other | [5 empty] | Pub An | 15 | NS
Crudine Ridge Wind Farm | Crudine Ridge Wind Farm Pty Ltd | 1-77 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 135 | SS |  | http://crudineridgewindfarm.com.au/facts_figures
Currawarra Solar Farm | RES Australia Pty Ltd |  | PV Panels | Solar | [5 empty] | Pub An | 195 | SS |  | http://www.currawarra-solarfarm.com/
Dubbo Solar Hub | Neoen |  | PV Panels | Solar | ü |  |  | ü |  | Adv | 20 | NS | Winter 2018 | https://dubbosolarhub.com.au/
Dunedoo Solar Farm | ib vogt GmbH |  | PV Panels | Solar | [5 empty] | Pub An | 66 | SS
Eastern Creek Energy from Waste Facility | Next Generation NSW |  | Waste to Energy | Biogas | [5 empty] | Pub An | 140 | SS |  | http://www.planning.nsw.gov.au/Assess-and-Regulate/Projects/Eastern-Creek-Energy-from-Waste/Key-Features-and-FAQs
Finley Solar Farm | ESCO Pacific |  | PV - single axis tracking | Solar | ü |  |  |  |  | Pub An | 150 | SS |  | http://finleysolarfarm.com.au/project/
Flyers Creek Wind Farm | Infigen Energy | 1-42 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 126 | SS | Jul-19
Gidginbung Solar Farm | ib vogt GmbH |  | PV Panels | Solar | [5 empty] | Pub An | 15 | NS |  | http://gidginbungsolarfarm.com.au/home/
Gilgandra Solar Farm | Neoen | 25 | PV - single axis tracking | Solar | [5 empty] | Pub An | 40 | SS
Glen Innes Wind Farm | Glen Innes WindPower Pty Ltd | Units 1-25 | Wind - Onshore | Wind |  |  |  |  | ü | Pub An | 90 | SS
Goonumbla Solar Farm | Goonumbla Solar Farm Pty Ltd | 1-31 | PV Panels | Solar | [5 empty] | Pub An | 70 | SS | Dec-17
Goulburn Bioenergy Project | ReNu Energy Limited | 1 | Biogas | Biomass | [5 empty] | Pub An | 1.6 | NS | Jan-2018
Granite Hills Wind Farm | Akuo Energy |  | Wind - Onshore | Wind | [5 empty] | Pub An | 121 | SS
Gregadoo Solar Farm | Gregadoo Solar Farm Pty Ltd |  | PV Panels | Solar | [5 empty] | Pub An | 45 | SS
Griffith Solar Farm | Griffith Solar Farm Pty Ltd | 1 | PV Panels | Solar | ü | ü | ü | ü | ü | Com | 34.9424 | SS | Summer 2018/19 | https://griffithsolarfarm.com.au/
Gullen Range Solar Farm (expansion) | New Gullen Range Wind Farm Pty Ltd | GRWFSO 1-4 | PV Panels | Solar | ü | ü | ü | ü | ü | Com | 10 | SS | Summer 2017/18 | http://www.goldwindaustralia.com/projects/under-construction/gullen-range-solar-farm/
Gunnedah Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 155 | SS |  | http://www.photonenergy.com.au/current-projects/gunnedah/
Gunning Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 316 | SS
Hay Sun Farm | Overland Sun Farming Pty Ltd |  | PV Tracking flat panel | Solar | ü |  |  |  |  | Pub An | 100 | SS
Hillston | Overland Sun Farming Pty Ltd |  | PV Tracking flat panel | Solar | ü |  |  |  |  | Pub An | 100 | SS
Hunter Economic Zone | Snowy Hydro Ltd | 16 | Diesel Peaking Power station reconnection | Other | ü | ü |  |  | ü | Com* | 28.8 | S | Sept - 2018
Jupiter Wind Farm | EPYC Pty Ltd | 1-88 | Wind - Onshore | Wind | [5 empty] | Pub An | 350 | SS
Kyoto Energy Park | Upper Hunter Energy Park Pty Limited | Units 1-29 | Wind - Onshore | Wind | [5 empty] | Pub An | TBC | SS
Leeton Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 26 | NS
Limondale Sun Farm | Overland Sun Farming |  | PV Panels | Solar | [5 empty] | Pub An | 250 | SS
Liverpool Range Wind Farm | EPURON Pty Ltd | 266 | Wind - Onshore | Wind | [5 empty] | Pub An | 1200 | SS
Manildra Photovoltaic Solar Farm | Manildra Prop Pty Ltd as trustee for the Manildra Asset Trust | Inverters 1-20 | PV Panels | Solar | ü | ü | ü | ü | ü | Com | 50 | SS | Winter 2018 | http://www.firstsolar.com/en-AU/Resources/Projects/Manildra-Solar-Farm
Maryvale Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 115 | SS
Metz Solar Farm | Infigen Energy | . | PV Panels | Solar | [5 empty] | Pub An | 100 | SS | .
Molong Solar Farm | Terrain Solar |  | PV Panels | Solar | [5 empty] | Pub An | 25 | NS
Moorambilla Solar Farm | Moorambilla Solar Pty Ltd | . | PV Panels | Solar | [5 empty] | Pub An | 5 | NS | .
Mumbil Solar Farm | Photon Energy |  | PV Panels | Solar | [5 empty] | Pub An | 138 | SS |  | http://www.photonenergy.com.au/current-projects/mumbil-solar-farm/
Narrabri South Solar Farm | Canadian Solar (Australia) P/L |  | PV Panels | Solar | [5 empty] | Pub An | 60 | SS
Narromine Solar Farm | Dubbo Solar Hub Pty Ltd |  | PV Tracking flat panel | Solar | ü | ü |  | ü | ü | Adv | 9.2 | NS | Summer 2017/18 | http://dubbosolarhub.com.au/the-dubbo-solar-hub-gets-financed-and-starts-construction/
Nevertire SF | Epuron Island GP Pty Ltd |  | PV - single axis tracking | Solar | [5 empty] | Pub An | 105 | SS
Newcastle Gas Peaker | AGL Energy Limited |  | Reciprocating engines (gas/diesel) | Natural Gas / Diesel | [5 empty] | Pub An | 250 | S | Summer 2022/23
NSW Energy Cluster | Alinta |  | Wind - Onshore | Wind | [5 empty] | Pub An | 500 | SS | 01/07/2020
NSW Gas Peaker | AGL Energy Limited |  | Reciprocating engines (gas/diesel) | Natural Gas / Diesel | [5 empty] | Pub An | 500 | S
Orange Grove Solar Farm | Overland Sun Farming |  | PV Panels | Solar | [5 empty] | Pub An | 110 | SS
Paling Yards Wind Farm | Union Fenosa Wind Australia Pty Ltd | Units 1-55 | Wind - Onshore | Wind | ü |  |  |  |  | Pub An | 178 | SS |  | http://www.unionfenosa.com.au/portfolio/nsw-paling-yards/ , http://www.unionfenosa.com.au/nsw-paling-yards-project-documents/
Parkes Shire Council STP | TBA |  | PV Panels | Solar | [5 empty] | Pub An | 0.1074 | NS | Sep-2017
Parkes Solar Farm | Parkes Solar Farm Pty Ltd |  | PV Panels | Solar | ü | ü | ü | ü | ü | Com | 55 | SS | Summer 2017/18 | https://parkessolarfarm.com.au/
Riverina Solar Farm | Riverina Solar |  | PV Panels | Solar | [5 empty] | Pub An | 150 | SS |  | http://www.riverinasolar.com/about
Rye Park Wind Farm | Tilt Renewables Australia | 1- 109 | Wind - Onshore | Wind | [5 empty] | Pub An | 327 | SS | Mar-20
Sandigo Solar Farm | ESCO Pacific |  | PV Panels | Solar | [5 empty] | Pub An | 300 | SS |  | http://www.sandigosolarfarm.com.au/
Sapphire Wind Farm Phase 1 and 2 | Sapphire Wind Farm Pty Ltd | 75 | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 270 | SS | July-2018 | http://www.sapphirewindfarm.com.au/
Shoalhaven Expansion | Origin Energy |  | Pump Storage | Water | [5 empty] | Pub An | TBC | S
Silverton Wind Farm | PARF Company 8 Pty Ltd as trustee for the Silverton Project Trust | 58 | Wind - Onshore | Wind | ü | ü | ü | ü | ü | Com | 199 | SS | Winter 2018 | https://www.agl.com.au/about-agl/how-we-source-energy/renewable-energy/silverton-wind-farm
Snowy 2.0 | Snowy Hydro Ltd | 6 | Pump Storage | Water | [5 empty] | Pub An | 2000 | S
South Keswick Solar Farm | Dubbo Solar Hub Pty Ltd |  | PV Panels | Solar | ü | ü |  | ü | ü | Adv | 15 | NS | Summer 2017/18 | http://dubbosolarhub.com.au/the-dubbo-solar-hub-gets-financed-and-starts-construction/
Springdale Solar Farm | Renew Estate |  | PV Panels | Solar | [5 empty] | Pub An | 100 | SS
Summerhill Solar Farm | Newcastle Council |  | PV Panels | Solar | [5 empty] | Pub An | 5 | NS
Sundown Solar Farm | CWP Renewables Pty Ltd | 600 | PV Panels | Solar | [5 empty] | Pub An | 600 | SS
Sunraysia | Maoneng Australia Pty Ltd | 100 | PV - single axis tracking | Solar | ü |  |  |  |  | Pub An | 200 | SS
Suntop Solar Farm | Photon Energy |  | PV Panels | Solar | ü |  |  |  |  | Pub An | 260 | SS |  | http://www.photonenergy.com.au/current-projects/suntop-solar-farm/
Tarleigh Park Solar Farm | RES Australia Pty Ltd |  | PV Panels | Solar | [5 empty] | Pub An | 90 | SS
Tomago GT | Manildra Prop Pty Ltd as trustee for the Manildra Asset Trust | Inverters 1-60 | PV - single axis tracking | Solar | ü |  |  |  | ü | Pub An | 100 | SS |  | http://www.firstsolar.com/en-AU/Resources/Projects/Beryl-Solar-Farm
Tumut Pulp and Paper Mill | Visy |  | Biogas | Biogas | [5 empty] | Pub An | 32 | S
Upper Hunter Energy Park | Upper Hunter Energy Park Pty Limited | 22 | Wind - Onshore | Wind | [5 empty] | Pub An | TBC | SS
Uungula Wind Farm | Uungula Wind Farm Pty Ltd | 1-249 | Wind - Onshore | Wind | [5 empty] | Pub An | 650 | SS
Vales Point Solar | Delta Electricity |  | PV - single axis tracking | Solar | ü |  |  |  |  | Pub An | 45 | SS
Vast Solar Jemalong STEG Plant Phase 1 | TBA |  | Solar Thermal + Storage | Solar | [5 empty] | Pub An | 1.1 | NS | Jan-2017
Wagga Wagga Solar Farm (Southern Cross) | Terrain Solar |  | PV Panels | Solar | [5 empty] | Pub An | 22 | NS |  | https://www.terrainsolar.com/wagga
Wagga Wagga Solar Farm (Terrain) | Terrain Solar |  | PV Panels | Solar | [5 empty] | Pub An | 26 | NS
Walgett SF | Epuron Island GP Pty Ltd |  | PV - single axis tracking | Solar | ü |  |  |  |  | Pub An | 29 | NS |  | http://walgettsolarfarm.com.au/
Wee Waa Sun Farm | Overland Sun Farming |  | PV Panels | Solar | [5 empty] | Pub An | 55 | SS
Wellington | Manildra Prop Pty Ltd as trustee for the Manildra Asset Trust | 1 | PV - single axis tracking | Solar | [5 empty] | Pub An | 200 | SS |  | http://www.firstsolar.com/en/Resources/Projects/Wellington-Solar-Farm
Wellington North Solar Farm | AGL Energy |  | PV Panels | Solar | [5 empty] | Pub An | 300 | SS |  | https://www.agl.com.au/about-agl/how-we-source-energy/renewable-energy/wellington-north-solar-project
West Narrabi Electricity Generating Facility | Power Generation Partners |  | Biogas | Biogas | [5 empty] | Pub An | 55 | S
White Rock Solar Farm | White Rock Wind Farm Pty Ltd |  | PV - single axis tracking | Solar |  |  |  |  | ü | Com* | 20 | NS | Winter 2018 | http://whiterocksolarfarm.com
White Rock Wind Farm | White Rock Wind Farm Pty Ltd | Stage 2 uncommitted 71-119 | Wind - Onshore | Wind | ü | ü |  |  |  | Pub An | 122.5 | SS |  | http://whiterocksolarfarm.com
Woolbrook Wind Farm | Newtricity |  | Wind - Onshore | Wind | [5 empty] | Pub An | 120 | SS
Yass Valley Wind Farm | Yass Valley Wind Farm Pty Ltd | Wind turbines 1-79 | Wind - Onshore | Wind | [5 empty] | Pub An | TBC | SS
Com* - Identifies projects that are under construction, but AEMO has not been informed that the project meets all 5 commitment criteria.

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as semi-scheduled or non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as scheduled or non-scheduled. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW, unless AEMO approves its classification as scheduled or semi-scheduled.
Generating systems greater than 30 MW must be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating of less than 5 MW may be exempted by AEMO if its generation is purchased entirely by the local retail or a customer at the generator's connection point or the generator is classified as a market generating unit by a market small generation aggregator. A generating unit with a nameplate rating between 5 MW and 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of reliability assessments, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedance (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation and storage for which formal commitment has been made for construction or installation.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects are either under construction or meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction and connection approvals/EIS | The proponent has obtained all required planning consents, construction approvals, connection contracts (including Generator Performance Standard agreement from AEMO in the form of the 534A letter), and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.