## Index
The National Electricity Market Constraint Report 2016
Electronic Material – supplementary data
This supplement provides:
* Binding constraint equations (energy and FCAS separately)
* Market Impact of constraint equations
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page

## Binding 2016
Constraint Equation ID | 2016 Hours (2015 Hours) | Description | Type | Region
Q>NIL_BI_xxx | 1409 (259) | Out = Nil, avoid overloading on Boyne Island feeder bushing on Calliope River to Boyne Island 132 kV lines, for the contingent loss of a single Calliope River to Boyne Island 132 kV line There are three constraint equations that make up the thermal limit on the Boyne Island feeder bushing (for each of the 132 kV network configurations). All the binding results have been combined. | NIL | Qld
V::N_NIL_xxx | 1,054 (1,091) | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 1,015 (951) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. | NIL | Vic
N_X_MBTE_3A & N_X_MBTE_3B | 865 (1,312) | Out = all three Directlink cables | Outage | NSW
VT_ZERO | 628 (8) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
S>V_NIL_NIL_RBNW | 587 (452) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink. | NIL | SA
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 577 (177) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
N_X_MBTE2_A & N_X_MBTE2_B | 569 (1,044) | Out = two Directlink cables | Outage | NSW
VSML_220 | 468 (124) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
V::S_NIL_MAXG_xxx | 398 (243) | Out = Nil, avoid transient instability for trip of the largest generation unit in South Australia There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
V_S_NIL_ROCOF | 393 (0) | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | Vic
V>>N-NIL_HA | 368 (36) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL | Vic
VSML_ZERO | 302 (81) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
VS_250_DYN | 245 (18) | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Vic
V::S_TB_275KV_W_B_1 | 232 (0) | Out= Tailembend 275kV West Bus; Vic to SA Transient Stability limit for loss of the parallel South East - Tailem Bend line. (South East Capacitor Available) | Outage | SA
S-STTX_SNWF | 210 (1) | Out = Snowtown 132/33kV TX or Snowtown CB4593 or Snowtown CB6265, limit for Snowtown WF generation of 0 MW | Outage | SA
V:S_600_HY_TEST_DYN | 182 (0) | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
V^S_NIL_SA_RECLASS | 179 (0) | Out = NIL, limit generation in SA to prevent flow on Heywood interconnector exceeding 700 MW following reduction in MW output from multiple generating units in SA. | NIL | SA
SVML_ZERO | 174 (67) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
V::S_NIL_TBSE | 166 (21) | Out = Nil; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available) | NIL | SA
T>T_NIL_110_1 | 154 (107) | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
V^SML_NSWRB_2 | 154 (73) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
V>>S_NIL_KHTB2_KHTB1 | 153 (78) | Out = Nil, avoid overloading Keith to Tailem Bend #1 132 kV line on trip of Keith to Tailem Bend #2 132 kV line | NIL | SA
V::S_SETB_TBSE_1 | 150 (0) | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available).(NOTE: Assumed both Black Range series capacitors O/S). | Outage | SA
SVML_000 | 135 (0) | South Australia to Victoria on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | SA
V>>S_NIL_SETB_SGKH | 130 (265) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line This will bind for high import into SA with high levels of generation from the wind farms and gas turbines in the south east. | NIL | SA
#V-SA_E_E | 128 (0) | V-SA.ENERGY * 1 <= 580 (Wt = 35) | Outage | Quick
V:S_PA_SVC_575 | 124 (0) | Out= one Para SVC, Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 575 MW | Outage | Vic
#V-S-MNSP1_E_E | 115 (0) | V-S-MNSP1.ENERGY * 1 = 100 (Wt = 35) | Outage | Quick
N>LSDU_LSDU | 110 (5) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
V::S_NIL_TBSE_2 | 105 (0) | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
T>T_GTSH_IMP_4K | 103 (0) | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
V>>SML_NIL_CONT_7B | 101 (20) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Buangor to Arrarat 66kV line for loss of the Arrarat to Horsham 220kV line | NIL | Vic
V>>V_ROTS_TX_2A_R | 99 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 98 (1) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
S>>NIL_SETB_KHTB1 | 92 (172) | Out = Nil, avoid overloading Keith to Tailem Bend #1 132 kV line on trip of South East to Tailem Bend 275 kV line | NIL | SA
V>>V_BTRT_2A_R | 91 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 500kV, Feedback | Outage | Vic
T>T_TUMBNN1_110_1 | 88 (0) | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to New Norfolk No.3 110kV line, Feedback | Outage | Tas
T>T_NIL_BL_IMP_7CC | 87 (10) | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
NQTE_ROC | 86 (14) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
QNTE_ROC | 86 (14) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
T>>T_NIL_BL_EXP_7C | 83 (11) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
N^Q_NIL_A | 82 (4) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
N^^V_NIL_1 | 82 (212) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
T>>T_NIL_BL_EXP_6E | 80 (0) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
S>NIL_HUWT_STBG | 79 (1) | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line overload on loss of Hummocks - Waterloo line | NIL | SA
TV_ZERO | 78 (0) | Tas to Vic on Basslink upper limit of 0 MW | Outage | Tas
V>>V_BTRT_2B_R | 77 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 220kV, Feedback | Outage | Vic
#NYNGAN1_E | 75 (52) | Quick constraint equation to limit Nyngan solar farm to various levels This constraint equation was invoked in 2016 for the Nyngan solar farm commissioning. | Outage | Quick
V>>V_BTRT_2_P | 72 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Parallel Mode, Feedback | Outage | Vic
S_V_000_HY_DYN | 70 (0) | SA to VIC on Heywood upper transfer limit of 0 MW, dynamic headroom, DS formulation only. | Outage | SA
#BLUFF1_E | 70 (0) | SBEL2P.ENERGY * 1 <= 55 (Wt = 35) | Outage | Quick
N>N-BAMB_132_OPEN_A | 69 (0) | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | NSW
#HDWF1_E | 67 (0) | SHDW1H.ENERGY * 1 <= 30 (Wt = 35) | Outage | Quick
V>>N_DDMS_2 | 66 (3) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Dederang to Murray 330 kV line, feedback | Outage | Vic
S>>KHKN_SETB_SGKH | 64 (7) | Out = Keith - Kincraig 132 kV line; avoid O/L of Snuggery - Keith 132kV line on trip of either South East - Tailem Bend 275 kV line | Outage | SA
V::S_XKHTB1+2_MAXG | 62 (87) | Out = both Keith to Tailem Bend 132 kV lines, avoid transient instability for trip of the largest generation unit in South Australia | Outage | SA
N>>N-NIL__3_OPENED & CLOSED | 61 (26) | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
Q:N_NIL_AR_2L-G | 61 (388) | Out = Nil, avoid transient instability for a 2 line to Ground fault at Armidale | NIL | Qld
S_LB3_0 | 61 (138) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
V>>N-BUDP_2N | 58 (0) | Out= Buronga-DarlingtonPt(X5), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
V::S_BLKRG_TBSE_2 | 55 (0) | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V>>V_KTS_TX_A2_2A_R | 55 (3) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
#NBHWF1_E | 49 (0) | SBEL1A.ENERGY * 1 <= 135 (Wt = 35) | Outage | Quick
#TORRB1_E | 49 (0) | STSB1.ENERGY * 1 <= 200 (Wt = 360) | Outage | Quick
V>>S_KNPW_SETB_SGKH | 48 (16) | Out= Kincraig - Penola West 132kV line, avoid O/L Snuggery - Keith 132kV on trip of one South East - Tailem Bend 275kV line, Feedback | Outage | SA
V_T_NIL_FCSPS | 48 (526) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
V:S_600_HY_TEST | 48 (0) | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
NSA_Q_BARCALDN | 47 (11) | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
#SNOWTWN1_E | 46 (0) | SNWF1T.ENERGY * 1 <= 0 (Wt = 35) | Outage | Quick
I_CTRL_ISSUE_TE | 44 (119) | DC Link Control Issue Constraint for Terranora | Outage | Other
V_MTMERCER_ZERO | 44 (5) | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
S>NIL_WERB_WEWT | 44 (3) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
#HALLWF2_E | 44 (0) | SMOK1H.ENERGY * 1 <= 0 (Wt = 35) | Outage | Quick
NSA_S_PORxxx | 43 (33) | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
#QPS5_E | 41 (0) | SQPS5Q.ENERGY * 1 >= 74 (Wt = 35) | Outage | Quick
#N-Q-MNSP1_I_E | 40 (5) | Quick constraint equation applied to Terranora Interconnector at various levels | Outage | Quick
V:S_PA_VC-POD_600 | 40 (0) | Out= One Para SVC POD O/S (with associated SVC I/S)(Note: with both Black Range Series caps I/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 600 MW | Outage | Vic
T_MRWF_QLIM_xx | 40 (59) | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
V::N_HYSE_xxx | 40 (266) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
N_NYNGANSF_051 | 39 (0) | Nyngan Solar Farm upper limit of 51 MW (50% capacity) | Outage | NSW
V_MACARTHUR_ZERO | 39 (5) | Macarthur upper limit of 0 MW | Outage | Vic
V>>V_KTSY_1_R | 39 (1) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
V:S_PA_SVC_600 | 38 (0) | Out= one Para SVC (Note: both Black Range series caps I/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 600 MW | Outage | Vic
S>NIL_NIL_NWMH2 | 37 (2) | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
SV_000 | 37 (0) | SA to Victoria on VicSA upper transfer limit of 0 MW | Outage | SA
V^S_HYCP | 36 (32) | Out = NIL, maintain adequate post contingent voltages for loss of the Heywood to Mortlake 500 kV line. | NIL | Vic
V^^S_MLSY_3 | 36 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
S>>NIL_TBCG_TBTU_1 | 35 (0) | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | SA
S>V_NWRB2_RBNW1 | 35 (94) | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage | SA
V::S_BLKRG_MAXG_2 | 35 (0) | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
SVML_ROC_80 | 34 (0) | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
V::N_HWSM_xxx | 34 (16) | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
S>>MOTB_TBTU_TBCG | 34 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
V>>SML_NIL_7B | 33 (35) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
#N-Q-MNSP1_E_E | 33 (0) | N-Q-MNSP1. * 1 = -57 (Wt = 0.0001) | Outage | Quick
V_S_ROCOF | 32 (15) | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | Vic
S>>NIL_HUBG-T_WEWT | 32 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Hummocks-Snowtown-Bungama 132kV T line (this trips Snowtown WF), Feedback | NIL | SA
#TNPS1_E | 32 (0) | QTNT.ENERGY * 1 <= 300 (Wt = 360) | Outage | Quick
V>SMLBAHO4 | 31 (77) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage | Vic
V>>N-DDWO_RADIAL_2 | 30 (2) | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V>>V_MLSY_KTSBP_1AR | 29 (0) | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage | Vic
S>>X_TB-EBUS+CGTB_3 | 28 (0) | Out = Tailembend 275kV East Bus (i.e. and associated CBs) + Cherry Gardens-Tailembend 275kV line +Tailembend CBs 6535 & 6536 O/S, avoid O/L TB-MO #1 132kV line on trip of SE-TB #2 275kV line (this offloads SE-TB #1 275kV & TB-TU 275kV lines), | Outage | SA
S-SNWWF_0 | 28 (4) | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
VSML_ROC_80 | 27 (0) | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
NRM_VIC1_SA1 | 27 (0) | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
#TORRB4_E | 26 (0) | STSB4.ENERGY * 1 >= 40 (Wt = 1160) | Outage | Quick
#LKBONNY3_E | 25 (0) | SMAY3W.ENERGY * 1 <= 35 (Wt = 35) | Outage | Quick
V>SML_BUDP_2 | 25 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
NSA_V_BDL0xxx | 25 (10) | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
NC_N_SITHE01 | 25 (3) | Non Conformance Constraint for Smithfield Energy Facility | Outage | Non-Conformance
V^^S_TB_275KV_E_SETB | 24 (0) | Out= Tailembend 275kV East Bus(i.e. CBs 6594, 6535 and 6597 OPEN with Tailembend 275/132kV TX4 & C64 O/S); Vic to SA Long Term Voltage Stability limit for loss of one South East-Tailembend 275kV line (NOTE: NPS and Playford assumed to be O/S) | Outage | SA
T^V_NIL_9 | 24 (3) | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
N_NYNGANSF_010 | 23 (0) | Nyngan Solar Farm upper limit of 10 MW | Outage | NSW
#HALLWF1_E | 23 (0) | SHPS2W.ENERGY * 1 <= 30 (Wt = 35) | Outage | Quick
#LKBONNY2_E | 22 (8) | SMAY2.ENERGY * 1 <= 130 (Wt = 35) | Outage | Quick
N_BROKENH1_ZERO | 22 (0) | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
V::N_BUDP_xxx | 22 (1) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
V:S_500_HY_TEST_DYN | 21 (0) | VIC to SA on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
V>>V_DDSM_1 | 21 (0) | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Vic
V>S_NWRB2_NWRB1 | 21 (14) | Out = North West Bend to Robertstown No.2 132 kV line, avoid overloading North West Bend to Robertstown No.1 132 kV line | Outage | SA
Q>NIL_MRTA_B | 20 (20) | Out = Nil, avoid overloading Middle Ridge to Tangkam (732) 110 kV line on no contingencies | NIL | Qld
V>S_CB6033+6225_TX1 | 20 (44) | Out = North West Bend CB6033 and CB6225, avoid overloading North West Bend transformer #1 132/66kV transformer on trip of Monash to North West Bend #2 132kV line or North West Bend to Morgan Whyalla Pump 1 132 kV line | Outage | Vic
S>>BRMN_BWPA_HUWT | 20 (2) | Out= Brinkworth - Mintaro (or any line section between Brinkworth and Mintaro) 132kV line, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
#TARONG#1_E | 19 (0) | QTRN1.ENERGY * 1 <= 350 (Wt = 360) | Outage | Quick
T>T_FASH_1_2_C1 | 19 (0) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, West Coast 220/110 kV parallel closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
V::N_SMSC_xxx | 19 (3) | Out = 1 x South Morang Series Capacitor 330kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V>S_460_DYN | 18 (6) | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Vic
V::S_HYSE | 18 (4) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of the remaining South East - Heywood 275 kV line. | Outage | SA
S>>V_NIL_SETX_SETX1 | 18 (0) | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
V::S_MOTB_MAXG | 17 (8) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
#PPCCGT_E | 17 (0) | SPPT.ENERGY * 1 >= 162 (Wt = 1160) | Outage | Quick
S>NIL_SGBN_SGSE-T2 | 17 (0) | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
N>N-CHKK_TE_1 | 17 (0) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
V:SS_820_HY_TEST_DYN | 16 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
S>BRTW_BWPA_HUWT | 16 (9) | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
#CLEMGPWF_E | 15 (0) | SCGW1P.ENERGY * 1 <= 60 (Wt = 35) | Outage | Quick
S>>V_NIL_SETX_SETX | 15 (75) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer This constraint equation binds when there is export from South Australia to Victoria and high generation from the wind farms and gas turbines in the south east of South Australia. | NIL | SA
Q>NIL_BI_CAGS_CLOSED | 15 (0) | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104/7105 (T022 Callide A to T152 Gladstone South) 132 kV lines closed with 132 kV split between T022 Callide A and H015 Lilyvale. | NIL | Qld
N_NYNGANSF_ZERO | 15 (0) | Nyngan Solar Farm upper limit of 0 MW | Outage | NSW
N>N-NIL_LSDU | 14 (5) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
NC_V_YWPS1 | 14 (43) | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Outage | Non-Conformance
N>>N-NIL__3_OPENED & CLOSED | 14 (26) | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
S>>BWMP_DVBR_RHBG-T | 14 (1) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | SA
V::N_DDSM_xxx | 14 (3) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S>>CNRB_MKRB_WEMWP4 | 14 (0) | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | SA
NSA_Q_GSTONE34_xxx | 14 (151) | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
T::T_NIL_2 | 13 (29) | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
S>NIL_BWMP_HUWT | 13 (1) | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
NC_V_YWPS2 | 13 (35) | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Outage | Non-Conformance
V_T_NIL_BL1 | 13 (537) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
S_WTE_0 | 13 (1) | Discretionary upper limit for Waterloo generation of 0 MW | Outage | SA
V::S_XKHTB1+2_SETB | 13 (105) | Out = both Keith to Tailem Bend 132 kV lines, avoid transient instability for trip a South East to Tailem Bend 275 kV line | Outage | SA
#SNOWNTH1_E | 12 (0) | SBLWS1.ENERGY * 1 <= 80 (Wt = 35) | Outage | Quick
S>>CNDV_MKRB_WEMWP4 | 12 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4- Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet 2 windfarm), Feedback | Outage | SA
V::N_HYTR_xxx | 12 (2) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
NC_V_YWPS4 | 12 (21) | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Outage | Non-Conformance
S>>X_CGTB+TB35+36_08 | 12 (0) | Out= Cherry Gardens- Tailembend 275kV line & Tailembend 275kV CBs 6536 & 6535, avoid O/L Snuggery-Keith 132kV line on trip of South East -Tailembend 275kV #2 line(this offloads South East -Tailembend 275kV #1 line), Feedback | Outage | SA
V>>V_CBTS_TX_2A_R | 12 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
NC_V_YWPS3 | 11 (33) | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Outage | Non-Conformance
S>>NIL_SETB_SETB_1 | 11 (0) | Out= Nil, avoid O/L one South East-Tailem Bend 275kV on trip of other South East-Tailem Bend 275kV line, feedback | NIL | SA
V^^S_TBCPTX_MAXG | 11 (0) | Out= Tailem Bend 275/132kV transformer and Tailem Bend 100Mvar Cap Bank; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage | SA
V:SS_PA_SVC_795 | 11 (0) | Out= one Para SVC, Oscillatory stability limit for Vic to SA on Heywood+ Murrylink upper transfer limit of 795 MW | Outage | Vic
V:T_SHGT_BL_1 | 11 (0) | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
S>>X_CGTB+TB35+36_13 | 11 (1) | Out= Cherry Gardens- Tailembend 275kV line & Tailembend 275kV CBs 6536 & 6535, avoid O/L Tailembend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line(this offloads Tailem Bend 275/132kC TX4), Feedback | Outage | SA
V^^S_MLSY_2 | 11 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
V::N_SMF2_xxx | 10 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V::S_NIL_SETB_SECP | 10 (0) | Out = Nil; Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V_ARARAT_5 | 10 (0) | Ararat Wind Farm upper limit of 5 MW, limit to manage islanding risk | Outage | Vic
N_MBTE1_B | 10 (53) | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
T>T_FASH_1_N-2 | 10 (2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
V^^S_XPAVC_SETB_2 | 10 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps) O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V^^S_BLKRG_TBSE_2 | 10 (0) | Out = both Black Range series capacitors O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V::N_KGRC_xxx | 10 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T_FASH_MAXGEN_1 | 9 (1) | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
T::T_NIL_4 | 9 (26) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
T>T_X_BWLF_TUMBNN1_1 | 9 (0) | Out= either Bridgewater to Lindisfarne or Bridgewater to Waddamana 110kV line and Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to New Norfolk No.3 110kV line, Feedback | Outage | Tas
TV_470 | 9 (0) | Tas to Vic on Basslink upper limit of 470 MW | Outage | Tas
V>>N-JNWO_RADIAL_2 | 9 (0) | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
N^^V_MSDD2 | 9 (0) | Out = Dederang to Murray 330 kV line, avoid voltage collapse for trip of the remaining Dederang to Murray 330 kV line | Outage | NSW
V::N_DDWO_xxx | 9 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S_TBL_0 | 8 (0) | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
S>MYTX2_MYTX1 | 8 (7) | Out = Mayura 132/33 kV transformer #2 with the 33kV bus tie isolator 44248 closed or open, avoid O/L Mayura 132/33 kV transformer #1, Feedback. | Outage | SA
S>NIL_BWMP_RHBR-T | 8 (2) | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
V::N_BAHO_xxx | 8 (12) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
CA_SPS_46545836_02 | 8 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
S_SNOWSTH1_ZERO | 8 (2) | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW | Outage | SA
T^V_NIL_BL_6 | 8 (6) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
V::N_X_2SVC_xxx | 8 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
S_SNOWNTH1_ZERO | 8 (1) | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW | Outage | SA
S_PLN_ISL2 | 8 (0) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
NRM_SA1_VIC1 | 7 (0) | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
N_GULLRWF1_ZERO | 7 (4) | Gullen Range WF upper limit of 0 MW | Outage | NSW
S>>NIL_RBTU_WEWT | 7 (3) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
S>>X_DVCN+CNRB+CB_10 | 7 (0) | Out= Davenport-Canowie-Robertstown 275kV and Robertstown 275kV CBs 6616 and 6571, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
V::N_MLSY_xxx | 7 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
T>T_TUNN3_110_1 | 7 (0) | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
V>>V_KTS_TX_A3_2A_R | 7 (2) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
NRM_QLD1_NSW1 | 7 (2) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V::N_EPMB_xxx | 7 (11) | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
Q>NIL_MRTA_A | 7 (10) | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line. | NIL | Qld
S::V_TBSE_TBSE | 7 (0) | Out = one Tailembend-South East 275kV line; SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
V::S_BLKRG_TBSE_3 | 7 (0) | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V>>V-JNWG_RADIAL_1A | 7 (0) | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage | Vic
#VP6_E | 7 (0) | NVPP6.ENERGY * 1 <= 450 (Wt = 360) | Outage | Quick
V:S_570_HY_TEST_DYN | 7 (0) | VIC to SA on Heywood upper transfer limit of 570 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
V>>V-MSUT_1 | 7 (3) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | Outage | Vic
CA_SPS_46BA5824_01 | 7 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
N^^Q_ARTW_B1 | 7 (14) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
Q:N_AR_CP2_AR_2L-G | 7 (9) | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
V>SMLMHNW2 | 7 (0) | Out = Monash-North West Bend # 2 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 1 132kV line | Outage | Vic
CA_SPS_46954420_01 | 6 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
I_CTRL_ISSUE_ML | 6 (9) | DC Link Control Issue Constraint for Murraylink | Outage | Other
S>>BRTW_BWPA_WTTP | 6 (19) | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>X_DVCN+CNRB+CB_16 | 6 (0) | Out= Davenport-Canowie-Robertstown 275kV and Robertstown 275kV CBs 6616 and 6571, avoid O/L Waterloo East-MWP4-RB 132kV line on trip of Mokota-Robertstown 275kV line(this offloads Belalie-Mokota 275kV line, RBTX1 and trips Hallet Hill WF), Feedback | Outage | SA
S_PLN_ISL32 | 6 (0) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T>T_NIL_BL_IMP_6E | 6 (0) | Out = Nil, avoid overloading Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) on trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action | NIL | Tas
V::N_KTSY_xxx | 6 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#TORRA3_E | 6 (0) | STSA3.ENERGY * 1 <= 60 (Wt = 360) | Outage | Quick
NC_N_TALWA1 | 6 (4) | Non Conformance Constraint for Tallawarra Power Station | Outage | Non-Conformance
V>>S_NIL_PWKN_SGKH | 6 (48) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL | SA
NC_Q_BRAEMAR1 | 6 (1) | Non Conformance Constraint for Braemar 1 Power Station | Outage | Non-Conformance
V::N_BYPASS_HW_SY_xxx | 6 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
S_V_NIL_ROCOF | 6 (0) | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | SA
N::Q_RGSW_KC | 6 (0) | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
#OAKLAND1_E | 6 (0) | VTGT3A.ENERGY * 1 <= 30 (Wt = 360) | Outage | Quick
#PPCCGT_D_E | 6 (0) | SPPT.ENERGY * 1 = 160 (Wt = 755) | Outage | Quick
V>>SML_NIL_MLTS_N-2 | 6 (23) | Out= Nil, avoid O/L Elaine to Ballarat 220kV line section on trip of Moorabool to Ballarat and Moorabool to Terang 220kV lines, Feedback | NIL | Vic
#ARWF1_E | 5 (0) | VART1A.ENERGY * 1 <= 120 (Wt = 360) | Outage | Quick
V::N_X_MLSM_EMTT_xxx | 5 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V:S_X-PA_S+P_525 | 5 (0) | Out= One Para SVC and other Para SVC POD O/S (Note: with both Black Range Series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 525 MW. | Outage | Vic
VS_350 | 5 (0) | Victoria to SA on VicSA upper transfer limit of 350 MW | Outage | Vic
S>>V_KNPW_SETX_SETX | 5 (1) | Out = Kincraig to Penola West 132 kV line, avoid overloading the remaining South East 275/132kV transformer on trip of one South East 275/132kV transformer | Outage | SA
N_GUNNING1_ZERO | 5 (6) | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
V:S_SA_PSS | 5 (0) | Out= Nil; Vic to SA Oscillatory stability limit on Heywood Interconnector based on SA Generator PSS out of service when associated generator is inservice (Note: Both Para SVCs assumed to be I/S). | NIL | Vic
N>>N-DTKV_E_15M | 5 (0) | Out = Dapto-KangarooValley(18), avoid O/L Canberra to Yass(9) on trip of Lower Tumut to Yass (3) line, Feedback | Outage | NSW
#MORTLK12_D_E | 5 (0) | VM0P2O.ENERGY * 1 = 0 (Wt = 755) | Outage | Quick
NC_Q_BRAEMAR3 | 5 (1) | Non Conformance Constraint for Braemar 3 Power Station | Outage | Non-Conformance
#TORRA4_E | 5 (0) | STSA4.ENERGY * 1 >= 40 (Wt = 1160) | Outage | Quick
V>>N_SMHTX_1 | 5 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V^^S_XPACP_MAXG | 5 (0) | Out = Para C61 and C62 capacitor banks (both capacitors) O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
S>V_CB6033+6225_TX2 | 5 (38) | Out= North West Bend_CB6033 and CB6225; avoid O/L of North West Bend transformer 132/66kV #2 on trip of either Robertstown-NWB #2 132kV line or NWB-Monash #2 132kV line . | Outage | SA
#MOREESF1_E | 5 (0) | NMR41M.ENERGY * 1 <= 28 (Wt = 35) | Outage | Quick
NC_N_HUMENSW | 5 (13) | Non Conformance Constraint for Hume Hydro Power Station | Outage | Non-Conformance
S>>NIL_TBTU_TBMO_1 | 5 (0) | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
V:S_500_HY_TEST | 5 (0) | VIC to SA on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
V>SMLHORC2 | 5 (0) | Out = Horsham to Redcliffs 220kV line, avoid overloading Bendigo to Kerang 220kV line for trip of Balranald to Darlington Point (X5/1) 220kV line | Outage | Vic
NC_N_VP5 | 4 (3) | Non Conformance Constraint for Vales Point VP5 Power Station | Outage | Non-Conformance
N^^Q_LS_VC_B1 | 4 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V:SS_PA_SVC_820 | 4 (0) | Out= one Para SVC(Note: both Black Range series caps I/S), Oscillatory stability limit for Vic to SA on Heywood+ Murrylink upper transfer limit of 820 MW | Outage | Vic
V>>SML_ARWB_6 | 4 (0) | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
VTBL_ROC | 4 (11) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
N>>N-DTSS_20 | 4 (0) | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage | NSW
N>N_LSDU_9U6_1 | 4 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | NSW
S>NWCB6024+25_TX3 | 4 (4) | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
N^^V_DDSM1 | 4 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
SA_HYSE1 | 4 (1) | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage | SA
S^NIL_PL_MAX | 4 (0) | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
V>>N-JNWO_RADIAL_1 | 4 (0) | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
V>V_HWJL3-4_RAD | 4 (0) | Outage=Hazelwood to Jeeralang #3 or #4 220kV line OR Jeeralang 220kV #2 bus CB for HWPS-JLTS #3 or #4 220kV line, avoid O/L HWTS A1 Tx for trip of HWPS-JLTS #4 or #3 220kV line, Radial Mode with 1&2 bus split and 3&4 bus split or tied | Outage | Vic
NC_N_MP1 | 4 (13) | Non Conformance Constraint for Mt Piper 1 Power Station | Outage | Non-Conformance
N^^Q_TW_330_BUS1_B1 | 4 (0) | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | NSW
T>T_NIL_BL_220_6B | 4 (0) | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
V::N_X_HWSM_ROTX_xxx | 4 (0) | Out = Hazelwood to South Morang 500kV line and Rowville (A) TX, prevent transient instability for trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_PAVC1_MAXG | 4 (0) | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | SA
V>>N_SMHTX_2 | 4 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V:S_550 | 4 (0) | Maintain maximum transfer limit of 550 MW on Heywood IC from Vic to SA to avoid oscillatory instability | Outage | Vic
NC_Q_STAN-2 | 4 (0) | Non Conformance Constraint for Stanwell STAN-2 Power Station | Outage | Non-Conformance
S>>BWMP_HUWT_RHBG-T | 4 (0) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill-Brinkworth 132kV T line on trip of Hummocks-Waterloo 132kV line, Feedback | Outage | SA
T>>T_GTSH_EXP_3H | 4 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage | Tas
T>T_PMSH_IMP_4E | 4 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
TV_500 | 4 (0) | Tas to Vic on Basslink upper limit of 500 MW | Outage | Tas
#WATERLWF_E | 4 (0) | SWLE.ENERGY * 1 <= 10 (Wt = 35) | Outage | Quick
S>>BRDV_RBTU_WEWT | 4 (0) | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
S>>BWMP_BGBR_HUWT | 4 (0) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | SA
V::S_PAVC1_SETB | 4 (0) | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | SA
V>>S_KHTB1_SETB_KHTB | 4 (27) | Out = Keith - Tailem Bend #1 132 kV line, avoid O/L on Keith - Tailem Bend #2 line for trip of either South East - Tailem Bend lines. | Outage | SA
VN_0800 | 4 (0) | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage | Vic
V::S_SETB_SETB | 4 (59) | Out = South East to Tailem Bend 275 kV line, avoid transient instability for loss of the parallel South East to Tailem Bend 275 kV line | Outage | SA
V>S_460 | 4 (261) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | Outage | Vic
N>>N-NIL_01N | 4 (0) | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
NRM_NSW1_VIC1 | 4 (10) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
SA_HYSE2 | 4 (0) | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
V::N_ROSM_xxx | 4 (5) | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
#TORRA1_O_R6 | 4 (0) | STSA1.RAISE6SEC * 1 = 10 (Wt = 60) | Outage | Quick
#TORRA1_P_R6 | 4 (0) | STSA1.RAISE6SEC * 1 <= 0 (Wt = 12) | Outage | Quick
N::V_GRYS_2 | 4 (0) | out = Gullen Range to Yass (3J), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | NSW
V>>N-NIL_HG | 4 (0) | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
N^^V_DDSM2 | 3 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse for loss of remaining Dederang to South Morang 330 kV line | Outage | NSW
S-LB2_0 | 3 (8) | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
TVBL_ROC | 3 (12) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
V>>V_MLSY_4BR | 3 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
V>SML_BUDP_5 | 3 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid O/L Ballarat to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line, feedback | Outage | Vic
NC_V_HWPS8 | 3 (1) | Non Conformance Constraint for Hazelwood HWPS 8 Power Station | Outage | Non-Conformance
S>CNDV_BWMP_HUWT | 3 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N::Q_NIL_KC | 3 (0) | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | NSW
N^^V_SMTXH1_1 | 3 (0) | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
T>T_HAPM_5L | 3 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L line terminal equipment of Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line, feedback | Outage | Tas
T_T_BA_JB_RC2_250 | 3 (2) | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
V:SS_PA_VC-POD_820 | 3 (0) | Out= one Para SVC(Note: both Black Range series caps I/S), Oscillatory stability limit for Vic to SA on Heywood+ Murrylink upper transfer limit of 820 MW | Outage | Vic
N^N-X_96H_LS_SVC | 3 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage | NSW
N_MBTE1_A | 3 (0) | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
V:SS_820_HY_TEST | 3 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
Q:N_DM_CB_AR_2L-G | 3 (7) | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
QNTE_ZERO | 3 (0) | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage | Qld
V:S_570_DYN | 3 (0) | Out = NIL, VIC to SA on Heywood upper transfer limit of 570 MW based on oscillatory stability, dynamic headroom, DS formulation only. | NIL | Vic
T>>T_HAPM_EXP_3H | 3 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
V::S_NIL_TBSE_1 | 3 (0) | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
N::V_CNUT_2 | 3 (4) | Out = Upper Tumut -Canberra(01), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | NSW
#TORRA2_E | 3 (0) | STSA2.ENERGY * 1 <= 120 (Wt = 360) | Outage | Quick
V::N_JNWG_xxx | 3 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
N_MOREESF1_ZERO | 3 (0) | Moree Solar Farm upper limit of 0 MW | Outage | NSW
Q>N-MUTE_757 | 3 (0) | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
T^^V_GTSH_1 | 3 (0) | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
#PPCCGT_O_E | 2 (0) | SPPT.ENERGY * 1 <= 165 (Wt = 755) | Outage | Quick
S::V_TBSE_TBSE_1 | 2 (0) | Out = one Tailembend-South East 275kV line; SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
S_LB2WF_CONF | 2 (8) | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
NC_Q_BRAEMAR2 | 2 (1) | Non Conformance Constraint for Braemar 2 Power Station | Outage | Non-Conformance
N^N_KKLS_1 | 2 (13) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
V>>N-JNWG_RADIAL_1 | 2 (0) | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
NC_Q_TNPS1 | 2 (1) | Non Conformance Constraint for Tarong North Power Station | Outage | Non-Conformance
S>RBTX1_RBTX2_WEMWP4 | 2 (20) | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, Feedbac | Outage | SA
V>>V_BTRT_SMF2_KT_DR | 2 (0) | Out=Brunswick-Richmond 220kV cable and South Morang F2 500/330kV TX, with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypass KTS to WMTS, avoid O/L Rowville-Thomastown 220kV line on trip of Rowville A1 500/220kV TX, Radial, YWPS1 on 500kV, Feedback | Outage | Vic
NRM_VIC1_NSW1 | 2 (1) | Negative Residue Management constraint equation for VIC to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
S_BLNBH_0 | 2 (1) | Outage of Belalie-North Brown Hill 275kV line | Outage | SA
V::S_X_KHTB1+SG_SETB | 2 (0) | Out = Keith-Tailem Bend #1 132kV & Keith-Snuggery 132kV; Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage | SA
V>>V_SMTXF2_6 | 2 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage | Vic
CA_SPS_4733E84B_01 | 2 (0) | Constraint Automation, O/L 9 @CANBERRA for CTG LNPY on trip of DAPTO-KANGAROO 18 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
T>T_NIL_LIPM_N-2_2A | 2 (0) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to North) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
T^V_NIL_11 | 2 (1) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
V::N_HORC_xxx | 2 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_KTSY_MLSM_ET_xxx | 2 (0) | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_BNMT_MAXG_2 | 2 (0) | Out= Blanche - Mt Gambier 132kV line; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
NC_N_MP2 | 2 (7) | Non Conformance Constraint for Mt Piper 2 Power Station | Outage | Non-Conformance
NC_V_HWPS3 | 2 (0) | Non Conformance Constraint for Hazelwood HWPS 3 Power Station | Outage | Non-Conformance
S>MYTX1_44248OPN_LB2 | 2 (0) | Out = Mayura No.1 132/33kV transformer O/S (with 33kV bus tie isolator 44248 open), Lake Bonney 2 Windfarm is constraint to a max of 60 MW | Outage | SA
V::S_KHTB1_SETB | 2 (0) | Out= Keith - Tailem Bend #1 132 kV line; Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
V^^S_XPAVC_MAXG_2 | 2 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps) O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
NC_Q_BARRON-2 | 2 (0) | Non Conformance Constraint for Barron Gorge 2 Power Station | Outage | Non-Conformance
T^V_NIL_BLCAP | 2 (0) | Outage = Nil, Basslink HF7 98 MVAr cap bank unavailable, limit Basslink to 460 MW at George Town under conditions of low George Town 220 kV voltage. | NIL | Tas
T_V_NIL_BL1 | 2 (6) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
V>V_NIL_RADIAL_10 | 2 (0) | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Vic
N>>V_DBUSS_1 | 2 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line DBUSS - line is a control scheme that splits Dederang 330 kV bus on trip of a Murray to Dederang line. This was implemented to allows higher NSW to Vic interconnector capability. For a number of outages in southern NSW and northern Victoria either the line or transformer control schemes are also taken out of service. | Outage | NSW
T_GO_ZERO | 2 (0) | Discretionary 0 MW upper limit on total Gordon generation | Outage | Tas
V::N_MLMO_xxx | 2 (1) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V>>V_NIL_1B | 2 (0) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
N>>N-BYSW_B | 2 (0) | Out = Bannaby-Sydney West(39), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage | NSW
NC_V_BDL01 | 2 (1) | Non Conformance constraint equation for Bairnsdale 1 Power Station | Outage | Non-Conformance
N_NIL_TE_B | 2 (0) | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
T^T_NIL_BL_6_DS | 2 (0) | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah-Waddamana-Palmerston 220 kV line, dispatch equation only | NIL | Tas
V>V_ROYP78_1AR | 2 (0) | Out = Rowville to Yallourn No. 7 or No. 8 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 8 or No. 7 220 kV line for trip of the Rowville to Yallourn No. 6 220 kV line, Yallourn W1 on 220 kV, feedback | Outage | Vic
N>>N-NIL__S | 2 (0) | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL | NSW
N>Q-MUTW_2 | 2 (1) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage | NSW
NC_S_WATERLWF | 2 (2) | Non Conformance Constraint for Waterloo Windfarm | Outage | Non-Conformance
N_WOODLWN1_ZERO | 2 (10) | Discretionary upper limit for Woodlawn generation of 0 MW | Outage | NSW
S>MYTX1_MYTX2 | 2 (24) | Out = Mayura 132/33 kV transformer #1 with the 33kV bus tie isolator 44248 open or closed, avoid O/L Mayura 132/33 kV transformer #2, Feedback | Outage | SA
T>T_NIL_LIPM_N-2_2B | 2 (3) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
V^^S_PWSE_SETB | 2 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
S>>NIL_SETB_KHTB2 | 2 (30) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
S>NIL_NIL_SETX12 | 2 (0) | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
V>V_NIL_RADIAL_9 | 2 (15) | Out = Nil, avoid O/L of Hazelwood to Jeeralang No. 4 220 kV line for trip of Hazelwood A4 500/220 kV transformer, Yallourn unit 1 in 500kV mode, radial mode, Hazelwood 3,4 busses split, feedback. | NIL | Vic
N^^N_NIL_1 | 1 (0) | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
S>V_NIL_SETX_SETX1 | 1 (0) | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
V>>S_MOTB_TBCG_TBTU | 1 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage | SA
V>>V_BTTT1MLSY_KT_AR | 1 (0) | Out = Brunswick to Thomastown #1 220kV and one Moorabool to Sydenham 500kV line, with KTS 220kV bus #1 & #2 tied and both TTS-KTS lines bypass KTS to WMTS, avoid O/L SMTS F2 txfmr on trip of ROTS A1 500/220kV txfmr, Radial Mode, YWPS1 on 500kV, Feedback | Outage | Vic
V>>V_NIL_8 | 1 (2) | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
NC_V_LYA1 | 1 (2) | Non Conformance Constraint for Loy Yang A1 Power Station | Outage | Non-Conformance
S>>PWSE_SETB_SETB_2 | 1 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps O/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage | SA
T_FAJB | 1 (1) | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Tas
T_V_FCSPS_RAMP | 1 (0) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
T_X_GTSH_1 | 1 (0) | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation <= West Coast + North West load + 10MW, limiting SH-PM line flow to 10 MW | Outage | Tas
#NSW1-QLD1_RAMP_I_F | 1 (5) | NSW1-QLD1 >= MIN(-293, InitialFlow + 200) (Wt=35) | Outage | Quick
NC_N_VP6 | 1 (1) | Non Conformance Constraint for Vales Point VP6 Power Station | Outage | Non-Conformance
S>>V_NIL_NIL_HUWT | 1 (0) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL | SA
S_HALWF_0 | 1 (2) | Discretionary upper limit for Hallett wind farm generation of 0 MW | Outage | SA
V::S_NIL_SETB_SECP_1 | 1 (0) | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V>>N-CNUT_HB_15M | 1 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
V>>V_NIL_1A | 1 (0) | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
VN_0950 | 1 (0) | Discretionary Vic to NSW transfer upper limit of 950 MW | Outage | Vic
V>NWB6024_TX1 | 1 (0) | Out= North West Bend 132kV CB6024, avoid O/L North West Bend 132/66kV #1 TX on trip of Monash-NorthWest Bend #1 132kV line, Feedback | Outage | Vic
#SNOWSTH1_E | 1 (0) | SBLWS2.ENERGY * 1 <= 50 (Wt = 35) | Outage | Quick
N::Q_BWTX_KC | 1 (0) | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
S>>BRMN_BWPA_BRTW | 1 (0) | Out= Brinkworth - Mintaro (or any line section between Brinkworth and Mintaro) 132kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>V_NIL_WTTP_WEMW4 | 1 (0) | Out = Nil, avoid overloading the Waterloo East to Morgan Whyalla pump 4 132 kV line on trip of the Waterloo to Templers 132 kV line | NIL | SA
S>NIL_PL_GENMAX_YDMD | 1 (0) | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | SA
V::S_TBCP1_SETB_2 | 1 (0) | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V:S_ARDM_560 | 1 (0) | Maintain maximum transfer limit of 560 MW on Heywood IC from VIC to SA to avoid oscillatory instability | Outage | Vic
V>>V_NIL_6A_R | 1 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL | Vic
#SA1_E_20160801 | 1 (0) | Multiple SA1 LHS = 0 (Wt = 35) | Outage | Quick
N::V_MNYS_2 | 1 (0) | Out= Marulan-Yass (4 or 5), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | NSW
N>>N-NIL_64 | 1 (0) | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | NSW
N>N-96H+LSTX_TE_1 | 1 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore 330/132kV Tx, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
NC_Q_MACKAYGT | 1 (0) | Non Conformance Constraint for Mackay Gas Turbine | Outage | Non-Conformance
NC_V_BDL02 | 1 (1) | Non conformance constraint equation for Bairnsdale 2 power station | Outage | Non-Conformance
NC_V_HWPS7 | 1 (1) | Non Conformance Constraint for Hazelwood HWPS 7 Power Station | Outage | Non-Conformance
NC_V_NPS | 1 (0) | Non Conformance Constraint for Newport Power Station | Outage | Non-Conformance
N^^Q_ARDM_B1 | 1 (0) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage | NSW
N_SH_080 | 1 (1) | Discretionary upper limit for Shoalhaven Generation of 80 MW | Outage | NSW
S>>NIL_TBTU_TBMO | 1 (119) | Out= Nil, avoid overloading Tailem Bend to Mobilong 132 kV line on trip of Tailem Bend to Tungkillo 275 kV line | NIL | SA
T^V_NIL_8 | 1 (6) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
V:S_570 | 1 (0) | Out = NIL, VIC to SA on Heywood upper transfer limit of 570 MW based on oscillatory stability. | NIL | Vic
NC_Q_STAN-1 | 1 (1) | Non Conformance Constraint for Stanwell STAN-1 Power Station | Outage | Non-Conformance
N^^V_EPMB_1 | 1 (24) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
N_HM_NSW_ZERO | 1 (0) | Hume NSW unit upper limit of 0 MW | Outage | NSW
S>>MOTB_SETX2_SETX1 | 1 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L South East 132/275kV TX1 on trip of South East 132/275kV TX2(for TX component SECS assumed O/S), Feedback | Outage | SA
T>T_LIPM_110_2A | 1 (0) | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
TV_300 | 1 (0) | Tas to Vic on Basslink upper limit of 300 MW | Outage | Tas
T_TAMARCCGT_GCS | 1 (0) | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) | NIL | Tas
T_T_FASH_5_N-2 | 1 (3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit Mackintosh + Tribute + Reece 1 <= 110% of West Coast load | Outage | Tas
V::N_MLTR_xxx | 1 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V:S_570_HY_TEST | 1 (0) | VIC to SA on Heywood upper transfer limit of 570 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
V>V_HW_TX12_35_OPT2 | 1 (1) | Out = Hazelwood A1 or A2 500/220 kV txfmr, HWTS A3 txfmr switched to HWPS No. 2 bus, avoid O/L Yallourn to Rowville No. 7 or 8 220 kV line on trip of Hazelwood A4 txfmr, 3/5 parallel mode, JLGB connected to HWPS B3/4 side, feedback | Outage | Vic
S:V_500_HY_TEST_DYN | 1 (0) | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
S>>NIL_NIL_SETX12 | 1 (0) | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
T>T_HAPM_IMP_4L | 1 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V>SML_BUDP_1 | 1 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Bendigo to Kerang 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
VN_1100 | 1 (1) | Discretionary Vic to NSW transfer upper limit of 1100 MW | Outage | Vic
V_HYMO2_1 | 1 (0) | Out = Heywood to Mortlake No.2 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
CA_MQS_473FDF2B_01 | 1 (0) | Constraint Automation, O/L TABSES_2 @S_EAST for CTG LSIC on trip of T_BEND-S_EAST 275KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage | Constraint Automation
N>>N-NIL__2_OPENED & CLOSED | 1 (0) | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
NC_Q_CPSA | 1 (0) | Non Conformance Constraint for Condamine Power Station | Outage | Non-Conformance
NC_Q_STAN-3 | 1 (0) | Non Conformance Constraint for Stanwell STAN-3 Power Station | Outage | Non-Conformance
V::S_NIL_SETB_SECP_2 | 1 (0) | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V>V_NIL_ROYP56_R2_1 | 1 (11) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 220 kV, feedback | NIL | Vic
V_HYML1_3 | 1 (1) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
V_HYML1_4 | 1 (1) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
#MINTARO_C_E | 1 (0) | SMPS.ENERGY * 1 >= 50 (Wt = 48) | Outage | Quick
#N-Q-MNSP1_RAMP_I_F | 1 (1) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage | Quick
NC_S_TORRA4 | 1 (0) | Non Conformance Constraint for Torrens A4 Power Station | Outage | Non-Conformance
NC_V_HWPS2 | 1 (0) | Non Conformance Constraint for Hazelwood HWPS 2 Power Station | Outage | Non-Conformance
S>DVBG_BWMP_RHBR-T | 1 (0) | Out= Davenport-Bungama 275kV line with Blyth West 275kV CB8001 CLOSED, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
SV_250_DYN | 1 (0) | SA to Victoria on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | SA
T::T_GTSH_2 | 1 (0) | Out = George Town to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Tas
T^T_LI_CL_CS_5_DS | 1 (0) | Out = Liapootah to Chapel St or Liapootah to Cluny Tee to Chapel St 220kV line, avoid voltage instability or violations for loss of remaining parallel Liapootah to Chapel St 220 kV circuit, dispatch only | Outage | Tas
T_LE_ZERO | 1 (0) | Discretionary 0 MW upper limit on Lake Echo generation | Outage | Tas
V:S_BLKRG_570 | 1 (0) | Out = both or one Black Range series capacitors O/S, VIC to SA to on Heywood upper transfer limit of 570 MW based on oscillatory stability. | Outage | Vic
V:S_MSUT_560 | 1 (0) | Out = Murray - Upper Tumut (65) 330kV line, VIC to SA on Heywood upper transfer limit of 560 MW based on oscillatory stability. | Outage | Vic
V>>DDSH_DDGN_N-2 | 1 (0) | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
VN_0600 | 1 (0) | Discretionary Vic to NSW transfer upper limit of 600 MW | Outage | Vic
N>N-96H+96R_TE_1 | 1 (0) | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
N>N-ARCH_TE_1 | 1 (0) | Out= Armidale to Coffs Harbour (96C), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (87), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | NSW
NC_Q_GSTONE6 | 1 (0) | Non Conformance Constraint for Gladstone 6 Power Station | Outage | Non-Conformance
NC_Q_KAREEYA1 | 1 (0) | Non Conformance Constraint for Kareeya 1 Power Station | Outage | Non-Conformance
NC_Q_TARONG#4 | 1 (2) | Non Conformance Constraint for Tarong 4 Power Station | Outage | Non-Conformance
NC_Q_YABULU | 1 (0) | Non Conformance Constraint for Yabulu Power Station | Outage | Non-Conformance
NC_S_DRYCGT1 | 1 (0) | Non Conformance Constraint for Dry Creek 1 Power Station | Outage | Non-Conformance
NC_S_SNUG1 | 1 (0) | Non Conformance Constraint for Snuggery 1 Power Station | Outage | Non-Conformance
NC_V_HWPS6 | 1 (0) | Non Conformance Constraint for Hazelwood HWPS 6 Power Station | Outage | Non-Conformance
Q:N_ARSVC_AR_2L-G | 1 (35) | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
S>>BWMP_MKRB_BRTW | 1 (0) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Brinkworth - Templers West 275kV on trip of Mokota - Robertstown 275kV line(this offloads Davenport-Mokota 275kV line and trips Hallet 2 windfarm), Feedback | Outage | SA
S>>DVBL_RBTU_WEWT | 1 (0) | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
T>T_NIL_BL_110_18_1 | 1 (4) | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
V::N_HYMO_xxx | 1 (3) | Out = Heywood to Mortlake (HYTS-MOPS) No.2 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_KHKN_SETB | 1 (0) | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line.. | Outage | SA
V::S_SEVC_MAXG | 1 (8) | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V>>V_NIL_5 | 1 (26) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
VN_0900 | 1 (0) | Discretionary Vic to NSW transfer upper limit of 900 MW | Outage | Vic
V_MB_BUS2 | 1 (0) | Dartmouth PS upper limit set to zero due to outage of Mt Beauty No 2 220 kV Bus | Outage | Vic
#LR_20161004084741 | 1 (0) | ((NSW1 + QLD1 + VIC1).LOWERREG) >= 250 (Wt = 10) | Outage | Quick
NC_Q_BARRON-1 | 1 (1) | Non Conformance Constraint for Barron Gorge 1 Power Station | Outage | Non-Conformance
NC_Q_KPP_1 | 1 (1) | Non Conformance Constraint for Kogan Creek Power Station | Outage | Non-Conformance
NC_Q_STAN-4 | 1 (0) | Non Conformance Constraint for Stanwell STAN-4 Power Station | Outage | Non-Conformance
NC_Q_TARONG#1 | 1 (1) | Non Conformance Constraint for Tarong 1 Power Station | Outage | Non-Conformance
NC_S_AGLHAL | 1 (1) | Non Conformance Constraint for AGL Hallet Power Station | Outage | Non-Conformance
NC_S_DRYCGT3 | 1 (0) | Non Conformance Constraint for Dry Creek 3 Power Station | Outage | Non-Conformance
S:V_PA_SVC_420 | 1 (0) | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
S>>BGBW_TWPA_TPRS | 1 (5) | Out= Bungama - Blyth West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West- Para 275kV line, Feedback | Outage | SA
S>X_RBPA+CB_01 | 1 (0) | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
T_V_NIL_FCSPS | 1 (0) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
V>>N-NIL_HH | 1 (0) | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL | Vic
V>>SML_ARWB_5 | 1 (0) | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L Kerang to Wemen 220 kV line section on loss of Balranald to Darlington Point (X5/1) line | Outage | Vic
VT_300 | 1 (0) | Vic to Tas on Basslink upper limit of 300 MW | Outage | Vic
V_ARARAT_ZERO | 1 (0) | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
CA_SPS_465E4858_01 | 0 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG TVVM on trip of HWPS-HWTS3 220KV LINE & HWTS A3 TR. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
N>N-ARTW85_1B | 0 (0) | Out= Tamworth-Armidale(85), avoid O/L Tamworth to Armidale (86) on trip of QLD maximum generation, Feedback | Outage | NSW
N>Q_LSLS_9U8 | 0 (27) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage | NSW
NC_N_LD01 | 0 (0) | Non Conformance Constraint for Liddell LD01 Power Station | Outage | Non-Conformance
NC_Q_CPP_3 | 0 (1) | Non Conformance Constraint for Callide C CPP_3 | Outage | Non-Conformance
NC_Q_GSTONE2 | 0 (1) | Non Conformance Constraint for Gladstone 2 Power Station | Outage | Non-Conformance
NC_Q_GSTONE5 | 0 (0) | Non Conformance Constraint for Gladstone 5 Power Station | Outage | Non-Conformance
NC_Q_MPP_1 | 0 (1) | Non Conformance Constraint for Millmerran 1 Power Station | Outage | Non-Conformance
NC_S_NPS2 | 0 (2) | Non Conformance Constraint for Northern NPS2 Power Station | Outage | Non-Conformance
NC_S_PPCCGT | 0 (0) | Non Conformance Constraint for Pelican Point Power Station | Outage | Non-Conformance
NC_V_HUMEV | 0 (1) | Non Conformance Constraint for Hume Power Station | Outage | Non-Conformance
NC_V_LYA3 | 0 (0) | Non Conformance Constraint for Loy Yang A3 Power Station | Outage | Non-Conformance
NC_V_LYA4 | 0 (0) | Non Conformance Constraint for Loy Yang A4 Power Station | Outage | Non-Conformance
S>>NIL_RBPA_WEWT | 0 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line, Feedback | NIL | SA
S_V_ROCOF | 0 (0) | Out = South Australia at credible risk of separation from NEM, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | SA
TV_450 | 0 (0) | Tas to Vic on Basslink upper limit of 450 MW | Outage | Tas
VN_0650 | 0 (0) | Discretionary Vic to NSW transfer upper limit of 650 MW | Outage | Vic
VN_0700 | 0 (0) | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
V^^S_MOTB_MAXG | 0 (0) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
V^^S_SETB_SETB | 0 (1) | Out= South East - Tailem Bend 275 kV line; Vic to SA Long Term Voltage Stability limit for loss of the parallel South East - Tailem Bend line. | Outage | SA
CA_MQS_46F62303_02 | 0 (0) | Constraint Automation, O/L 275KV_848 @H10_BCMB for CTG LQIL on trip of 849 H29_STAN-H10_BCMB 275KV LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage | Constraint Automation
CA_SPS_46545836_01 | 0 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
NC_N_BW02 | 0 (0) | Non Conformance Constraint for Bayswater 2 Power Station | Outage | Non-Conformance
NC_N_ER04 | 0 (0) | Non Conformance Constraint for Eraring ER04 Power Station | Outage | Non-Conformance
NC_Q_DDPS1 | 0 (0) | Non Conformance Constraint for Darling Downs Power Station | Outage | Non-Conformance
NC_T_TREVALLN | 0 (0) | Non Conformance Constraint for Trevallyn Power Station | Outage | Non-Conformance
NC_V_HWPS4 | 0 (0) | Non Conformance Constraint for Hazelwood HWPS 4 Power Station | Outage | Non-Conformance
NC_V_JLB01 | 0 (0) | Non Conformance Constraint for Jeeralang B - 01 Power Station | Outage | Non-Conformance
S>>CNDV_BLDV_WEWT | 0 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Belalie-Davenport 275kV line, Feedback | Outage | SA
S>>NIL_TBSE_TBKH1 | 0 (0) | Out= Nil, avoid O/L Tailem Bend - Keith #1 132kV on trip of either Tailem Bend - South East 275kV line, Feedback | NIL | SA
S>DVBL_BWMP_RHBR-T | 0 (0) | Out= Davenport-Belalie 275kV line,, avoid O/L Redhil-Brinkworth T 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | SA
T:T_LIPM_1 | 0 (0) | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
T>T_NIL_BL_IMP_6EE | 0 (0) | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V:SS_ARDM_780 | 0 (0) | Maintain maximum transfer limit of 780 MW on VIC-SA and Murraylink combined to avoid oscillatory instability during the outage of one or more of the major transmission lines connecting NEM regions. | Outage | Vic
V>>BABE_DDGN_N-2 | 0 (0) | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage | Vic
V^^S_TBCB94_35_SETB | 0 (0) | Out= Tailem Bend 275kV CB6594 OR CB6535 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
#V-SA_I_E | 0 (0) | V-SA.ENERGY * -1 <= 250 (Wt = 1150) | Outage | Quick
#V-SA_RAMP_I_F | 0 (3) | V-SA >= MIN(-37, InitialFlow + 50) (Wt=35) | Outage | Quick
N>>N-DTKV_8N | 0 (0) | Out = Dapto-KangarooValley(18), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage | NSW
N>N-CMWI_TWO | 0 (0) | Out= Both Cooma to Williamsdale (97D+978) 132kV line, avoid O/L Murray-Guthega Tx 1 and 2 on nil trip, Feedback. Using TG formulation in PD. | Outage | NSW
N>N-GITN_TE_C1 | 0 (0) | Out = Glen Innes to Tenterfield (96R) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
NC_N_LD03 | 0 (0) | Non Conformance Constraint for Liddell LD03 Power Station | Outage | Non-Conformance
NC_Q_CALL_B_1 | 0 (0) | Non Conformance Constraint for Callide B_1 | Outage | Non-Conformance
NC_Q_CPP_4 | 0 (2) | Non Conformance Constraint for Callide C CPP_4 | Outage | Non-Conformance
NC_Q_GSTONE1 | 0 (0) | Non Conformance Constraint for Gladstone 1 Power Station | Outage | Non-Conformance
NC_Q_TARONG#2 | 0 (0) | Non Conformance Constraint for Tarong 2 Power Station | Outage | Non-Conformance
NC_Q_YABULU2 | 0 (0) | Non Conformance Constraint for Yabulu 2 Power Station | Outage | Non-Conformance
NC_S_MINTARO | 0 (0) | Non Conformance Constraint for Mintaro Gas Turbine | Outage | Non-Conformance
NC_S_OSB-AG | 0 (4) | Non Conformance Constraint for Osborne Power Station | Outage | Non-Conformance
NC_S_POR03 | 0 (0) | Non Conformance Constraint for Port Lincoln unit 3 | Outage | Non-Conformance
NC_S_QPS4 | 0 (0) | Non Conformance Constraint for Quarantine QPS4 Power Station | Outage | Non-Conformance
NC_S_TORRA3 | 0 (1) | Non Conformance Constraint for Torrens A3 Power Station | Outage | Non-Conformance
NC_T_POAT110 | 0 (0) | Non Conformance Constraint for Poatina 110kV Power Station | Outage | Non-Conformance
NC_V_HWPS5 | 0 (1) | Non Conformance Constraint for Hazelwood HWPS 5 Power Station | Outage | Non-Conformance
NC_V_JLA01 | 0 (0) | Non Conformance Constraint for Jeeralang A - 01 Power Station | Outage | Non-Conformance
NC_V_JLA03 | 0 (0) | Non Conformance Constraint for Jeeralang A - 03 Power Station | Outage | Non-Conformance
NC_V_JLB03 | 0 (0) | Non Conformance Constraint for Jeeralang B - 03 Power Station | Outage | Non-Conformance

## Binding FCAS 2016
Constraint Equation ID | 2016 Hours (2015 Hours) | Description | Type
F_T+LREG_0050 | 4,177 (747) | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T+RREG_0050 | 4,175 (802) | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 4,170 (1,202) | Out = Nil, raise 6 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 4,170 (1,200) | Out = Nil, raise 5 min requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 4,170 (1,200) | Out = Nil, raise 60 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL
F_I+NIL_MG_R5 | 4,108 (7,338) | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL
F_MAIN+APD_TL_L5 | 4,087 (1,257) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 4,079 (1,250) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_DYN_LREG | 4,040 (501) | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL
F_T+NIL_TL_L6 | 3,974 (1,068) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_T+NIL_TL_L60 | 3,972 (1,068) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_I+NIL_MG_R6 | 3,955 (7,102) | NEM raise 6 second requirement for a NEM generation event | NIL
F_I+NIL_MG_R60 | 3,886 (6,974) | NEM raise 60 second requirement for a NEM generation event | NIL
F_MAIN+ML_L6_0400 | 3,591 (1,213) | Out = Nil, lower 6 sec requirement for a Mainland load event, ML = 400, Basslink unable transfer FCAS | NIL
F_T+NIL_TL_L5 | 3,245 (1,068) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_I+NIL_APD_TL_L5 | 3,203 (4,626) | NEM lower 5 min Service Requirement for the loss of APD potlines | NIL
F_I+NIL_APD_TL_L60 | 3,141 (3,724) | NEM lower 60 sec Service Requirement for the loss of APD potlines | NIL
F_I+NIL_DYN_LREG | 3,042 (3,935) | NEM lower regulation requirement | NIL
F_I+NIL_DYN_RREG | 3,019 (767) | NEM raise regulation requirement | NIL
F_T+NIL_MG_R6 | 2,952 (2,139) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R60 | 2,927 (1,920) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_I+ML_L6_0400 | 2,900 (1,974) | NEM lower 6 second requirement for a NEM load event | NIL
F_MAIN+NIL_DYN_RREG | 2,473 (362) | Mainland raise regulation requirement, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL
F_I+LREG_0120 | 1,434 (0) | NEM Lower Regulation Requirement greater than 120 MW | NIL
F_I+NIL_RREG | 1,340 (0) | NEM Raise Regulation Requirement | NIL
F_T+NIL_WF_TG_R6 | 1,215 (1,591) | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 1,200 (1,485) | Tasmania raise 60 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R5 | 900 (2,240) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L5 | 872 (3,651) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
F_I+ML_L5_0400 | 668 (26) | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL
F_MAIN++NIL_MG_R60 | 635 (647) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_T+NIL_WF_TG_R5 | 562 (1,825) | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_S+RREG_0035 | 532 (619) | South Australia raise regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage
F_S+LREG_0035 | 532 (621) | South Australia lower regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage
F_T+NIL_MG_RECL_R5 | 470 (0) | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 466 (0) | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN+ML_L6_APD | 428 (15) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_T+NIL_MG_RECL_R60 | 396 (0) | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R6 | 395 (551) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_T++NIL_TL_L60 | 377 (585) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_T+NIL_BB_TG_R6 | 377 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T+NIL_BB_TG_R60 | 363 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_MAIN++ML_L6_0400 | 355 (3,386) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_I+ML_L60_0400 | 355 (9) | NEM lower 60 second requirement for a NEM load event | NIL
F_T++NIL_TL_L6 | 352 (654) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 318 (3,532) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
F_ESTN+MG_R5 | 310 (1) | Raise 5 min Service Requirement for Eastern Generation Event | Outage
F_ESTN+MG_R6 | 307 (1) | Raise 6 sec Service Requirement for Eastern Generation Event | Outage
F_ESTN+MG_R60 | 305 (1) | Raise 60 sec Service Requirement for Eastern Generation Event | Outage
F_ESTN+APD_TL_L60 | 301 (0) | Lower 60 sec requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_ESTN+APD_TL_L5 | 297 (0) | Lower 5 min requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_T++RREG_0050 | 294 (3,062) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_ESTN+ML_L6_0400 | 292 (0) | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_T++NIL_MG_R5 | 273 (70) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 250 (240) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_DYN_LREG | 241 (1,067) | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL
F_MAIN++NIL_BL_L60 | 229 (25) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
F_T+NIL_ML_L60 | 197 (1) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L6 | 195 (1) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T++NIL_MG_R6 | 161 (33) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_T++NIL_MG_R60 | 126 (32) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_T++NIL_ML_L60 | 121 (0) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_QNV++MG_R60 | 111 (0) | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_T+BB_N-2_TG_R60 | 93 (0) | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_T++NIL_ML_L6 | 92 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_MAIN++ML_L5_0400 | 86 (13) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_MAIN+LREG_0120 | 85 (0) | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL
F_T++NIL_WF_TG_R5 | 78 (93) | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS In Nov 2013 educe by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+NIL_RREG | 72 (0) | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL
F_T++NIL_WF_TG_R6 | 61 (43) | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS Out= Nil, Tasmania raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_WF_TG_R60 | 60 (32) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_QNV++APD_TL_L5 | 58 (1) | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_T+BB_N-2_TG_R6_1 | 58 (0) | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment1 | Outage
F_MAIN+ML_L5_0400 | 57 (4) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_S++HYSE_L6_1 | 53 (97) | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_ESTN++HYMO_L60 | 53 (5) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
F_ESTN++HYMO_L5 | 52 (1) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
F_MAIN+ML_L60_0400 | 51 (2) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++LREG_0120 | 51 (0) | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
F_T++LREG_0050 | 48 (132) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_T++NIL_TL_L5 | 47 (302) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_I+ML_L6_APD | 42 (207) | NEM lower 6 second requirement for loss of APD potlines | Outage
F_QNV++HYMO_L5 | 36 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_ML_L5 | 35 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_ESTN++MLTR_L60 | 33 (4) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_ESTN++MLTR_L5 | 30 (5) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_T++NIL_MG_RECL_R5 | 29 (0) | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+ML_L5_APD | 28 (0) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_V_APD01_R5 | 28 (0) | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_V_APD01_R6 | 27 (0) | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_V_APD01_R60 | 27 (0) | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_QNV++MLTR_L5 | 27 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_MG_RECL_R6 | 27 (0) | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+ML_L60_APD | 27 (0) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_S++HYSE_L60 | 27 (38) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
F_V_APD01_L5 | 26 (0) | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage
F_V_APD01_L60 | 23 (0) | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage
F_T++NIL_MG_RECL_R60 | 23 (0) | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_QNV++MG_R6 | 22 (0) | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_V_APD01_L6 | 22 (0) | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage
F_T+FASH_N-2_RREG | 21 (5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_T+FASH1_2C_TG_R5 | 19 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T+FARE_N-2_TG_R60 | 17 (2) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_T+FARE_N-2_TG_R6_1 | 17 (4) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_MAIN++ML_L60_0400 | 17 (2) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_QNV++APD_TL_L60 | 16 (1) | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
F_QNV++HYMO_L60 | 15 (4) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T++CO_752_TL_L60 | 15 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T++CO_752_TL_L6 | 14 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_ESTN++MLMO_L60 | 13 (16) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_Q++ARTW_L60 | 12 (35) | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_Q++ARTW_L6 | 12 (35) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
F_MAIN++NIL_RREG | 12 (0) | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
F_QNV++ML_L6_0400 | 11 (1) | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_MAIN++NIL_DYN_RREG | 11 (6) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL
F_ESTN+LREG_0120 | 10 (0) | Eastern Lower Regulation Requirement greater than 120 MW | Outage
F_QNV++HYMO_L6 | 10 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_QNV++MLTR_L60 | 10 (3) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_ESTN++MLMO_L5 | 10 (4) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
F_QNV++MLTR_L6 | 10 (2) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++ARTW_L5 | 9 (22) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
F_ESTN+RREG_0130 | 9 (0) | Eastern Raise Regulation Requirement greater than 130 MW | Outage
F_QNV++MG_R5 | 8 (0) | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
F_Q++MUTW_L60 | 8 (16) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_T++NIL_TL_L60_DS | 8 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_Q++MUTW_L6 | 8 (16) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_T+CSGO_TG_R6_1 | 8 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage
F_T+FARE_N-2_RREG | 8 (3) | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_T++FASH_N-2_TG_R6 | 7 (3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_QNV++MLMO_L5 | 7 (8) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T+CO_752_TL_L6 | 7 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_T+CO_752_TL_L5 | 7 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_T++NIL_TL_L6_DS | 7 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_T+FASH_N-2_TG_R6_1 | 7 (2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage
F_T+CO_752_TL_L60 | 6 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage
F_I+LREG_0400 | 6 (0) | NEM Lower Regulation Requirement greater than 400 MW | Outage
F_QNV+ML_L6_0400 | 6 (0) | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS | Outage
F_QNV+MG_R6 | 6 (0) | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_QNV+APD_TL_L5 | 6 (0) | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage
F_QNV+MG_R5 | 6 (0) | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_QNV+APD_TL_L60 | 6 (0) | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage
F_QNV+MG_R60 | 6 (0) | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_Q++MUTW_L5 | 6 (11) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_Q++ARTW_R6 | 6 (6) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage
F_Q++ARTW_R60 | 5 (7) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_T++COGT_TL_L6 | 5 (1) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T+FASH_N-2_TG_R60 | 5 (6) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T++FASH_N-2_TG_R5 | 5 (3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_ESTN++HYMO_L6 | 5 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
F_MAIN++LREG_0400 | 5 (0) | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
F_T++COGT_TL_L60 | 5 (0) | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_S++TIB4_R6_1 | 5 (1) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 1 | Outage
F_S++TIB3_R6_1 | 5 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 1 | Outage
F_S+PPT_R6_1 | 5 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage
F_S++TIB2_R6_1 | 5 (1) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA, Segment 1 | Outage
F_S+TL_L60_OD | 5 (1) | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_S+TL_L6_OD | 5 (1) | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_S+TL_L5_OD | 5 (1) | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_Q_MACKAYGT_R5 | 4 (0) | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage
F_S+PPT_R5 | 4 (0) | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_S+PPT_R60 | 4 (0) | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_QNV++MLMO_L60 | 4 (15) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+GO_A752_TG_R5 | 4 (0) | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_ESTN+ML_L5_0400 | 4 (0) | Lower 5 min requirement for a Eastern Load Event, ML = 400 | Outage
F_T+GO_A752_TG_R6 | 4 (0) | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_T+GO_A752_TG_R60 | 4 (0) | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_Q++MUTW_R60 | 4 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
F_T+CSGO_TG_R5 | 4 (6) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_T++BLSPS_EXP_L60_1 | 4 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_T++FASH_N-2_TG_R60 | 4 (2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T++BLSPS_EXP_L6_1 | 4 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_T+GO_C752_TG_R6 | 3 (0) | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_T+GO_C752_TG_R5 | 3 (0) | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_T+GO_C752_TG_R60 | 3 (0) | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_T+FARE_N-2_TG_R5 | 3 (4) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_S++QP5_R6_1 | 3 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Quarantine Power Station unit 5 is the largest generation risk in SA, Segment 1 | Outage
F_I+RREG_0350 | 3 (1) | NEM Raise Regulation Requirement greater than 350 MW | Outage
F_Q++MUTW_R6 | 3 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
F_MAIN+TG_R60_1200 | 3 (0) | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS | Outage
F_MAIN+TG_R6_1200 | 3 (0) | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS | Outage
F_MAIN+TG_R5_1200 | 3 (0) | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS | Outage
F_MAIN++NIL_BL_R60 | 3 (0) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
F_T+FASH_N-2_TG_R5 | 3 (7) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T+NIL_TL_L60_DS | 3 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_ESTN+ML_L60_0400 | 3 (0) | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_ESTN++MLTR_L6 | 3 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_T+NIL_TL_L5_DS | 3 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_QNV++ML_L5_0400 | 3 (0) | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_Q++LDTW_R60 | 3 (1) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_T+NIL_TL_L6_DS | 3 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_ESTN++HYTR_L60 | 2 (9) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_T+CSGO_TG_R60 | 2 (2) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_Q++LDTW_R6 | 2 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
F_T+FASH1_2C_TG_R6 | 2 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_QNV+MLMO_L5 | 2 (1) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+MLMO_L60 | 2 (3) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T+FASH1_2C_RREG | 2 (0) | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage
F_MAIN+RREG_0300 | 2 (2) | Mainland Raise Regulation Requirement greater than 300 MW, Basslink unable to transfer FCAS | Outage
F_S++HYSE_L5 | 2 (16) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage
F_V+NIL_APD01_R60 | 2 (6) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_APD01_L60 | 2 (2) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_MAIN++ML_L6_APD | 1 (56) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | Outage
F_V+NIL_APD01_L5 | 1 (5) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_APD01_L6 | 1 (2) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_T++FARE_N-2_TG_R6 | 1 (1) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_V+NIL_APD01_R5 | 1 (6) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_T+FARE_N-2_TG_R6_2 | 1 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_V+NIL_APD01_R6 | 1 (6) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_Q++LDTW_L6 | 1 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
F_Q++LDTW_L60 | 1 (0) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_QNV++LREG_0120 | 1 (1) | Qld, NSW and Vic Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | Outage
F_S++ML_R6_1 | 1 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA, Segment 1 | Outage
F_S+HL_TG_R6_1 | 1 (0) | Raise 6 sec Service Requirement for the loss of Canowie to Hallett 275 kV line, Segment1 | Outage
F_QNV+MLSY_L60 | 1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_I+RREG_0300 | 1 (4) | NEM Raise Regulation Requirement greater than 300 MW | Outage
F_T+FASH1_2C_TG_R60 | 1 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_S++HYSE_L6_2 | 1 (0) | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
F_T+FASH_N-2_TG_R6_2 | 1 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage
F_Q++ARTW_R5 | 1 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
F_MAIN++RREG_0350 | 1 (0) | Mainland Raise Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
F_QNV+MLSY_L5 | 1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+MLSY_L6 | 1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+HYMO_L5 | 1 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+HYMO_L60 | 1 (2) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_Q++LDTW_L5 | 1 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
F_T++FARE_N-2_TG_R60 | 1 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_I+RREG_0400 | 1 (0) | NEM Raise Regulation Requirement greater than 400 MW | Outage
F_S++TIA1_R6_1 | 1 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island A unit 1 is the largest generation risk in SA, Segment 1 | Outage
F_T+COGT_TL_L5 | 0 (0) | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_QNV+HYMO_L6 | 0 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+MLTR_L60 | 0 (1) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T+COGT_TL_L60 | 0 (0) | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_S++TIB4_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage
F_QNV++ML_L60_0400 | 0 (0) | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
F_S++ML_L6_1 | 0 (0) | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage
F_T+COGT_TL_L6 | 0 (0) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_T+CSGO_TG_R6_3 | 0 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment3 | Outage
F_Q++NIL_R5 | 0 (2) | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_T+CSGO_TG_R6_4 | 0 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment4 | Outage
F_T++CO_752_TL_L5 | 0 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_S++TIB4_R60 | 0 (0) | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage
F_S++TIB3_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage
F_ESTN++HYTR_L5 | 0 (1) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_T+CSGO_TG_R6_2 | 0 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage
F_T+FASH_N-2_TG_R6_3 | 0 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment3 | Outage
F_S+HL_TG_R5 | 0 (0) | Raise 5 min Service Requirement for the loss of Canowie to Hallett 275 kV line | Outage
F_S++TIA4_R6_1 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island A unit 4 is the largest generation risk in SA, Segment 1 | Outage
F_S++OSB_R6_1 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA, Segment 1 | Outage
F_S++ML_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA | Outage
F_S++ML_L60 | 0 (0) | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
F_S+SNS_TG_R6_1 | 0 (0) | Raise 6 sec Service Requirement for the loss of Blyth West - Snowtown 275 kV line, Segment1 | Outage
F_S++TIA2_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island A unit 2 is the largest generation risk in SA | Outage
F_ESTN+LREG_0250 | 0 (0) | Eastern Lower Regulation Requirement greater than 250 MW | Outage
F_S++QP5_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Quarantine Power Station unit 5 is the largest generation risk in SA | Outage
F_T+FASH_N-2_TG_R6_4 | 0 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment4 | Outage
F_S++TIA3_R6_1 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island A unit 3 is the largest generation risk in SA, Segment 1 | Outage
F_S++TIA3_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island A unit 3 is the largest generation risk in SA | Outage
F_S++TIA1_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island A unit 1 is the largest generation risk in SA | Outage
F_QNV+MLTR_L5 | 0 (1) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN++RREG_0300 | 0 (0) | Mainland Raise Regulation Requirement greater than 300 MW, Basslink able transfer FCAS | Outage
F_S+SNS_TG_R5 | 0 (0) | Raise 5 min Service Requirement for the loss of Blyth West - Snowtown 275 kV line | Outage
F_S+NBH_TG_R6_1 | 0 (0) | Raise 6 sec Service Requirement for the loss of North Brown Hill windfarm to Belalie 275 kV line - Segment 1 | Outage
F_S++TIA4_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island A unit 4 is the largest generation risk in SA | Outage
F_QNV+HYTR_L60 | 0 (1) | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_S++TIA2_R6_1 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island A unit 2 is the largest generation risk in SA, Segment 1 | Outage
F_S++TIB1_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA | Outage
F_S++TIB2_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA | Outage
F_S++TIB4_R6_2 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 2 | Outage
F_S++OSB_R5 | 0 (0) | Raise 5 min Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage
F_S+LB_TG_R6_1 | 0 (0) | Raise 6 sec Service Requirement for the loss of Mayura to Snuggery 132 kV line, Segment1 | Outage
F_S++TIB1_R6_1 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 1 is the largest generation risk in SA, Segment 1 | Outage
F_S+LB_TG_R5 | 0 (0) | Raise 5 min Service Requirement for the loss of Mayura to Snuggery 132 kV line | Outage
F_S+NBH_TG_R5 | 0 (0) | Raise 5 min Service Requirement for the loss of North Brown Hill windfarm to Belalie 275 kV line | Outage
F_T++BLSPS_EXP_L5 | 0 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
F_Q++ARDM_L60 | 0 (80) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 60 second requirement | Outage
F_S++TIB3_R60 | 0 (0) | Raise 60 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage
F_I+LREG_0250 | 0 (0) | NEM Lower Regulation Requirement greater than 250 MW | Outage
F_T++COGT_TL_L5 | 0 (0) | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q++ARDM_L6 | 0 (85) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
F_T+FARE_N-2_TG_R6_3 | 0 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 3 | Outage
F_S++TIB3_R6_2 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 2 | Outage
F_T++FARE_N-2_TG_R5 | 0 (1) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_S++TIB2_R6_2 | 0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA, Segment 2 | Outage
F_NVS+ARTW_L60 | 0 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T_FAJB_RREG | 0 (0) | Out=Farrell-John Butters 220KV line. RREG <= 0MW | Outage
F_Q++ARDM_L5 | 0 (61) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage
F_T+NIL_BB_TG_R5 | 0 (0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_QNV++LREG_0250 | 0 (0) | Qld, NSW and Vic Lower Regulation Requirement greater than 250 MW, Basslink able transfer FCAS | Outage
F_T+NIL_ML_L5 | 0 (1) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T++BLSPS_EXP_L6_2 | 0 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage
F_NVS+MUTW_L60 | 0 (0) | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage

## Market Impact 2016
Constraint Equation ID | 2016 Marginal Values (2015 Marginal Values) | 2016 Hours (2015 Hours) | Description | Type | Region
F_S+LREG_0035 | $9,234,806 ($4,643,040) | 531.0 (620.6) | South Australia lower regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage | FCAS
F_S+RREG_0035 | $8,814,511 ($4,630,036) | 531.7 (618.6) | South Australia raise regulation FCAS requirement greater than 35 MW This constraint equation is normally invoked for a risk of islanding or an islanded South Australia | Outage | FCAS
NSA_S_PORxxx | $7,120,984 ($5,306,096) | 42.8 (32.3) | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
T>T_NIL_110_1 | $1,976,230 ($1,370,198) | 153.9 (107.1) | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
Q>NIL_BI_xxx | $1,777,995 ($223,253) | 1,408.8 (258.8) | Out = Nil, avoid overloading on Boyne Island feeder bushing on Calliope River to Boyne Island 132 kV lines, for the contingent loss of a single Calliope River to Boyne Island 132 kV line | NIL | Qld
V^S_NIL_SA_RECLASS | $1,702,651 (0) | 178.3 (0) | Out = NIL, limit generation in SA to prevent flow on Heywood interconnector exceeding 700 MW following reduction in MW output from multiple generating units in SA. | NIL | SA
S-STTX_SNWF | $1,362,930 ($1,238) | 210.0 (1.2) | Out = Snowtown 132/33kV TX or Snowtown CB4593 or Snowtown CB6265, limit for Snowtown WF generation of 0 MW | Outage | SA
SVML_000 | $1,217,528 (0) | 134.8 (0) | South Australia to Victoria on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | SA
V::S_TB_275KV_W_B_1 | $1,180,827 (0) | 232.3 (0) | Out= Tailembend 275kV West Bus; Vic to SA Transient Stability limit for loss of the parallel South East - Tailem Bend line. (South East Capacitor Available) | Outage | SA
S_PLN_ISL2 | $988,797 (0) | 7.4 (0) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
S>NIL_HUWT_STBG | $968,995 ($738) | 78.9 (0.9) | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line overload on loss of Hummocks - Waterloo line | NIL | SA
VSML_220 | $890,029 ($183,598) | 468.1 (123.4) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
S_V_000_HY_DYN | $850,076 (0) | 69.8 (0) | SA to VIC on Heywood upper transfer limit of 0 MW, dynamic headroom, DS formulation only. | Outage | SA
F_S+TL_L6_OD | $749,800 ($110,400) | 4.5 (0.7) | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
VT_ZERO | $710,463 ($13,408) | 628.3 (8.3) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
F_S+PPT_R5 | $691,000 (0) | 4.2 (0) | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS
NSA_Q_GSTONE34_xxx | $645,921 ($16,446,885) | 13.6 (149.7) | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
VSML_ZERO | $640,207 ($99,360) | 301.6 (78.2) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
NSA_Q_BARCALDN | $597,006 ($145,049) | 46.4 (10.8) | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
F_S+TL_L5_OD | $555,400 ($100,800) | 4.5 (0.7) | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
F_I+NIL_DYN_RREG | $548,217 ($7,337) | 3,019.2 (766.4) | NEM raise regulation requirement | NIL | FCAS
V_MTMERCER_ZERO | $547,971 ($58,555) | 43.9 (4.7) | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
V^SML_NSWRB_2 | $518,333 ($207,805) | 153.9 (72.3) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
NSA_V_BDL0xxx | $515,001 ($363,365) | 21.3 (7.3) | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
T_MRWF_QLIM_xx | $510,541 ($730,553) | 39.8 (58.5) | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
N_NYNGANSF_051 | $497,692 (0) | 39.3 (0) | Nyngan Solar Farm upper limit of 51 MW (50% capacity) | Outage | NSW
F_S+PPT_R60 | $489,102 (0) | 4.2 (0) | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | $466,661 ($1,101,202) | 576.5 (177.2) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
SV_000 | $353,393 (0) | 37.3 (0) | SA to Victoria on VicSA upper transfer limit of 0 MW | Outage | SA
F_T+RREG_0050 | $333,580 ($105,025) | 4,174.8 (802.1) | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN+NIL_DYN_RREG | $311,963 ($5,263) | 2,473.0 (362.1) | Mainland raise regulation requirement, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL | FCAS
N_NYNGANSF_010 | $304,496 (0) | 23.0 (0) | Nyngan Solar Farm upper limit of 10 MW | Outage | NSW
V_S_NIL_ROCOF | $303,197 (0) | 393.0 (0) | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | Vic
F_S+TL_L60_OD | $301,998 ($96,000) | 4.5 (0.7) | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
F_T+NIL_MG_R6 | $300,225 ($147,047) | 2,951.2 (2,138.3) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
N>>N-NIL__3_OPENED | $288,656 ($298,577) | 61.3 (26.2) | Out = Nil, avoid overloading Liddell to Muswellbrook (83) 330kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL | NSW
F_S++HYSE_L6_1 | $287,598 ($43,108) | 53.0 (96.9) | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS
F_S++TIB2_R6_1 | $286,820 ($53,814) | 4.4 (0.6) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA, Segment 1 | Outage | FCAS
F_MAIN+NIL_MG_R6 | $285,459 ($38,683) | 4,169.5 (1,202.2) | Out = Nil, raise 6 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL | FCAS
F_S++TIB4_R6_1 | $283,181 ($67,137) | 4.5 (0.7) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 1 | Outage | FCAS
F_S++TIB3_R6_1 | $280,151 (0) | 4.5 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 1 | Outage | FCAS
N_BROKENH1_ZERO | $275,825 (0) | 22.1 (0) | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
F_S++HYSE_L60 | $243,873 ($57,202) | 26.5 (37.9) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage | FCAS
N^Q_NIL_A | $241,714 ($3,659) | 82.1 (3.8) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
S_PLN_ISL32 | $239,609 (0) | 6.3 (0) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
V::S_SETB_TBSE_1 | $239,277 (0) | 149.8 (0) | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available).(NOTE: Assumed both Black Range series capacitors O/S). | Outage | SA
V::N_NIL_xxx | $238,531 ($117,936) | 1,054.3 (1,090.6) | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
F_T+NIL_WF_TG_R6 | $231,751 ($306,329) | 1,214.5 (1,590.3) | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
SA_HYSE1 | $223,340 ($12,924) | 4.5 (0.7) | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage | SA
F_I+NIL_MG_R6 | $219,671 ($80,554) | 3,955.0 (7,101.3) | NEM raise 6 second requirement for a NEM generation event | NIL | FCAS
F_MAIN+NIL_DYN_LREG | $218,244 ($3,995) | 4,039.7 (500.6) | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL | FCAS
F_S+PPT_R6_1 | $211,426 (0) | 2.3 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage | FCAS
F_S++QP5_R6_1 | $202,216 (0) | 4.3 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Quarantine Power Station unit 5 is the largest generation risk in SA, Segment 1 | Outage | FCAS
F_I+NIL_DYN_LREG | $196,206 ($20,144) | 3,041.7 (3,935.7) | NEM lower regulation requirement | NIL | FCAS
F_MAIN+NIL_MG_R60 | $195,479 ($26,866) | 4,169.5 (1,199.9) | Out = Nil, raise 60 sec requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL | FCAS
N_NYNGANSF_ZERO | $184,947 (0) | 14.5 (0) | Nyngan Solar Farm upper limit of 0 MW | Outage | NSW
F_MAIN+NIL_MG_R5 | $169,241 ($25,520) | 4,169.5 (1,199.9) | Out = Nil, raise 5 min requirement for a Mainland generation event, Basslink unable transfer FCAS | NIL | FCAS
SVML_ZERO | $168,998 ($11,788) | 173.8 (70.3) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
F_I+NIL_RREG | $168,056 (0) | 1,339.5 (0) | NEM Raise Regulation Requirement | NIL | FCAS
S_LB3_0 | $167,526 ($517,724) | 60.8 (137.5) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
F_T+NIL_TL_L6 | $164,242 ($162,334) | 3,974.3 (1,067.7) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
F_T+LREG_0050 | $148,620 ($56,865) | 4,176.0 (746.9) | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
V>>SML_NIL_CONT_7B | $146,166 ($31,699) | 100.6 (20.2) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Buangor to Arrarat 66kV line for loss of the Arrarat to Horsham 220kV line | NIL | Vic
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | $144,342 ($97,998) | 1,014.5 (951.3) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. | NIL | Vic
S>NIL_NIL_NWMH2 | $142,013 ($7,525) | 36.9 (2.2) | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
V_HYMO2_1 | $140,000 (0) | 0.8 (0) | Out = Heywood to Mortlake No.2 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
N>>N-NIL_01N | $135,243 (0) | 3.6 (0) | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
Q:N_NIL_AR_2L-G | $130,743 ($30,804) | 61.3 (388.3) | Out = Nil, avoid transient instability for a 2 line to Ground fault at Armidale | NIL | Qld
S>V_NIL_NIL_RBNW | $127,120 ($270,134) | 586.8 (451.3) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink. | NIL | SA
V>>S_KNPW_SETB_SGKH | $126,044 ($3,404) | 48.4 (16.3) | Out= Kincraig - Penola West 132kV line, avoid O/L Snuggery - Keith 132kV on trip of one South East - Tailem Bend 275kV line, Feedback | Outage | SA
V_HYML1_4 | $126,000 ($82,205) | 0.8 (0.9) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
F_S++ML_R6_1 | $125,910 ($8,823) | 1.7 (0.3) | Raise 6 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA, Segment 1 | Outage | FCAS
V>>S_NIL_KHTB2_KHTB1 | $123,409 ($114,379) | 152.9 (78.3) | Out = Nil, avoid overloading Keith to Tailem Bend #1 132 kV line on trip of Keith to Tailem Bend #2 132 kV line | NIL | SA
V>>SML_NIL_7B | $123,287 ($129,791) | 33.0 (34.9) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
VS_250_DYN | $123,270 ($2,796) | 244.8 (18.3) | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Vic
F_I+NIL_MG_R5 | $121,786 ($131,883) | 4,108.0 (7,337.6) | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL | FCAS
F_T+NIL_MG_RECL_R6 | $121,664 (0) | 465.7 (0) | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_I+LREG_0120 | $120,562 (0) | 1,434.0 (0) | NEM Lower Regulation Requirement greater than 120 MW | NIL | FCAS
VSML_ROC_80 | $119,759 (0) | 26.8 (0) | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
S>NIL_SGBN_SGSE-T2 | $116,502 (0) | 16.9 (0) | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
V::S_NIL_MAXG_xxx | $116,390 ($132,038) | 397.5 (242.8) | Out = Nil, avoid transient instability for trip of the largest generation unit in South Australia There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
T>>T_NIL_BL_EXP_6E | $115,906 (0) | 79.6 (0) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | $112,850 ($5) | 97.3 (0.3) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
V>>DDSH_DDGN_N-2 | $110,400 (0) | 0.7 (0) | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
T>T_TUMBNN1_110_1 | $107,962 (0) | 87.8 (0) | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to New Norfolk No.3 110kV line, Feedback | Outage | Tas
V::S_BLKRG_TBSE_2 | $107,046 (0) | 54.2 (0) | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
F_S++TIA1_R6_1 | $105,989 (0) | 3.0 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island A unit 1 is the largest generation risk in SA, Segment 1 | Outage | FCAS
S>>V_NIL_SETX_SETX | $100,856 ($68,441) | 15.0 (75.2) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer This constraint equation binds when there is export from South Australia to Victoria and high generation from the wind farms and gas turbines in the south east of South Australia. | NIL | SA
F_S++HYSE_L5 | $99,626 ($48,433) | 1.6 (15.8) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage | FCAS
V>>N-NIL_HA | $97,517 ($27,769) | 367.9 (35.9) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL | Vic
F_I+NIL_MG_R60 | $89,935 ($59,162) | 3,886.3 (6,974.1) | NEM raise 60 second requirement for a NEM generation event | NIL | FCAS
V::S_NIL_TBSE_2 | $83,817 (0) | 104.6 (0) | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
T_LE_ZERO | $82,800 (0) | 0.5 (0) | Discretionary 0 MW upper limit on Lake Echo generation | Outage | Tas
T>T_GTSH_IMP_4K | $78,219 ($48) | 103.4 (0.1) | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
V:S_600_HY_TEST_DYN | $76,535 (0) | 181.8 (0) | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
N_X_MBTE2_A & N_X_MBTE2_B | $74,246 ($228,731) | 568.8 (1,036.1) | Out = two Directlink cables | Outage | NSW
S:V_500_HY_TEST_DYN | $73,402 (0) | 0.7 (0) | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
T>T_TUNN3_110_1 | $73,108 (0) | 7.1 (0) | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
V>>S_NIL_SETB_SGKH | $72,857 ($92,337) | 130.4 (265.0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line This will bind for high import into SA with high levels of generation from the wind farms and gas turbines in the south east. | NIL | SA
V_MACARTHUR_ZERO | $70,597 ($5,183) | 39.2 (5.3) | Macarthur upper limit of 0 MW | Outage | Vic
Q>NIL_MRTA_B | $70,159 ($300,622) | 19.7 (19.6) | Out = Nil, avoid overloading Middle Ridge to Tangkam (732) 110 kV line on no contingencies | NIL | Qld
Q>NIL_MRTA_A | $69,363 ($131,236) | 6.8 (10.2) | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line. | NIL | Qld
NRM_SA1_VIC1 | $68,770 (0) | 6.5 (0) | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
N>N-BAMB_132_OPEN_A | $68,547 (0) | 68.4 (0) | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | NSW
S>>NIL_SETB_KHTB1 | $67,786 ($181,073) | 92.3 (172.0) | Out = Nil, avoid overloading Keith to Tailem Bend #1 132 kV line on trip of South East to Tailem Bend 275 kV line | NIL | SA
S_LB2WF_CONF | $63,855 ($5,672) | 2.4 (8.0) | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
S^NIL_PL_MAX | $62,683 (0) | 3.8 (0) | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
S>>X_TB-EBUS+CGTB_3 | $62,073 (0) | 27.9 (0) | Out = Tailembend 275kV East Bus (i.e. and associated CBs) + Cherry Gardens-Tailembend 275kV line +Tailembend CBs 6535 & 6536 O/S, avoid O/L TB-MO #1 132kV line on trip of SE-TB #2 275kV line (this offloads SE-TB #1 275kV & TB-TU 275kV lines), | Outage | SA
T>>T_NIL_BL_EXP_7C | $60,844 ($25,870) | 82.6 (11.3) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
N_HM_NSW_ZERO | $59,848 (0) | 0.7 (0) | Hume NSW unit upper limit of 0 MW | Outage | NSW
V::S_NIL_TBSE | $59,149 ($2,623) | 165.5 (21.4) | Out = Nil; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available) | NIL | SA
T>T_NIL_BL_IMP_7CC | $58,707 ($1,284) | 86.5 (10.0) | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V>SMLBAHO4 | $58,218 ($34,142) | 31.3 (77.3) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage | Vic
F_T++NIL_MG_R6 | $55,950 ($10,654) | 160.5 (33.3) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
S>BRTW_BWPA_HUWT | $54,697 ($8,952) | 15.7 (9.0) | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V>V_HWJL3-4_RAD | $53,398 (0) | 4.2 (0) | Outage=Hazelwood to Jeeralang #3 or #4 220kV line OR Jeeralang 220kV #2 bus CB for HWPS-JLTS #3 or #4 220kV line, avoid O/L HWTS A1 Tx for trip of HWPS-JLTS #4 or #3 220kV line, Radial Mode with 1&2 bus split and 3&4 bus split or tied | Outage | Vic
V:S_PA_SVC_575 | $52,396 (0) | 123.8 (0) | Out= one Para SVC, Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 575 MW | Outage | Vic
S>NIL_BWMP_HUWT | $52,165 ($983) | 13.4 (0.8) | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
S>>NIL_HUBG-T_WEWT | $52,136 (0) | 31.7 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Hummocks-Snowtown-Bungama 132kV T line (this trips Snowtown WF), Feedback | NIL | SA
F_T++RREG_0050 | $52,113 ($91,336) | 293.2 (3,061.5) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
V>>N_DDMS_2 | $51,744 ($2,559) | 66.1 (2.9) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Dederang to Murray 330 kV line, feedback | Outage | Vic
N>>N-NIL__S | $50,793 (0) | 1.6 (0) | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL | NSW
S>>V_NIL_SETX_SETX1 | $49,147 (0) | 17.7 (0) | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
N^^V_NIL_1 | $42,416 ($94,201) | 81.9 (211.7) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
F_S+HL_TG_R6_1 | $41,839 ($122) | 0.9 (0.2) | Raise 6 sec Service Requirement for the loss of Canowie to Hallett 275 kV line, Segment1 | Outage | FCAS
NRM_NSW1_VIC1 | $41,396 ($116,040) | 3.6 (9.8) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
S>NIL_WERB_WEWT | $39,865 ($1,962) | 43.8 (2.5) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
S>>V_KNPW_SETX_SETX | $38,549 ($768) | 5.3 (1.2) | Out = Kincraig to Penola West 132 kV line, avoid overloading the remaining South East 275/132kV transformer on trip of one South East 275/132kV transformer | Outage | SA
SA_HYSE2 | $38,459 (0) | 3.3 (0) | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
F_ESTN+MG_R6 | $37,954 ($13) | 307.4 (0.7) | Raise 6 sec Service Requirement for Eastern Generation Event | Outage | FCAS
N_X_MBTE_3A & N_X_MBTE_3B | $36,411 ($341,591) | 863.6 (1,311.2) | Out = all three Directlink cables | Outage | NSW
N::V_GRYS_2 | $35,356 (0) | 3.5 (0) | out = Gullen Range to Yass (3J), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | NSW
N_MOREESF1_ZERO | $34,775 (0) | 2.4 (0) | Moree Solar Farm upper limit of 0 MW | Outage | NSW
F_MAIN++NIL_MG_R60 | $34,673 ($7,247) | 635.2 (646.7) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
F_T+NIL_MG_R60 | $34,429 ($26,544) | 2,926.1 (1,919.3) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN+APD_TL_L5 | $34,400 ($14,208) | 4,086.8 (1,257.1) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL | FCAS
N>LSDU_LSDU | $33,988 ($9,334) | 109.8 (5.0) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
V>>N-BUDP_2N | $33,774 (0) | 57.9 (0) | Out= Buronga-DarlingtonPt(X5), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
I_CTRL_ISSUE_ML | $32,998 ($2,019) | 6.3 (9.3) | DC Link Control Issue Constraint for Murraylink | Outage | Other
S-SNWWF_0 | $31,322 ($18,508) | 27.5 (4.4) | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
V>S_NWRB2_NWRB1 | $31,196 ($625) | 20.6 (13.8) | Out = North West Bend to Robertstown No.2 132 kV line, avoid overloading North West Bend to Robertstown No.1 132 kV line | Outage | SA
S>>X_CGTB+TB35+36_13 | $30,028 ($26) | 10.7 (0.7) | Out= Cherry Gardens- Tailembend 275kV line & Tailembend 275kV CBs 6536 & 6535, avoid O/L Tailembend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line(this offloads Tailem Bend 275/132kC TX4), Feedback | Outage | SA
T_FAJB | $29,964 ($29,138) | 1.3 (1.2) | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Tas
S>>BWMP_DVBR_RHBG-T | $29,680 ($4,018) | 14.0 (0.7) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | SA
F_MAIN++NIL_MG_R6 | $28,842 ($9,304) | 395.4 (550.5) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
S>>KHKN_SETB_SGKH | $28,231 ($1,256) | 64.0 (7.3) | Out = Keith - Kincraig 132 kV line; avoid O/L of Snuggery - Keith 132kV line on trip of either South East - Tailem Bend 275 kV line | Outage | SA
F_T++NIL_WF_TG_R6 | $27,910 ($2,232) | 61.0 (42.8) | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS Out= Nil, Tasmania raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
NRM_VIC1_NSW1 | $27,240 ($17,339) | 2.0 (0.8) | Negative Residue Management constraint equation for VIC to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V_T_NIL_FCSPS | $27,031 ($108,206) | 48.0 (525.5) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
F_Q++ARTW_R6 | $26,098 ($402) | 5.8 (5.8) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
F_S++TIB4_R5 | $25,782 (0) | 0.3 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA | Outage | FCAS
V>>V_NIL_1B | $25,680 (0) | 1.8 (0) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
S>>NIL_RBTU_WEWT | $25,088 ($510) | 7.3 (2.6) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
F_T+FARE_N-2_TG_R6_1 | $24,520 ($1,785) | 17.0 (3.7) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS
V>>V-JNWG_RADIAL_1A | $24,365 (0) | 6.8 (0) | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage | Vic
V>>V_MLSY_4BR | $24,248 (0) | 3.4 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
V::S_BLKRG_MAXG_2 | $24,175 (0) | 34.4 (0) | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
TV_ZERO | $23,083 ($24) | 77.4 (0.2) | Tas to Vic on Basslink upper limit of 0 MW | Outage | Tas
N_WOODLWN1_ZERO | $22,696 ($124,965) | 1.6 (10.0) | Discretionary upper limit for Woodlawn generation of 0 MW | Outage | NSW
CA_SPS_4733E84B_01 | $21,837 (0) | 2.0 (0) | Constraint Automation, O/L 9 @CANBERRA for CTG LNPY on trip of DAPTO-KANGAROO 18 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
NRM_QLD1_NSW1 | $21,736 ($239) | 6.9 (1.2) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V>>N-DDWO_RADIAL_2 | $21,416 ($1,894) | 29.6 (1.8) | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
S>NIL_BWMP_RHBR-T | $21,296 ($5,152) | 8.0 (2.3) | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | SA
F_MAIN++NIL_DYN_LREG | $20,934 ($9,273) | 241.0 (1,065.7) | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL | FCAS
F_T+NIL_MG_R5 | $20,267 ($30,999) | 900.3 (2,239.9) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
F_T++NIL_TL_L6 | $20,156 ($10,367) | 351.7 (654.4) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
V_S_ROCOF | $19,988 ($949) | 31.8 (14.9) | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | Vic
V_ARARAT_5 | $19,937 (0) | 10.3 (0) | Ararat Wind Farm upper limit of 5 MW, limit to manage islanding risk | Outage | Vic
T>T_FASH_1_N-2 | $19,767 ($1,605) | 9.8 (2.0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
V:S_PA_SVC_600 | $19,606 (0) | 38.0 (0) | Out= one Para SVC (Note: both Black Range series caps I/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 600 MW | Outage | Vic
N^^Q_LS_VC_B1 | $19,295 (0) | 4.4 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V>>V_BTRT_2_P | $18,524 (0) | 71.6 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Parallel Mode, Feedback | Outage | Vic
S>NIL_NIL_SETX12 | $18,355 (0) | 1.5 (0) | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
V>>V_BTRT_2B_R | $17,865 (0) | 76.8 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 220kV, Feedback | Outage | Vic
V>>V_BTRT_2A_R | $17,795 (0) | 90.8 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 500kV, Feedback | Outage | Vic
CA_SPS_46545836_02 | $17,665 (0) | 7.9 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
V>>V_ROTS_TX_2A_R | $17,193 ($8) | 99.3 (0.2) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
T>>T_GTSH_EXP_3H | $16,854 (0) | 3.8 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage | Tas
VTBL_ROC | $16,544 ($17,742) | 4.3 (10.7) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
S_WTE_0 | $16,181 ($1,746) | 12.9 (1.4) | Discretionary upper limit for Waterloo generation of 0 MW | Outage | SA
V>SML_BUDP_2 | $14,707 (0) | 25.2 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
S_TBL_0 | $14,697 ($1,465) | 8.3 (0.3) | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
T_FASH_MAXGEN_1 | $14,605 ($1,096) | 9.3 (1.3) | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
V::N_BUDP_xxx | $14,538 ($242) | 22.0 (1.4) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
S>>NIL_TBSE_TBKH1 | $14,414 (0) | 0.3 (0) | Out= Nil, avoid O/L Tailem Bend - Keith #1 132kV on trip of either Tailem Bend - South East 275kV line, Feedback | NIL | SA
F_T++FASH_N-2_TG_R6 | $14,341 ($2,007) | 7.1 (3.2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
S>V_NIL_SETX_SETX1 | $14,312 (0) | 1.4 (0) | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL | SA
V:S_600_HY_TEST | $14,235 (0) | 47.9 (0) | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
CA_MQS_46F62303_02 | $14,144 (0) | 0.3 (0) | Constraint Automation, O/L 275KV_848 @H10_BCMB for CTG LQIL on trip of 849 H29_STAN-H10_BCMB 275KV LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage | Constraint Automation
F_S++TIB3_R6_2 | $14,000 (0) | 0.1 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA, Segment 2 | Outage | FCAS
V>S_NIL_HYSE | $14,000 ($464) | 0.1 (6.2) | Out = NIL, avoid O/L either Heywood to South East 275 kV line on trip of parallel circuit, flow VIC to SA, feedback | NIL | Vic
S>>BRMN_BWPA_HUWT | $13,949 ($997) | 19.6 (1.5) | Out= Brinkworth - Mintaro (or any line section between Brinkworth and Mintaro) 132kV line, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_T+NIL_WF_TG_R60 | $13,835 ($10,375) | 1,200.3 (1,484.3) | Tasmania raise 60 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
V>>V_NIL_4A | $13,800 (0) | 0.1 (0) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. Similar to DBUSS - Line, the DBUSS – Transformer scheme splits the Dederang 330 kV bus on trip of a Dederang transformer. | NIL | Vic
V_LY_BUS1 | $13,800 (0) | 0.1 (0) | Loy Yang Unit A1 upper limit set to zero due to outage of Loy Yang No 1 500 kV Bus | Outage | Vic
F_S++TIB3_R5 | $13,800 (0) | 0.1 (0) | Raise 5 min Service Requirement for SA Generation Event, where Torrens Island B unit 3 is the largest generation risk in SA | Outage | FCAS
T>T_NIL_BL_IMP_5FF | $13,661 (0) | 0.1 (0) | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
V^^S_MLSY_3 | $13,331 (0) | 35.5 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
T_TAMARCCGT_GCS | $12,877 (0) | 0.9 (0) | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) | NIL | Tas
T>T_X_BWLF_TUMBNN1_1 | $12,757 (0) | 9.3 (0) | Out= either Bridgewater to Lindisfarne or Bridgewater to Waddamana 110kV line and Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, avoid O/L Meadowbank Tee 2 to New Norfolk 110kV line on trip of Tungatinah to New Norfolk No.3 110kV line, Feedback | Outage | Tas
S>>BWMP_MKRB_BRTW | $12,706 (0) | 0.6 (0) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Brinkworth - Templers West 275kV on trip of Mokota - Robertstown 275kV line(this offloads Davenport-Mokota 275kV line and trips Hallet 2 windfarm), Feedback | Outage | SA
N^^Q_ARTW_B1 | $12,654 ($28,656) | 6.5 (13.7) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
SVML_ROC_80 | $12,554 (0) | 33.8 (0) | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
N::V_CNUT_2 | $12,470 ($146,865) | 2.8 (3.5) | Out = Upper Tumut -Canberra(01), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | NSW
S>NIL_PL_GENMAX_YDMD | $12,470 (0) | 1.1 (0) | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating. | NIL | SA
F_T+NIL_WF_TG_R5 | $12,087 ($29,597) | 561.6 (1,824.8) | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN+NIL_RREG | $12,028 (0) | 71.7 (0) | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL | FCAS
S>>V_NIL_NIL_HUWT | $11,778 (0) | 1.3 (0) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL | SA
T>T_FASH_1_2_C1 | $11,347 (0) | 19.3 (0) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, West Coast 220/110 kV parallel closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
F_QNV++MG_R60 | $11,258 (0) | 111.4 (0) | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS
V::N_HWSM_xxx | $11,196 ($3,689) | 33.6 (15.5) | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
F_MAIN+LREG_0120 | $11,004 (0) | 84.7 (0) | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL | FCAS
V::N_HYSE_xxx | $10,928 ($34,794) | 39.6 (265.6) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
V>>V_DDSM_1 | $10,895 (0) | 20.8 (0) | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Vic
V>S_CB6033+6225_TX1 | $10,780 ($44,200) | 19.7 (44.0) | Out = North West Bend CB6033 and CB6225, avoid overloading North West Bend transformer #1 132/66kV transformer on trip of Monash to North West Bend #2 132kV line or North West Bend to Morgan Whyalla Pump 1 132 kV line | Outage | SA
F_MAIN++NIL_MG_R5 | $10,680 ($4,329) | 249.6 (240.3) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
F_ESTN+MG_R60 | $10,375 ($6) | 305.0 (0.7) | Raise 60 sec Service Requirement for Eastern Generation Event | Outage | FCAS
T_X_GTSH_1 | $10,152 (0) | 1.3 (0) | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation <= West Coast + North West load + 10MW, limiting SH-PM line flow to 10 MW | Outage | Tas
T^V_NIL_9 | $10,067 ($1,506) | 23.7 (3.3) | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
V>V_NIL_RADIAL_10 | $10,017 ($110) | 1.8 (0.2) | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Vic
S>DVBG_BWMP_RHBR-T | $10,013 (0) | 0.7 (0) | Out= Davenport-Bungama 275kV line with Blyth West 275kV CB8001 CLOSED, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V::N_BAHO_xxx | $9,743 ($1,761) | 8.0 (12.0) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V>V_NIL_RADIAL_9 | $9,561 ($70,503) | 1.5 (14.6) | Out = Nil, avoid O/L of Hazelwood to Jeeralang No. 4 220 kV line for trip of Hazelwood A4 500/220 kV transformer, Yallourn unit 1 in 500kV mode, radial mode, Hazelwood 3,4 busses split, feedback. | NIL | Vic
V>V_NIL_ROYP56_R2_1 | $9,494 ($35,595) | 0.8 (11.4) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 220 kV, feedback | NIL | Vic
S>>PWSE_SETB_SETB_2 | $9,353 (0) | 1.3 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps O/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage | SA
T_T_BA_JB_RC2_250 | $9,282 ($5,739) | 3.3 (2.1) | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
V:S_PA_VC-POD_600 | $9,213 (0) | 39.9 (0) | Out= One Para SVC POD O/S (with associated SVC I/S)(Note: with both Black Range Series caps I/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 600 MW | Outage | Vic
V::S_XKHTB1+2_MAXG | $9,070 ($40,058) | 61.7 (86.8) | Out = both Keith to Tailem Bend 132 kV lines, avoid transient instability for trip of the largest generation unit in South Australia | Outage | SA
F_ESTN+MG_R5 | $8,610 ($14) | 309.5 (0.7) | Raise 5 min Service Requirement for Eastern Generation Event | Outage | FCAS
F_T+NIL_TL_L60 | $8,580 ($2,098) | 3,972.0 (1,067.7) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
F_T+NIL_MG_RECL_R60 | $8,457 (0) | 395.9 (0) | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_APD_TL_L5 | $8,419 ($18,369) | 3,203.3 (4,626.3) | NEM lower 5 min Service Requirement for the loss of APD potlines | NIL | FCAS
V>V_ROYP78_1AR | $8,390 (0) | 1.7 (0) | Out = Rowville to Yallourn No. 7 or No. 8 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 8 or No. 7 220 kV line for trip of the Rowville to Yallourn No. 6 220 kV line, Yallourn W1 on 220 kV, feedback | Outage | Vic
V^^S_TBCPTX_MAXG | $8,387 (0) | 11.0 (0) | Out= Tailem Bend 275/132kV transformer and Tailem Bend 100Mvar Cap Bank; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage | SA
F_T+NIL_TL_L5 | $8,015 ($5,550) | 3,244.3 (1,067.7) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
V^^S_BLKRG_TBSE_2 | $7,989 (0) | 9.8 (0) | Out = both Black Range series capacitors O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
S_SNOWSTH1_ZERO | $7,683 ($4,151) | 7.8 (1.6) | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW | Outage | SA
V>>S_NIL_PWKN_SGKH | $7,622 ($74,955) | 5.9 (48.4) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL | SA
S_SNOWNTH1_ZERO | $7,483 ($3,735) | 7.6 (1.1) | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW | Outage | SA
S>>NIL_TBCG_TBTU_1 | $7,362 (0) | 35.3 (0) | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL | SA
V>>SML_ARWB_6 | $7,334 (0) | 4.4 (0) | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
S>>MOTB_TBTU_TBCG | $7,244 (0) | 33.5 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
N_GULLRWF1_ZERO | $7,162 ($1,859) | 7.4 (4.0) | Gullen Range WF upper limit of 0 MW | Outage | NSW
S>MYTX2_MYTX1 | $7,144 ($6,215) | 8.1 (7.1) | Out = Mayura 132/33 kV transformer #2 with the 33kV bus tie isolator 44248 closed or open, avoid O/L Mayura 132/33 kV transformer #1, Feedback. | Outage | SA
V_T_NIL_BL1 | $7,102 ($160,102) | 12.9 (536.3) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
S>>NIL_NIL_SETX12 | $7,080 (0) | 0.8 (0) | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
F_T+FASH_N-2_RREG | $6,659 ($6,032) | 21.1 (5.1) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | FCAS
T::T_HA_GT_PM_4 | $6,445 ($1,501) | 0.2 (5.7) | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
F_T+NIL_MG_RECL_R5 | $6,350 (0) | 469.7 (0) | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
V>>V_KTS_TX_A2_2A_R | $6,198 ($170) | 54.8 (2.7) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
S>>X_CGTB+TB35+36_08 | $6,143 ($0) | 11.8 (0.1) | Out= Cherry Gardens- Tailembend 275kV line & Tailembend 275kV CBs 6536 & 6535, avoid O/L Snuggery-Keith 132kV line on trip of South East -Tailembend 275kV #2 line(this offloads South East -Tailembend 275kV #1 line), Feedback | Outage | SA
V>>V_MLSY_KTSBP_1AR | $6,108 (0) | 28.5 (0) | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage | Vic
N>N-CHKK_TE_1 | $6,080 ($46) | 16.5 (0.4) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
N^^Q_TW_330_BUS1_B1 | $6,055 (0) | 3.8 (0) | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | NSW
V::N_SMSC_xxx | $6,035 ($283) | 19.1 (2.7) | Out = 1 x South Morang Series Capacitor 330kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
F_T+CSGO_TG_R6_1 | $6,024 ($1,981) | 7.8 (0.2) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
F_MAIN++APD_TL_L5 | $5,884 ($35,074) | 871.8 (3,651.0) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL | FCAS
NQTE_ROC | $5,677 ($8,442) | 85.0 (14.3) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
S>X_RBPA+CB_01 | $5,492 (0) | 0.5 (0) | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
N_GUNNING1_ZERO | $5,422 ($4,743) | 5.1 (5.5) | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
S>V_NWRB2_RBNW1 | $5,337 ($21,293) | 34.9 (93.9) | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage | SA
F_MAIN+APD_TL_L60 | $5,320 ($3,077) | 4,078.8 (1,250.2) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink unable to transfer FCAS | NIL | FCAS
T>T_NIL_BL_IMP_6E | $5,075 (0) | 6.3 (0) | Out = Nil, avoid overloading Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) on trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action | NIL | Tas
T::T_NIL_2 | $4,889 ($2,869) | 13.4 (29.3) | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL | Tas
V:T_SHGT_BL_1 | $4,691 (0) | 10.8 (0) | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
S>>V_KHTB1_TBSE_TBKH | $4,671 (0) | 0.3 (0) | Out = Keith - Tailem bend #1 132 kV line; avoid Tailem Bend - Keith #2 line OL on trip of either one of Tailem Bend - South East 275 kV lines. | Outage | SA
F_MAIN++LREG_0120 | $4,670 (0) | 50.8 (0) | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL | FCAS
T>T_NIL_LIPM_N-2_2B | $4,569 ($3,638) | 1.6 (2.5) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
F_T+NIL_BB_TG_R6 | $4,539 ($2) | 377.2 (0.4) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
CA_SPS_465E4858_01 | $4,491 (0) | 0.4 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG TVVM on trip of HWPS-HWTS3 220KV LINE & HWTS A3 TR. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
V:SS_PA_SVC_795 | $4,385 (0) | 10.9 (0) | Out= one Para SVC, Oscillatory stability limit for Vic to SA on Heywood+ Murrylink upper transfer limit of 795 MW | Outage | Vic
V::N_X_HWSM_ROTX_xxx | $4,312 (0) | 4.0 (0) | Out = Hazelwood to South Morang 500kV line and Rowville (A) TX, prevent transient instability for trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_PWSE_SETB_2 | $4,257 (0) | 0.1 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series cap O/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
S_BLNBH_0 | $4,236 ($1,769) | 2.0 (1.1) | Outage of Belalie-North Brown Hill 275kV line | Outage | SA
F_T+FARE_N-2_RREG | $4,196 ($84) | 7.5 (3.3) | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | FCAS
F_T++NIL_MG_RECL_R6 | $4,150 (0) | 27.1 (0) | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_Q++ARTW_L60 | $4,058 ($2,122) | 11.8 (34.6) | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS
V::N_SMF2_xxx | $4,028 (0) | 10.4 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
N^^V_MSDD2 | $3,992 (0) | 9.1 (0) | Out = Dederang to Murray 330 kV line, avoid voltage collapse for trip of the remaining Dederang to Murray 330 kV line | Outage | NSW
N>>N-NIL__3_CLOSED | $3,979 (0) | 14.1 (0) | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
T>>T_HAPM_EXP_3H | $3,965 (0) | 2.8 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
V^S_HYCP | $3,917 ($1,939) | 35.8 (32.3) | Out = NIL, maintain adequate post contingent voltages for loss of the Heywood to Mortlake 500 kV line. | NIL | Vic
V::N_HYTR_xxx | $3,863 ($236) | 11.8 (2.2) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
T::T_NIL_4 | $3,815 ($2,989) | 9.3 (25.6) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
Q>NIL_BI_CAGS_CLOSED | $3,785 (0) | 14.8 (0) | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104/7105 (T022 Callide A to T152 Gladstone South) 132 kV lines closed with 132 kV split between T022 Callide A and H015 Lilyvale. | NIL | Qld
V^^S_TB_275KV_E_SETB | $3,779 (0) | 24.1 (0) | Out= Tailembend 275kV East Bus(i.e. CBs 6594, 6535 and 6597 OPEN with Tailembend 275/132kV TX4 & C64 O/S); Vic to SA Long Term Voltage Stability limit for loss of one South East-Tailembend 275kV line (NOTE: NPS and Playford assumed to be O/S) | Outage | SA
N_MBTE1_B | $3,766 ($9,683) | 10.1 (52.7) | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
F_T+FASH_N-2_TG_R6_1 | $3,723 ($80) | 6.3 (1.5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
V::S_SETB_SETB | $3,611 ($28,306) | 3.6 (58.3) | Out = South East to Tailem Bend 275 kV line, avoid transient instability for loss of the parallel South East to Tailem Bend 275 kV line | Outage | SA
QNTE_ROC | $3,606 ($567) | 82.2 (13.8) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
N>>Q-LDTW_2 | $3,535 ($569) | 0.2 (5.2) | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage | NSW
F_T+NIL_BB_TG_R60 | $3,488 ($1) | 363.3 (0.4) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
V::N_DDWO_xxx | $3,473 (0) | 8.6 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::S_NIL_SETB_SECP | $3,469 ($9) | 10.4 (0.4) | Out = Nil; Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
S>>X_DVCN+CNRB+CB_10 | $3,469 (0) | 7.3 (0) | Out= Davenport-Canowie-Robertstown 275kV and Robertstown 275kV CBs 6616 and 6571, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | SA
V>>V_KTSY_1_R | $3,468 ($185) | 38.8 (1.4) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
N>>N-BYSW_B | $3,424 (0) | 1.7 (0) | Out = Bannaby-Sydney West(39), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage | NSW
V:S_500_HY_TEST_DYN | $3,420 (0) | 21.3 (0) | VIC to SA on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
N^^N_NIL_1 | $3,378 (0) | 1.4 (0) | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
V::N_X_2SVC_xxx | $3,364 (0) | 7.7 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
N>>N-NIL_64 | $3,265 (0) | 1.0 (0) | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | NSW
S-LB2_0 | $3,262 ($6,141) | 3.4 (8.4) | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
V::N_DDSM_xxx | $3,241 ($264) | 13.8 (2.8) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>S_460_DYN | $3,122 ($353) | 18.0 (5.6) | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Vic
V:SS_820_HY_TEST_DYN | $3,100 (0) | 15.9 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
S_V_NIL_ROCOF | $3,096 (0) | 5.7 (0) | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL | SA
F_T+BB_N-2_TG_R6_1 | $3,035 (0) | 58.2 (0) | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
V:S_550 | $2,969 (0) | 3.9 (0) | Maintain maximum transfer limit of 550 MW on Heywood IC from Vic to SA to avoid oscillatory instability | Outage | Vic
V::S_HYSE | $2,926 ($319) | 17.7 (3.9) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of the remaining South East - Heywood 275 kV line. | Outage | SA
S>>NIL_SETB_SETB_1 | $2,920 (0) | 11.0 (0) | Out= Nil, avoid O/L one South East-Tailem Bend 275kV on trip of other South East-Tailem Bend 275kV line, feedback | NIL | SA
T>T_NIL_110_2 | $2,889 ($111,537) | 0.3 (8.9) | Out = NIL, avoid O/L Scottsdale Tee to Norwood 110 kV line (flow to Norwood) on trip of Scottsdale to Norwood 110 kV line or 110/22 kV txfmr at Scottsdale, feedback. Swamped when Musselroe Runback Control Scheme available | NIL | Tas
N>Q-MUTW_2 | $2,865 ($965) | 1.6 (1.3) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage | NSW
V>>N-JNWO_RADIAL_2 | $2,834 (0) | 9.3 (0) | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
N>>N-DTSS_20 | $2,814 (0) | 4.3 (0) | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage | NSW
N^^V_DDSM2 | $2,768 (0) | 3.4 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse for loss of remaining Dederang to South Morang 330 kV line | Outage | NSW
F_MAIN++NIL_DYN_RREG | $2,720 ($276) | 10.9 (5.9) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL | FCAS
S>>BWMP_BGBR_HUWT | $2,710 ($165) | 3.7 (0.1) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | SA
F_T+FASH1_2C_TG_R6 | $2,689 (0) | 2.0 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
S_HALWF_0 | $2,675 ($14,468) | 1.3 (2.2) | Discretionary upper limit for Hallett wind farm generation of 0 MW | Outage | SA
S>>BRDV_RBTU_WEWT | $2,627 (0) | 3.7 (0) | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
T_MRWF_ZERO | $2,475 ($4,164) | 0.2 (0.3) | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Tas
CA_SPS_46954420_01 | $2,471 (0) | 6.4 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
T^V_NIL_BL_6 | $2,459 ($1,477) | 7.8 (6.0) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
I_CTRL_ISSUE_TE | $2,448 ($3,430) | 44.3 (118.5) | DC Link Control Issue Constraint for Terranora | Outage | Other
N>>N-NIL__B_15M | $2,432 (0) | 0.2 (0) | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL | NSW
F_T++NIL_ML_L6 | $2,400 (0) | 92.3 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
T^T_NIL_BL_6_DS | $2,379 (0) | 1.7 (0) | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah-Waddamana-Palmerston 220 kV line, dispatch equation only | NIL | Tas
T_T_FASH_5_N-2 | $2,372 ($2,422) | 0.9 (3.2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit Mackintosh + Tribute + Reece 1 <= 110% of West Coast load | Outage | Tas
F_T++LREG_0050 | $2,344 ($2,553) | 47.9 (131.8) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
V>>V_NIL_8 | $2,309 ($7,710) | 1.4 (2.0) | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
F_S++TIB2_R6_2 | $2,290 (0) | 0.1 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 2 is the largest generation risk in SA, Segment 2 | Outage | FCAS
F_T++NIL_MG_R5 | $2,283 ($599) | 273.1 (69.7) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
F_Q++ARTW_L6 | $2,268 ($1,676) | 11.8 (34.7) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
V>SMLMHNW2 | $2,244 (0) | 6.5 (0) | Out = Monash-North West Bend # 2 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 1 132kV line | Outage | SA
F_QNV+MG_R60 | $2,182 (0) | 6.3 (0) | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
TV_500 | $2,151 ($18) | 3.8 (0.3) | Tas to Vic on Basslink upper limit of 500 MW | Outage | Tas
V::N_MLSY_xxx | $2,146 (0) | 7.2 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V::N_BYPASS_HW_SY_xxx | $2,120 (0) | 5.8 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
F_QNV++MG_R6 | $2,097 (0) | 22.3 (0) | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS
N::V_MNYS_2 | $2,045 (0) | 1.0 (0) | Out= Marulan-Yass (4 or 5), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | NSW
Q:N_DM_CB_AR_2L-G | $2,011 ($1,772) | 3.1 (7.3) | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
T^^V_GTSH_1 | $2,006 (0) | 2.5 (0) | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
F_I+NIL_APD_TL_L60 | $1,970 ($2,636) | 3,140.8 (3,724.3) | NEM lower 60 sec Service Requirement for the loss of APD potlines | NIL | FCAS
F_T+CO_752_TL_L6 | $1,949 (0) | 7.1 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | Outage | FCAS
V:S_570_HY_TEST_DYN | $1,920 (0) | 6.8 (0) | VIC to SA on Heywood upper transfer limit of 570 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
N>>N-DTKV_E_15M | $1,890 (0) | 5.0 (0) | Out = Dapto-KangarooValley(18), avoid O/L Canberra to Yass(9) on trip of Lower Tumut to Yass (3) line, Feedback | Outage | NSW
S>>X_DVCN+CNRB+CB_16 | $1,885 (0) | 6.3 (0) | Out= Davenport-Canowie-Robertstown 275kV and Robertstown 275kV CBs 6616 and 6571, avoid O/L Waterloo East-MWP4-RB 132kV line on trip of Mokota-Robertstown 275kV line(this offloads Belalie-Mokota 275kV line, RBTX1 and trips Hallet Hill WF), Feedback | Outage | SA
V^^S_XPAVC_SETB_2 | $1,857 (0) | 10.0 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps) O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
N>N-ARTW85_1B | $1,837 (0) | 0.4 (0) | Out= Tamworth-Armidale(85), avoid O/L Tamworth to Armidale (86) on trip of QLD maximum generation, Feedback | Outage | NSW
F_MAIN++LREG_0400 | $1,828 (0) | 5.1 (0) | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage | FCAS
V::S_MOTB_MAXG | $1,819 ($4,255) | 17.1 (8.3) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
S>NWCB6024+25_TX3 | $1,808 ($6,707) | 4.3 (4.3) | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage | SA
TV_470 | $1,804 (0) | 9.3 (0) | Tas to Vic on Basslink upper limit of 470 MW | Outage | Tas
V>>SML_NIL_MLTS_N-2 | $1,798 ($77,190) | 5.5 (23.0) | Out= Nil, avoid O/L Elaine to Ballarat 220kV line section on trip of Moorabool to Ballarat and Moorabool to Terang 220kV lines, Feedback | NIL | Vic
S>CNDV_BWMP_HUWT | $1,795 (0) | 3.3 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_T++BLSPS_EXP_L6_1 | $1,787 (0) | 3.5 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
F_I+RREG_0350 | $1,783 ($265) | 3.2 (0.7) | NEM Raise Regulation Requirement greater than 350 MW | Outage | FCAS
T^V_NIL_11 | $1,769 ($14,190) | 2.0 (1.0) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
F_V_APD01_R6 | $1,736 (0) | 27.2 (0) | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | FCAS
Q:N_AR_CP2_AR_2L-G | $1,691 ($202) | 6.5 (8.6) | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
F_MAIN+RREG_0300 | $1,689 ($492) | 1.6 (1.8) | Mainland Raise Regulation Requirement greater than 300 MW, Basslink unable to transfer FCAS | Outage | FCAS
F_Q++MUTW_L60 | $1,660 ($471) | 8.3 (15.6) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS
T>T_LIPM_110_2A | $1,659 (0) | 0.9 (0) | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
S::V_TBSE_TBSE_1 | $1,656 (0) | 2.4 (0) | Out = one Tailembend-South East 275kV line; SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
F_Q++ARTW_R60 | $1,656 ($85) | 5.4 (7.1) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS
S>MYTX1_44248OPN_LB2 | $1,647 (0) | 1.9 (0) | Out = Mayura No.1 132/33kV transformer O/S (with 33kV bus tie isolator 44248 open), Lake Bonney 2 Windfarm is constraint to a max of 60 MW | Outage | SA
F_Q++MUTW_L6 | $1,627 ($739) | 7.9 (15.6) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS
N^^Q_ARDM_B1 | $1,616 ($1) | 1.0 (0.1) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage | NSW
V^^S_XPACP_MAXG | $1,613 (0) | 4.8 (0) | Out = Para C61 and C62 capacitor banks (both capacitors) O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
F_Q++LDTW_R6 | $1,587 ($6) | 2.2 (0.3) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
V>>V_CBTS_TX_2A_R | $1,586 (0) | 11.5 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
V::N_X_MLSM_EMTT_xxx | $1,579 (0) | 5.4 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_Q++MUTW_L5 | $1,569 ($192) | 6.2 (10.8) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS
S>>CNDV_MKRB_WEMWP4 | $1,563 (0) | 12.3 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4- Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet 2 windfarm), Feedback | Outage | SA
V>>N-NIL_HG | $1,559 (0) | 3.5 (0) | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
F_Q++ARTW_L5 | $1,544 ($588) | 9.3 (22.0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
F_QNV+MG_R6 | $1,534 (0) | 6.3 (0) | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
V::S_BLKRG_TBSE_3 | $1,526 (0) | 6.8 (0) | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
N_SH_080 | $1,521 ($11,616) | 1.0 (1.0) | Discretionary upper limit for Shoalhaven Generation of 80 MW | Outage | NSW
CA_SPS_46BA5824_01 | $1,451 (0) | 6.6 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
V::N_KGRC_xxx | $1,448 (0) | 9.7 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_QNV++APD_TL_L5 | $1,446 ($4) | 58.3 (0.7) | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS
S>MYTX1_MYTX2 | $1,438 ($23,346) | 1.6 (23.5) | Out = Mayura 132/33 kV transformer #1 with the 33kV bus tie isolator 44248 open or closed, avoid O/L Mayura 132/33 kV transformer #2, Feedback | Outage | SA
V>V_HW_TX12_35_OPT2 | $1,431 ($4,628) | 0.9 (1.3) | Out = Hazelwood A1 or A2 500/220 kV txfmr, HWTS A3 txfmr switched to HWPS No. 2 bus, avoid O/L Yallourn to Rowville No. 7 or 8 220 kV line on trip of Hazelwood A4 txfmr, 3/5 parallel mode, JLGB connected to HWPS B3/4 side, feedback | Outage | Vic
T^T_LI_CL_CS_5_DS | $1,400 (0) | 0.7 (0) | Out = Liapootah to Chapel St or Liapootah to Cluny Tee to Chapel St 220kV line, avoid voltage instability or violations for loss of remaining parallel Liapootah to Chapel St 220 kV circuit, dispatch only | Outage | Tas
F_T+GO_A752_TG_R6 | $1,379 (0) | 3.8 (0) | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
V::S_XKHTB1+2_SETB | $1,374 ($40,134) | 12.8 (105.3) | Out = both Keith to Tailem Bend 132 kV lines, avoid transient instability for trip a South East to Tailem Bend 275 kV line | Outage | SA
TVBL_ROC | $1,352 ($30,580) | 3.4 (12.0) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
F_MAIN+ML_L6_0400 | $1,308 ($856) | 3,590.8 (1,212.7) | Out = Nil, lower 6 sec requirement for a Mainland load event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_ESTN+RREG_0130 | $1,303 (0) | 9.0 (0) | Eastern Raise Regulation Requirement greater than 130 MW | Outage | FCAS
F_T++NIL_WF_TG_R60 | $1,299 ($1,343) | 60.3 (32.3) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
VS_350 | $1,281 (0) | 5.4 (0) | Victoria to SA on VicSA upper transfer limit of 350 MW | Outage | Vic
S>>BWMP_HUWT_RHBG-T | $1,258 (0) | 3.8 (0) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Redhill-Brinkworth 132kV T line on trip of Hummocks-Waterloo 132kV line, Feedback | Outage | SA
S::V_TBSE_TBSE | $1,231 (0) | 6.8 (0) | Out = one Tailembend-South East 275kV line; SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
V>>N-JNWG_RADIAL_1 | $1,203 (0) | 2.3 (0) | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
N^^V_DDSM1 | $1,194 (0) | 4.3 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
F_I+LREG_0400 | $1,182 (0) | 6.3 (0) | NEM Lower Regulation Requirement greater than 400 MW | Outage | FCAS
T_V_FCSPS_RAMP | $1,180 (0) | 1.3 (0) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
V^^S_MLSY_2 | $1,179 (0) | 10.7 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
F_MAIN++NIL_RREG | $1,169 (0) | 11.5 (0) | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL | FCAS
V>>N-JNWO_RADIAL_1 | $1,158 (0) | 4.2 (0) | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Vic
F_Q++LDTW_R60 | $1,131 ($16) | 2.6 (0.8) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS
V>>V_NIL_1A | $1,108 (0) | 1.3 (0) | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
V_YP_BUS2 | $1,100 ($6,332) | 0.1 (0.5) | Yallourn W Unit 2 upper limit set to zero due to outage of Yallourn PS No 2 220 kV Bus | Outage | Vic
CA_SPS_46545836_01 | $1,092 (0) | 0.3 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
V>>V_BTRT_SMF2_KT_DR | $1,070 (0) | 2.2 (0) | Out=Brunswick-Richmond 220kV cable and South Morang F2 500/330kV TX, with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypass KTS to WMTS, avoid O/L Rowville-Thomastown 220kV line on trip of Rowville A1 500/220kV TX, Radial, YWPS1 on 500kV, Feedback | Outage | Vic
F_T++NIL_WF_TG_R5 | $1,065 ($765) | 77.5 (92.7) | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS In Nov 2013 educe by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_V_APD01_R60 | $1,059 (0) | 27.5 (0) | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | FCAS
F_I+ML_L5_0400 | $1,049 ($67) | 667.6 (25.5) | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL | FCAS
T>T_NIL_BL_220_6B | $1,028 (0) | 4.0 (0) | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
S>>NIL_TBTU_TBMO_1 | $1,021 (0) | 4.5 (0) | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
S>>CNRB_MKRB_WEMWP4 | $1,010 (0) | 13.8 (0) | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage | SA
F_T++NIL_MG_R60 | $1,010 ($1,751) | 126.0 (31.6) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
V:SS_PA_VC-POD_820 | $989 (0) | 3.3 (0) | Out= one Para SVC(Note: both Black Range series caps I/S), Oscillatory stability limit for Vic to SA on Heywood+ Murrylink upper transfer limit of 820 MW | Outage | Vic
F_MAIN++RREG_0350 | $985 ($501) | 0.6 (0.3) | Mainland Raise Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage | FCAS
T>T_NIL_LIPM_N-2_2A | $980 ($0) | 2.0 (0.2) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to North) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
N::Q_RGSW_KC | $968 (0) | 5.6 (0) | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
V:S_SA_PSS | $965 (0) | 5.3 (0) | Out= Nil; Vic to SA Oscillatory stability limit on Heywood Interconnector based on SA Generator PSS out of service when associated generator is inservice (Note: Both Para SVCs assumed to be I/S). | NIL | Vic
V^^S_XPAVC_MAXG_2 | $954 (0) | 1.9 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps) O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
V>>V-MSUT_1 | $949 ($318) | 6.7 (3.2) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | Outage | Vic
N>N-NIL_LSDU | $915 ($12,128) | 14.8 (4.8) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
CA_MQS_473FDF2B_01 | $912 (0) | 0.8 (0) | Constraint Automation, O/L TABSES_2 @S_EAST for CTG LSIC on trip of T_BEND-S_EAST 275KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage | Constraint Automation
F_T+BB_N-2_TG_R60 | $893 (0) | 92.8 (0) | Out= Nil, loss of all Bell Bay 3 units and Tamar Valley OCGT unit declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
N_NIL_TE_B | $889 (0) | 1.6 (0) | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
V:S_500_HY_TEST | $887 (0) | 4.5 (0) | VIC to SA on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
V::S_PAVC1_MAXG | $873 (0) | 3.9 (0) | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | SA
F_T++FASH_N-2_TG_R5 | $864 ($46) | 5.3 (3.3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
V::S_NIL_TBSE_1 | $857 (0) | 2.8 (0) | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
V::S_KHTB1_SETB | $832 (0) | 1.9 (0) | Out= Keith - Tailem Bend #1 132 kV line; Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
F_Q++MUTW_R6 | $832 ($3) | 3.2 (0.2) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage | FCAS
V>SML_BUDP_5 | $825 (0) | 3.4 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid O/L Ballarat to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line, feedback | Outage | Vic
V>>S_MOTB_TBCG_TBTU | $804 (0) | 1.4 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage | SA
S>DVBL_BWMP_RHBR-T | $803 (0) | 0.3 (0) | Out= Davenport-Belalie 275kV line,, avoid O/L Redhil-Brinkworth T 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | SA
F_T++FARE_N-2_TG_R6 | $802 ($133) | 1.3 (0.8) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
F_I+ML_L6_0400 | $784 ($583) | 2,899.6 (1,973.7) | NEM lower 6 second requirement for a NEM load event | NIL | FCAS
V:SS_820_HY_TEST | $780 (0) | 3.2 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
F_ESTN+LREG_0120 | $748 ($0) | 10.3 (0.1) | Eastern Lower Regulation Requirement greater than 120 MW | Outage | FCAS
V::N_KTSY_xxx | $735 (0) | 6.2 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T>T_NIL_BL_110_18_1 | $730 ($1,345) | 0.6 (4.3) | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
N>>V_DBUSS_1 | $726 (0) | 1.8 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line DBUSS - line is a control scheme that splits Dederang 330 kV bus on trip of a Murray to Dederang line. This was implemented to allows higher NSW to Vic interconnector capability. For a number of outages in southern NSW and northern Victoria either the line or transformer control schemes are also taken out of service. | Outage | NSW
V>>SML_NIL_CONT_7A | $726 (0) | 0.2 (0) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Ballarat North to Buangor 66kV line for loss of the Arrarat to Horsham 220kV line | NIL | Vic
N^^V_SMTXH1_1 | $716 (0) | 3.3 (0) | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
F_QNV++MG_R5 | $715 (0) | 8.3 (0) | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage | FCAS
F_ESTN+APD_TL_L5 | $714 (0) | 296.7 (0) | Lower 5 min requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
V:SS_PA_SVC_820 | $714 (0) | 4.4 (0) | Out= one Para SVC(Note: both Black Range series caps I/S), Oscillatory stability limit for Vic to SA on Heywood+ Murrylink upper transfer limit of 820 MW | Outage | Vic
T>T_PMSH_IMP_4E | $693 ($184) | 3.8 (0.4) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V:S_570_DYN | $683 (0) | 2.9 (0) | Out = NIL, VIC to SA on Heywood upper transfer limit of 570 MW based on oscillatory stability, dynamic headroom, DS formulation only. | NIL | Vic
V>>V_SMTXF2_6 | $677 (0) | 2.1 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage | Vic
T>T_SH_TX | $671 ($159) | 0.3 (0.3) | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Tas
V::N_KTSY_MLSM_ET_xxx | $667 (0) | 2.0 (0) | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V_ARARAT_ZERO | $652 (0) | 0.5 (0) | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
F_T++NIL_TL_L60 | $619 ($1,006) | 376.9 (584.6) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
QNTE_ZERO | $601 (0) | 3.0 (0) | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage | Qld
VN_0800 | $591 (0) | 3.7 (0) | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage | Vic
V>>N_SMHTX_1 | $583 (0) | 4.8 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V:S_X-PA_S+P_525 | $579 (0) | 5.4 (0) | Out= One Para SVC and other Para SVC POD O/S (Note: with both Black Range Series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 525 MW. | Outage | Vic
S>>DVBL_RBTU_WEWT | $554 (0) | 0.6 (0) | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
V>S_460 | $545 ($103,301) | 3.5 (261.0) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | Outage | Vic
F_T++CO_752_TL_L6 | $541 (0) | 14.4 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
V>SMLHORC2 | $541 (0) | 4.5 (0) | Out = Horsham to Redcliffs 220kV line, avoid overloading Bendigo to Kerang 220kV line for trip of Balranald to Darlington Point (X5/1) 220kV line | Outage | Vic
T^V_NIL_BLCAP | $539 (0) | 1.8 (0) | Outage = Nil, Basslink HF7 98 MVAr cap bank unavailable, limit Basslink to 460 MW at George Town under conditions of low George Town 220 kV voltage. | NIL | Tas
S>BRDV_BWPA_RHBR | $538 ($3,208) | 0.3 (1.3) | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N>>N-NIL__2_OPENED | $536 ($11,420) | 0.8 (0.2) | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
F_T+FASH_N-2_TG_R6_2 | $530 (0) | 0.6 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS
F_V_APD01_R5 | $529 (0) | 27.5 (0) | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | FCAS
V::N_EPMB_xxx | $525 ($1,939) | 7.0 (10.8) | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
S>>BRTW_BWPA_WTTP | $524 ($10,458) | 6.3 (18.5) | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>V_NIL_WTTP_WEMW4 | $524 (0) | 1.1 (0) | Out = Nil, avoid overloading the Waterloo East to Morgan Whyalla pump 4 132 kV line on trip of the Waterloo to Templers 132 kV line | NIL | SA
F_T+NIL_TL_L6_DS | $522 (0) | 2.3 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN++APD_TL_L60 | $514 ($9,187) | 317.7 (3,531.9) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL | FCAS
T_V_NIL_BL1 | $511 ($3,219) | 1.8 (6.4) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
V^SML_NIL_3 | $510 (0) | 0.3 (0) | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW | NIL | Vic
S>>MOTB_SETX2_SETX1 | $487 (0) | 0.9 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L South East 132/275kV TX1 on trip of South East 132/275kV TX2(for TX component SECS assumed O/S), Feedback | Outage | SA
V>>V_KTS_TX_A3_2A_R | $464 ($168) | 7.1 (2.1) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
V::S_PAVC1_SETB | $464 (0) | 3.8 (0) | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | SA
F_T+CSGO_TG_R60 | $450 ($1,652) | 2.2 (2.3) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
F_I+RREG_0400 | $445 (0) | 0.5 (0) | NEM Raise Regulation Requirement greater than 400 MW | Outage | FCAS
T^V_NIL_8 | $438 ($453) | 1.0 (5.7) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
V::S_X_KHTB1+SG_SETB | $432 (0) | 2.1 (0) | Out = Keith-Tailem Bend #1 132kV & Keith-Snuggery 132kV; Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage | SA
F_T+NIL_ML_L60 | $426 ($2) | 197.1 (1.1) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
V>>S_KHTB1_SETB_KHTB | $425 ($7,687) | 3.7 (26.6) | Out = Keith - Tailem Bend #1 132 kV line, avoid O/L on Keith - Tailem Bend #2 line for trip of either South East - Tailem Bend lines. | Outage | SA
T_V_NIL_FCSPS | $408 (0) | 0.5 (0) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
Q:N_ARSVC_AR_2L-G | $407 ($2,833) | 0.6 (34.6) | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
V>>N_SMHTX_2 | $403 (0) | 3.9 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
T>T_HAPM_5L | $387 (0) | 3.3 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L line terminal equipment of Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line, feedback | Outage | Tas
F_MAIN+TG_R60_1200 | $385 (0) | 3.2 (0) | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS | Outage | FCAS
V::S_NIL_SETB_SECP_1 | $379 (0) | 1.3 (0) | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
VT_300 | $374 (0) | 0.5 (0) | Vic to Tas on Basslink upper limit of 300 MW | Outage | Vic
T^T_NIL_LICS_N-2_DS | $365 (0) | 0.2 (0) | Outage = Nil, Loss of both Liapootah to Chapel St 220 kV lines declared credible, avoid voltage instability or violations for loss of both Liapootah to Chapel St 220 kV lines, dispatch only | NIL | Tas
F_T++COGT_TL_L6 | $364 ($1) | 5.3 (0.5) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
T^T_NIL_BL_5_DS | $359 (0) | 0.1 (0) | Out = Nil, Palmerston 110 kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line | NIL | Tas
F_S++TIB4_R6_2 | $352 (0) | 0.1 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Torrens Island B unit 4 is the largest generation risk in SA, Segment 2 | Outage | FCAS
T>T_NIL_BL_IMP_6EE | $348 (0) | 0.3 (0) | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V^^S_SETB_SETB | $347 ($25,338) | 0.4 (0.6) | Out= South East - Tailem Bend 275 kV line; Vic to SA Long Term Voltage Stability limit for loss of the parallel South East - Tailem Bend line. | Outage | SA
V>>V_NIL_5 | $345 ($16,496) | 0.6 (26.3) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
S:V_PA_SVC_420 | $337 (0) | 0.5 (0) | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
S>>NIL_RBPA_WEWT | $333 (0) | 0.4 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line, Feedback | NIL | SA
N::Q_NIL_KC | $331 (0) | 3.3 (0) | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | NSW
V_MB_BUS2 | $319 (0) | 0.6 (0) | Dartmouth PS upper limit set to zero due to outage of Mt Beauty No 2 220 kV Bus | Outage | Vic
V>>N-CNUT_HB_15M | $316 (0) | 1.3 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
V::S_TBCP1_SETB_2 | $316 (0) | 1.1 (0) | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
T:T_LIPM_1 | $312 (0) | 0.3 (0) | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
F_Q++MUTW_R60 | $307 ($6) | 3.8 (0.3) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage | FCAS
F_T+FASH1_2C_TG_R5 | $305 (0) | 19.0 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_ESTN+APD_TL_L60 | $305 (0) | 301.3 (0) | Lower 60 sec requirement for a Eastern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
V::N_ROSM_xxx | $298 ($393) | 3.6 (4.9) | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
F_T+COGT_TL_L6 | $291 ($332) | 0.3 (0.1) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS
F_T+NIL_ML_L6 | $281 ($21) | 194.9 (1.1) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
V^^S_SETB_TBSE_1 | $277 (0) | 0.1 (0) | Out= one South East to Tailem Bend 275kV line; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available).(NOTE: Assumed both Black Range series capacitors O/S). | Outage | SA
S>V_CB6033+6225_TX2 | $271 ($3,225) | 4.7 (38.0) | Out= North West Bend_CB6033 and CB6225; avoid O/L of North West Bend transformer 132/66kV #2 on trip of either Robertstown-NWB #2 132kV line or NWB-Monash #2 132kV line . | Outage | SA
VSML_030 | $268 (0) | 0.3 (0) | Vic to SA on ML upper transfer limit of 30 MW | Outage | Vic
F_T++NIL_MG_RECL_R5 | $267 (0) | 28.5 (0) | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
N>Q_LSLS_9U8 | $266 ($17,816) | 0.4 (26.8) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage | NSW
F_Q++LDTW_L5 | $266 ($0) | 0.6 (0.1) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
F_T++NIL_MG_RECL_R60 | $266 (0) | 22.5 (0) | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V>>V_NIL_6A_R | $253 (0) | 1.1 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL | Vic
F_I+RREG_0300 | $250 ($1,402) | 0.9 (4.3) | NEM Raise Regulation Requirement greater than 300 MW | Outage | FCAS
T>T_HAPM_IMP_4L | $247 (0) | 0.8 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
F_QNV+MG_R5 | $238 (0) | 6.3 (0) | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
T::T_GTSH_2 | $237 ($18) | 0.7 (0.1) | Out = George Town to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage | Tas
V>NWB6024_TX1 | $237 ($71) | 1.2 (0.2) | Out= North West Bend 132kV CB6024, avoid O/L North West Bend 132/66kV #1 TX on trip of Monash-NorthWest Bend #1 132kV line, Feedback | Outage | SA
F_MAIN+ML_L6_APD | $231 ($8) | 427.8 (14.9) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
V::N_HORC_xxx | $228 (0) | 2.0 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_T+CSGO_TG_R5 | $225 ($97) | 3.7 (6.2) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
V::N_MLTR_xxx | $225 ($70) | 0.9 (0.3) | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V::S_SEVC_MAXG | $224 ($805) | 0.6 (8.1) | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
F_T++NIL_ML_L60 | $220 ($0) | 121.1 (0.3) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
VN_0600 | $219 (0) | 0.7 (0) | Discretionary Vic to NSW transfer upper limit of 600 MW | Outage | Vic
VN_0950 | $218 (0) | 1.3 (0) | Discretionary Vic to NSW transfer upper limit of 950 MW | Outage | Vic
S>>BRMN_BWPA_BRTW | $207 (0) | 1.1 (0) | Out= Brinkworth - Mintaro (or any line section between Brinkworth and Mintaro) 132kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_MAIN++ML_L5_0400 | $205 ($66) | 86.1 (12.6) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
F_T+FARE_N-2_TG_R6_2 | $195 ($13) | 1.0 (0.2) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS
F_QNV++MLTR_L5 | $195 ($0) | 27.1 (0.3) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
V:S_570_HY_TEST | $195 (0) | 0.9 (0) | VIC to SA on Heywood upper transfer limit of 570 MW, limit for testing of Heywood interconnection upgrade. | Outage | Vic
V::N_HYMO_xxx | $193 ($346) | 0.6 (3.0) | Out = Heywood to Mortlake (HYTS-MOPS) No.2 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S>>NIL_SETB_KHTB2 | $192 ($5,270) | 1.5 (29.4) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
T_GO_ZERO | $192 (0) | 1.8 (0) | Discretionary 0 MW upper limit on total Gordon generation | Outage | Tas
F_MAIN++NIL_BL_L60 | $189 ($53) | 228.4 (25.3) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL | FCAS
F_T+FARE_N-2_TG_R60 | $187 ($9) | 17.4 (1.6) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T+FASH1_2C_RREG | $182 (0) | 1.8 (0) | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage | FCAS
V:SS_790_HY_TEST_DYN | $181 (0) | 0.2 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 790 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
T>>T_GTSH_EXP_3FH | $180 (0) | 0.3 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown and Palmerston to Sheffield 220 kV line for trip of Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overloads. | Outage | Tas
T>T_X_BWLF_TUMBNN1_3 | $174 (0) | 0.2 (0) | Out= either Bridgewater to Lindisfarne or Bridgewater to Waddamana 110kV line and Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, avoid O/L Tungatinah to New Norfolk No.3 on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV line, FB | Outage | Tas
V^^S_PWSE_SETB | $171 (0) | 1.6 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
F_MAIN+ML_L5_APD | $168 ($1) | 27.6 (0.2) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_MAIN+TG_R5_1200 | $162 (0) | 3.2 (0) | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS | Outage | FCAS
V>>V_BTTT1MLSY_KT_AR | $157 (0) | 1.4 (0) | Out = Brunswick to Thomastown #1 220kV and one Moorabool to Sydenham 500kV line, with KTS 220kV bus #1 & #2 tied and both TTS-KTS lines bypass KTS to WMTS, avoid O/L SMTS F2 txfmr on trip of ROTS A1 500/220kV txfmr, Radial Mode, YWPS1 on 500kV, Feedback | Outage | Vic
F_QNV++HYMO_L5 | $155 (0) | 35.8 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_Q++LDTW_L6 | $154 ($4) | 1.1 (0.4) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
V::S_BNMT_MAXG_2 | $154 (0) | 2.0 (0) | Out= Blanche - Mt Gambier 132kV line; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
F_T++NIL_TL_L6_DS | $150 (0) | 6.5 (0) | Out = Comalco 220 kV CB 752 - swamp if CB in service in Dispatch, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
N:Q_MUTW_1 | $150 (0) | 0.1 (0) | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | NSW
V:S_ARDM_560 | $146 (0) | 1.1 (0) | Maintain maximum transfer limit of 560 MW on Heywood IC from VIC to SA to avoid oscillatory instability | Outage | Vic
F_T+FASH_N-2_TG_R60 | $145 ($54) | 5.3 (6.4) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_T++NIL_TL_L5 | $144 ($474) | 47.3 (302.0) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
N>N-CMWI_TWO | $138 (0) | 0.3 (0) | Out= Both Cooma to Williamsdale (97D+978) 132kV line, avoid O/L Murray-Guthega Tx 1 and 2 on nil trip, Feedback. Using TG formulation in PD. | Outage | NSW
F_QNV++APD_TL_L60 | $137 ($1) | 15.7 (0.7) | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage | FCAS
V:SS_790_DYN | $136 (0) | 0.1 (0) | Out = NIL, VIC to SA on Heywood and Murraylink combined upper transfer limit of 790 MW based on oscillatory stability, dynamic headroom, DS formulation only. | NIL | Vic
V:S_570 | $135 (0) | 1.0 (0) | Out = NIL, VIC to SA on Heywood upper transfer limit of 570 MW based on oscillatory stability. | NIL | Vic
F_MAIN+ML_L5_0400 | $134 ($16) | 57.3 (3.6) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
VN_0900 | $134 (0) | 0.6 (0) | Discretionary Vic to NSW transfer upper limit of 900 MW | Outage | Vic
F_T+FASH_N-2_TG_R6_4 | $133 (0) | 0.2 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment4 | Outage | FCAS
VN_1100 | $132 ($41) | 0.8 (0.9) | Discretionary Vic to NSW transfer upper limit of 1100 MW | Outage | Vic
F_MAIN++ML_L6_0400 | $132 ($2,615) | 354.8 (3,385.3) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
V>>SML_ARWB_5 | $129 (0) | 0.5 (0) | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L Kerang to Wemen 220 kV line section on loss of Balranald to Darlington Point (X5/1) line | Outage | Vic
V>SMLKGRC1 | $117 (0) | 0.2 (0) | Out = Kerang to Redcliffs 220kV line, avoid overloading Darlington Pt to Balranald (X5/1) 220kV line for trip of either Ararat to Horsham or Ballarat to Waubra to Ararat 220 kV line | Outage | Vic
F_Q_MACKAYGT_R5 | $116 (0) | 4.4 (0) | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage | FCAS
F_I+ML_L60_0400 | $116 ($4) | 354.8 (9.3) | NEM lower 60 second requirement for a NEM load event | NIL | FCAS
F_ESTN+ML_L6_0400 | $115 (0) | 291.6 (0) | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS
N::Q_BWTX_KC | $111 (0) | 1.1 (0) | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
TV_300 | $110 (0) | 0.9 (0) | Tas to Vic on Basslink upper limit of 300 MW | Outage | Tas
VN_0650 | $109 (0) | 0.4 (0) | Discretionary Vic to NSW transfer upper limit of 650 MW | Outage | Vic
TV_410 | $107 (0) | 0.2 (0) | Tas to Vic on Basslink upper limit of 410 MW | Outage | Tas
F_ESTN++HYMO_L5 | $106 ($6) | 51.9 (1.3) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage | FCAS
V::N_JNWG_xxx | $105 (0) | 2.7 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
F_ESTN++HYMO_L60 | $105 ($5) | 52.8 (4.9) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage | FCAS
S>>CNDV_BLDV_WEWT | $102 (0) | 0.3 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Belalie-Davenport 275kV line, Feedback | Outage | SA
F_QNV+LREG_0120 | $101 (0) | 0.7 (0) | Qld, NSW and Vic Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | Outage | FCAS
F_T+GO_A752_TG_R5 | $97 (0) | 3.8 (0) | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
N^^V_EPMB_1 | $94 ($7,156) | 0.9 (24.3) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
V::S_KHKN_SETB | $89 (0) | 0.6 (0) | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line.. | Outage | SA
S>>NIL_TBTU_TBMO | $88 ($30,484) | 1.0 (119.0) | Out= Nil, avoid overloading Tailem Bend to Mobilong 132 kV line on trip of Tailem Bend to Tungkillo 275 kV line | NIL | SA
V:S_BLKRG_570 | $85 (0) | 0.7 (0) | Out = both or one Black Range series capacitors O/S, VIC to SA to on Heywood upper transfer limit of 570 MW based on oscillatory stability. | Outage | Vic
F_T+GO_C752_TG_R5 | $84 (0) | 3.3 (0) | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
T>T_NIL_BL_6A | $84 (0) | 0.1 (0) | Out = Nil, avoid pre-contingent O/L of Sheffield to Georgetown No. 1 220kV line (flow to Georgetown), feedback | NIL | Tas
V>>SML_NIL_8 | $80 ($336) | 0.3 (0.7) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V::S_NIL_SETB_SECP_2 | $79 (0) | 0.8 (0) | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V>>BABE_DDGN_N-2 | $79 (0) | 0.3 (0) | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage | Vic
T>T_GTSH_5K | $77 (0) | 0.3 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L line terminal equipment of Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
F_MAIN+TG_R6_1200 | $77 (0) | 3.2 (0) | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS | Outage | FCAS
F_Q++LDTW_L60 | $74 ($10) | 1.1 (0.4) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS
V>>N-NIL_HH | $72 (0) | 0.5 (0) | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL | Vic
V::N_MLMO_xxx | $71 ($133) | 1.8 (0.8) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V>>S_KH_X_SETB_SETB | $69 ($4,459) | 0.3 (16.4) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East - Tailembend 275kV on trip of one South East - Tailembend 275kV line, Feedback | Outage | SA
VN_0700 | $64 (0) | 0.4 (0) | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
F_QNV++LREG_0120 | $62 ($2) | 0.4 (0.6) | Qld, NSW and Vic Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | Outage | FCAS
F_ESTN++MLTR_L5 | $61 ($24) | 29.8 (4.6) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS
CA_SPS_4667C455_01 | $60 (0) | 0.2 (0) | Constraint Automation, O/L HWTS TRANSF A2TR_500 for CTG TVVK on trip of HWPS-HWTS1 220KV LINE & HWTS A1 TR. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
F_QNV++MLMO_L5 | $59 ($49) | 7.2 (8.2) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
T>T_NIL_BL_IMP_7C | $57 (0) | 0.2 (0) | Out = Nil, avoid overloading Farrell to Sheffield No.1 220 kV line for trip of the Farrell to Sheffield No.2 220 kV line with no SPS action | NIL | Tas
S>RBTX1_RBTX2_WEMWP4 | $57 ($985) | 2.2 (19.8) | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, Feedbac | Outage | SA
F_ESTN++MLTR_L60 | $56 ($7) | 32.7 (3.8) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_T+GO_C752_TG_R6 | $54 (0) | 3.3 (0) | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
V:SS_720_HY_TEST_DYN | $53 (0) | 0.3 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 720 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Vic
F_T+FASH_N-2_TG_R5 | $53 ($170) | 3.2 (7.3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_MAIN++NIL_BL_R60 | $49 (0) | 3.2 (0) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL | FCAS
N>N_LSDU_9U6_1 | $49 ($49) | 4.3 (0.1) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | NSW
F_T++NIL_ML_L5 | $49 (0) | 34.7 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
TV_450 | $48 (0) | 0.4 (0) | Tas to Vic on Basslink upper limit of 450 MW | Outage | Tas
F_T+FARE_N-2_TG_R5 | $47 ($71) | 3.3 (3.5) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
VN_0850 | $47 (0) | 0.3 (0) | Discretionary Vic to NSW transfer upper limit of 850 MW | Outage | Vic
F_V_APD01_L5 | $46 (0) | 26.2 (0) | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage | FCAS
F_QNV++HYMO_L60 | $46 ($8) | 15.4 (4.3) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
S:VS_X-PA_S+P_380 | $45 (0) | 0.1 (0) | Out= One Para SVC and other Para SVC POD O/S (Note: with both Black Range Series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 380 MW | Outage | SA
N^N-X_96H_LS_SVC | $44 (0) | 3.2 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage | NSW
V^^S_MOTB_MAXG | $44 (0) | 0.4 (0) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
F_V+NIL_APD01_R6 | $42 ($55) | 1.3 (5.8) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
V^^S_TBCB94_35_SETB | $41 (0) | 0.3 (0) | Out= Tailem Bend 275kV CB6594 OR CB6535 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
N>N-ARCH_TE_1 | $41 (0) | 0.6 (0) | Out= Armidale to Coffs Harbour (96C), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (87), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | NSW
Q>N-MUTE_757 | $39 (0) | 2.5 (0) | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
V>>SML_NIL_1 | $38 ($17,063) | 0.2 (2.5) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V>SML_BUDP_1 | $38 (0) | 0.8 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Bendigo to Kerang 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
N>N-96H+LSTX_TE_1 | $38 (0) | 1.0 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore 330/132kV Tx, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage | NSW
F_QNV+APD_TL_L5 | $37 (0) | 6.3 (0) | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable transfer FCAS | Outage | FCAS
V:S_MSUT_560 | $37 (0) | 0.7 (0) | Out = Murray - Upper Tumut (65) 330kV line, VIC to SA on Heywood upper transfer limit of 560 MW based on oscillatory stability. | Outage | Vic
F_T+GO_A752_TG_R60 | $37 (0) | 3.8 (0) | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
V:S_PA_SVC_550 | $36 (0) | 0.3 (0) | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage | Vic
V>>SML_NIL_7C | $36 (0) | 0.1 (0) | Out = Nil, avoid O/L Ararat to Stawell 66kV line for loss of the Ararat to Horsham 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL | Vic
F_T+GO_C752_TG_R60 | $32 (0) | 3.3 (0) | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
V::S_SEVC_SETB | $31 ($66) | 0.1 (0.8) | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | SA
F_T++BLSPS_EXP_L6_2 | $30 (0) | 0.1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage | FCAS
V>>N-MSUT_4 | $30 (0) | 0.1 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
F_T++FASH_N-2_TG_R60 | $30 ($9) | 3.4 (2.0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
VN_0750 | $29 (0) | 0.3 (0) | Discretionary Vic to NSW transfer upper limit of 750 MW | Outage | Vic
F_V+NIL_APD01_R60 | $29 ($41) | 1.2 (5.8) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
F_MAIN+ML_L60_0400 | $28 ($1) | 51.3 (2.4) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_QNV++MLTR_L60 | $26 ($7) | 10.0 (3.3) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_QNV+MLSY_L5 | $25 (0) | 0.6 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
V>>S_SETB_SETB_SGKH | $25 ($18) | 0.1 (0.2) | Out= one South East to Tailem Bend 275kV line, avoid O/L Snuggery to Keith line on trip of the remaining South East to Tailem Bend line. | Outage | SA
F_MAIN+ML_L60_APD | $25 ($0) | 26.5 (0.2) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
N_MBTE1_A | $24 ($49) | 3.2 (0.1) | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
N>>N-CNUT_HA | $24 (0) | 0.1 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Upper Tumut to Lower Tumut (64) on trip of Upper Tumut to Yass (2) line, Feedback | Outage | NSW
F_T++CO_752_TL_L60 | $23 (0) | 14.6 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
N>>N-DTKV_8N | $22 (0) | 0.3 (0) | Out = Dapto-KangarooValley(18), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage | NSW
N^^Q_TW_330_BUS3_B3 | $21 (0) | 0.2 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Millmerran unit 2 generator | Outage | NSW
F_ESTN++MLMO_L5 | $20 ($18) | 9.9 (3.9) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage | FCAS

## Interconnector Binding 2016
Interconnector Direction | Constraint Equation ID | 2016 Hours (2015 Hours) | Description | Type
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 340.2 (60.3) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
N-Q-MNSP1 Export | N_X_MBTE_3A | 211.2 (273.3) | Out = all three Directlink cables, NSW to Queensland limit All three Directlink cables was out for 37.0 days in 2015 compared to 55.1 days in 2014 | Outage
N-Q-MNSP1 Export | N_X_MBTE2_A | 137.0 (39.9) | Out = two Directlink cables, NSW to Queensland limit Two Directlink cables was out for 122.3 days in 2015 compared to 251.4 days in 2014 | Outage
N-Q-MNSP1 Export | NQTE_ROC | 82.8 (13.6) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL
N-Q-MNSP1 Export | N^Q_NIL_A | 72.3 (2.5) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
N-Q-MNSP1 Export | N>LSDU_LSDU | 59.4 (3.7) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 43.1 (117.5) | DC Link Control Issue Constraint for Terranora The DC Link Control Issue Constraint for Terranora was out for 1.8 days in 2015 compared to 4.9 days in 2014 | Outage
N-Q-MNSP1 Export | N>>N-NIL__3_OPENED | 40.2 (10.7) | Out = Nil, avoid overloading Liddell to Muswellbrook (83) 330kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL
N-Q-MNSP1 Export | #N-Q-MNSP1_I_E | 40.0 (5.2) | Quick constraint equation applied to Terranora Interconnector at various levels | Outage
N-Q-MNSP1 Export | N>N-BAMB_132_OPEN_A | 39.7 (0) | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_E_E | 31.8 (0) | N-Q-MNSP1. * 1 = -57 (Wt = 0.0001) | Outage
N-Q-MNSP1 Export | N>>N-NIL__3_CLOSED | 12.9 (0) | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL
N-Q-MNSP1 Export | N>N-CHKK_TE_1 | 12.7 (0.4) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | N>N-NIL_LSDU | 10.6 (2.8) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line | NIL
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 6.5 (10.4) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Export | N^^Q_TW_330_BUS1_B1 | 4.0 (0) | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | N>N_LSDU_9U6_1 | 3.7 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N::Q_RGSW_KC | 3.5 (0) | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Export | N^N-X_96H_LS_SVC | 3.2 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 3.2 (0.1) | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R6 | 3.0 (0.2) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R6 | 2.7 (0.9) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage
N-Q-MNSP1 Export | N::Q_NIL_KC | 2.7 (0) | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
N-Q-MNSP1 Export | N^N_KKLS_1 | 2.3 (13.3) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | N>Q-MUTW_2 | 1.6 (1.3) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R6 | 1.5 (0.3) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R60 | 1.0 (0.1) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-96H+LSTX_TE_1 | 1.0 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore 330/132kV Tx, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage
N-Q-MNSP1 Export | #R014275_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013555_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint N:Q_MUTW_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | N^^Q_ARDM_B1 | 0.8 (0) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N>>N-NIL__2_OPENED | 0.6 (0) | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
N-Q-MNSP1 Export | N>N-96H+96R_TE_1 | 0.6 (0) | Out= Coffs Harbour to Koolkhan (96H) and Glen Innes to Tenterfield (96R) 132kV line, avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S,TG formulation for PD/ST | Outage
N-Q-MNSP1 Export | N>N-ARCH_TE_1 | 0.6 (0) | Out= Armidale to Coffs Harbour (96C), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (87), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | #R014873_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014889_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014895_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_RAMP_I_F | 0.4 (0.2) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage
N-Q-MNSP1 Export | #R013496_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013496_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013706_006_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R014364_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014656_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014998_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013511_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014654_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014998_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R60 | 0.3 (0.5) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | #R013511_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013717_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014490_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | CA_MQS_46F62303_02 | 0.3 (0) | Constraint Automation, O/L 275KV_848 @H10_BCMB for CTG LQIL on trip of 849 H29_STAN-H10_BCMB 275KV LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage
N-Q-MNSP1 Export | N>N-GITN_TE_C1 | 0.3 (0) | Out = Glen Innes to Tenterfield (96R) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | #R013698_006_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R013714_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE2_A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014490_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014514_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014636_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014646_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014649_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R5 | 0.2 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R60 | 0.2 (0.2) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_TW_330_BUS3_B3 | 0.2 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Millmerran unit 2 generator | Outage
N-Q-MNSP1 Export | #R013636_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE2_A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013706_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R013717_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013963_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE2_A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R013963_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N_X_MBTE2_A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014203_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014275_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014364_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014514_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R014979_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | N:Q_MUTW_1 | 0.1 (0) | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | N>N-ARTW85_1B | 0.1 (0) | Out= Tamworth-Armidale(85), avoid O/L Tamworth to Armidale (86) on trip of QLD maximum generation, Feedback | Outage
N-Q-MNSP1 Export | N>Q_LSLS_9U8 | 0.1 (21.1) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 0.1 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 653.5 (1038.6) | Out = all three Directlink cables, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 431.7 (1004.2) | Out = two Directlink cables, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | QNTE_ROC | 84.8 (13.9) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 22.8 (0.1) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies | NIL
N-Q-MNSP1 Import | N_MBTE1_B | 10.0 (52.6) | Out = one Directlink cable, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 6.8 (2.1) | Negative Residue Management constraint equation for QLD to NSW flow | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 6.8 (18.7) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 5.0 (2.5) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 4.8 (7.5) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | N>>N-DTSS_20 | 4.3 (0) | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
N-Q-MNSP1 Import | QNTE_ZERO | 3.0 (0) | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 2.9 (0.3) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_757 | 2.5 (0) | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | N>>N-BYSW_B | 1.7 (0) | Out = Bannaby-Sydney West(39), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage
N-Q-MNSP1 Import | N_NIL_TE_B | 1.7 (0) | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | I_CTRL_ISSUE_TE | 1.2 (1.0) | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 0.9 (0.3) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | N>>N-NIL__S | 0.8 (0) | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL
N-Q-MNSP1 Import | #N-Q-MNSP1_E_E | 0.7 (0) | N-Q-MNSP1. * 1 = -57 (Wt = 0.0001) | Outage
N-Q-MNSP1 Import | N>>N-NIL_64 | 0.6 (0) | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
N-Q-MNSP1 Import | #R014203_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014627_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014636_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014646_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014649_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014654_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014656_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014873_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014889_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014895_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014979_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_I_F | 0.3 (0.3) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage
N-Q-MNSP1 Import | N>>N-DTKV_8N | 0.3 (0) | Out = Dapto-KangarooValley(18), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage
N-Q-MNSP1 Import | #R014203_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014636_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014646_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014649_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014654_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014889_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 0.2 (0.1) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | #R014627_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014656_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R014979_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | N>N-NIL_MBDU | 0.1 (0.3) | Out = Nil, avoid overloading Mullumbimby to Dunoon (9U6 or 9U7) 132 kV line on trip of the other Mullumbimby to Dunoon (9U7 or 9U6) 132 kV line | NIL
N-Q-MNSP1 Import | N>N_LSDU_9U6_2 | 0.1 (0) | Out = one of Lismore to Dunoon (9U6 or 9U7) 132 kV line, avoid overloading on the Mullumbimby 132/66 kV transformer on trip of the remaining Lismore to Dunoon (9U6 or 9U7) 132 kV line The Lismore to Dunoon 132 kV line was out for 7.1 days in 2015 compared to 2.3 days in 2014 | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 0.1 (0) | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 572.0 (176.0) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
NSW1-QLD1 Export | N^Q_NIL_A | 79.3 (3.7) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 60.0 (25.7) | Out = Nil, avoid overloading Liddell to Muswellbrook (83) 330kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL
NSW1-QLD1 Export | N>>N-NIL__3_CLOSED | 14.1 (0) | Out= Nil, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 6.4 (13.4) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Export | N::Q_RGSW_KC | 5.6 (0) | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | F_Q++ARTW_R6 | 5.4 (1.3) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 4.4 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS1_B1 | 3.8 (0) | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | N::Q_NIL_KC | 3.3 (0) | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
NSW1-QLD1 Export | F_Q++MUTW_R6 | 3.0 (0.2) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++LDTW_R6 | 1.6 (0.3) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
NSW1-QLD1 Export | N>Q-MUTW_2 | 1.6 (1.3) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage
NSW1-QLD1 Export | N::Q_BWTX_KC | 1.1 (0) | Out= Bayswater 500/330kV tie Tx, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | F_Q++MUTW_R60 | 1.0 (0.2) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_ARDM_B1 | 1.0 (0.1) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | #R013555_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint N:Q_MUTW_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | N>>N-NIL__2_OPENED | 0.8 (0.2) | Out= Nil, avoid O/L Liddell to Tamworth (84) using 15 mins rating on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | #R013717_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R014277_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint Q>>LCCP_BCCP_CLWU, Effective Date: 17/02/2015, Version: 1 | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_I_F | 0.4 (0.2) | NSW1-QLD1 >= MIN(-293, InitialFlow + 200) (Wt=35) | Outage
NSW1-QLD1 Export | #R013706_006_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R014750_002_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint Q>>RGLC_CLWU_BCCP, Effective Date: 17/10/2016, Version: 1 | Outage
NSW1-QLD1 Export | F_Q++ARTW_R60 | 0.4 (1.3) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++ARTW_R5 | 0.3 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | #R014750_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q>>RGLC_CLWU_BCCP, Effective Date: 17/10/2016, Version: 1 | Outage
NSW1-QLD1 Export | CA_MQS_46F62303_02 | 0.3 (0) | Constraint Automation, O/L 275KV_848 @H10_BCMB for CTG LQIL on trip of 849 H29_STAN-H10_BCMB 275KV LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage
NSW1-QLD1 Export | N>N-ARTW85_1B | 0.3 (0) | Out= Tamworth-Armidale(85), avoid O/L Tamworth to Armidale (86) on trip of QLD maximum generation, Feedback | Outage
NSW1-QLD1 Export | #R014490_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R014490_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R014514_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R013698_006_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Outage
NSW1-QLD1 Export | F_Q++LDTW_R60 | 0.2 (0.3) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS3_B3 | 0.2 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Millmerran unit 2 generator | Outage
NSW1-QLD1 Export | #R013706_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R013717_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R014514_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R015023_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N::Q_BWTX_KC, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | F_NVS+ARTW_L60 | 0.1 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
NSW1-QLD1 Export | N:Q_MUTW_1 | 0.1 (0) | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | N>>Q-LDTW_2 | 0.1 (5.1) | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage
NSW1-QLD1 Export | Q>>RGLC_CLWU_BCCP | 0.1 (0) | Out= Raglan to Larcom Creek (8875), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871), Feedback | Outage
NSW1-QLD1 Import | V::N_NILxxx | 97.2 (25.2) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G | 61.1 (377.3) | Out = Nil, avoid transient instability for a 2 line to Ground fault at Armidale | NIL
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 7.0 (2.1) | Negative Residue Management constraint equation for QLD to NSW flow | NIL
NSW1-QLD1 Import | F_Q++ARTW_L6 | 6.8 (23.8) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | Q:N_AR_CP2_AR_2L-G | 6.5 (8.4) | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++MUTW_L6 | 5.0 (10.3) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L5 | 4.9 (10.8) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | N>>N-DTSS_20 | 4.3 (0) | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
NSW1-QLD1 Import | V::N_HYTR_Q4 | 4.0 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
NSW1-QLD1 Import | Q:N_DM_CB_AR_2L-G | 3.1 (7.3) | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++MUTW_L5 | 2.9 (5.3) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | V::N_MLSY_Q4 | 2.3 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
NSW1-QLD1 Import | V::N_HYSE_Q1 | 1.8 (0.5) | Outage = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
NSW1-QLD1 Import | N>>N-BYSW_B | 1.7 (0) | Out = Bannaby-Sydney West(39), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage
NSW1-QLD1 Import | N>>N-NIL__S | 1.1 (0) | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL
NSW1-QLD1 Import | F_Q++LDTW_L6 | 0.9 (0.3) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | V::N_MLSY_Q1 | 0.9 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 0.8 (5.0) | NSW1-QLD1 >= MIN(-293, InitialFlow + 200) (Wt=35) | Outage
NSW1-QLD1 Import | N>>N-NIL_64 | 0.7 (0) | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
NSW1-QLD1 Import | Q:N_ARSVC_AR_2L-G | 0.6 (34.6) | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | #R014065_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint Q:N_DM_CB_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R014602_004_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | #R015058_007_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HYTR_Q4, Effective Date: 24/11/2016, Version: 1 | Outage
NSW1-QLD1 Import | #R014613_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q:N_AR_CP2_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R014680_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q2, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | #R014731_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R014864_022_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | N>>N-DTKV_8N | 0.3 (0) | Out = Dapto-KangarooValley(18), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage
NSW1-QLD1 Import | #R014477_004_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTR_Q2, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | #R014602_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | #R014613_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint Q:N_AR_CP2_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R014731_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 0.2 (0.1) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | #R013776_014_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BUDP_Q4, Effective Date: 24/03/2016, Version: 1 | Outage
NSW1-QLD1 Import | #R014570_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLMO_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | #R014699_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint Q:N_AR_CP2_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R014743_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R014923_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_Q2, Effective Date: 08/04/2016, Version: 2 | Outage
NSW1-QLD1 Import | #R015060_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLMO_Q4, Effective Date: 24/11/2016, Version: 1 | Outage
NSW1-QLD1 Import | F_Q++ARDM_L6 | 0.1 (53.4) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 814.0 (859.5) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 173.5 (97.8) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 148.8 (174.5) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_TL_L60 | 101.8 (170.6) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_TL_L6 | 82.3 (187.6) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_BTRT_2A_R | 78.3 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 500kV, Feedback | Outage
T-V-MNSP1 Export | TV_ZERO | 75.6 (0.2) | Tas to Vic on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Export | V>>V_BTRT_2_P | 67.0 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Parallel Mode, Feedback | Outage
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 59.3 (51.8) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 49.2 (2.7) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_2A_R | 47.0 (0.2) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | V>>V_KTSY_1_R | 37.6 (1.4) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | F_QNV++MG_R60 | 29.8 (0) | Raise 60 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_MLSY_KTSBP_1AR | 27.3 (0) | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 26.9 (0.1) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | T^V_NIL_9 | 21.1 (2.9) | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 14.8 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | V>>V_CBTS_TX_2A_R | 11.5 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | V>>V_BTRT_2B_R | 10.2 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 220kV, Feedback | Outage
T-V-MNSP1 Export | F_T++NIL_TL_L5 | 7.1 (65.7) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | CA_SPS_46BA5824_01 | 6.6 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
T-V-MNSP1 Export | CA_SPS_46954420_01 | 6.4 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
T-V-MNSP1 Export | F_QNV++MG_R6 | 5.3 (0) | Raise 6 sec Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | TV_470 | 5.3 (0) | Tas to Vic on Basslink upper limit of 470 MW | Outage
T-V-MNSP1 Export | F_T++CO_752_TL_L60 | 5.0 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++LREG_0050 | 5.0 (27.3) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 4.5 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | T^V_NIL_BL_6 | 4.5 (4.0) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL
T-V-MNSP1 Export | V>>V_MLSY_4BR | 3.4 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2A_R | 3.3 (2.0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | TVBL_ROC | 3.1 (12.1) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Export | F_QNV++MG_R5 | 2.8 (0) | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | TV_500 | 2.7 (0.3) | Tas to Vic on Basslink upper limit of 500 MW | Outage
T-V-MNSP1 Export | T^^V_GTSH_1 | 2.5 (0) | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 2.3 (0.4) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 2.3 (0.2) | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | V>>V_BTRT_SMF2_KT_DR | 2.1 (0) | Out=Brunswick-Richmond 220kV cable and South Morang F2 500/330kV TX, with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypass KTS to WMTS, avoid O/L Rowville-Thomastown 220kV line on trip of Rowville A1 500/220kV TX, Radial, YWPS1 on 500kV, Feedback | Outage
T-V-MNSP1 Export | F_T++CO_752_TL_L6 | 2.0 (0) | Out = 220 kV bus tie CB 752 open in Comalco 220 kV switchyard, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L60_1 | 1.7 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_1 | 1.7 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | T_V_NIL_BL1 | 1.7 (3.5) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL
T-V-MNSP1 Export | T^V_NIL_11 | 1.4 (0.8) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL
T-V-MNSP1 Export | T^V_NIL_BLCAP | 1.2 (0) | Outage = Nil, Basslink HF7 98 MVAr cap bank unavailable, limit Basslink to 460 MW at George Town under conditions of low George Town 220 kV voltage. | NIL
T-V-MNSP1 Export | V>>V_BTTT1MLSY_KT_AR | 1.2 (0) | Out = Brunswick to Thomastown #1 220kV and one Moorabool to Sydenham 500kV line, with KTS 220kV bus #1 & #2 tied and both TTS-KTS lines bypass KTS to WMTS, avoid O/L SMTS F2 txfmr on trip of ROTS A1 500/220kV txfmr, Radial Mode, YWPS1 on 500kV, Feedback | Outage
T-V-MNSP1 Export | T_V_FCSPS_RAMP | 1.1 (0) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage
T-V-MNSP1 Export | TV_300 | 0.9 (0) | Tas to Vic on Basslink upper limit of 300 MW | Outage
T-V-MNSP1 Export | #R014363_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
T-V-MNSP1 Export | F_MAIN++NIL_DYN_RREG | 0.8 (0.1) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T^V_NIL_8 | 0.8 (5.5) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | F_MAIN++NIL_RREG | 0.8 (0) | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | #R013624_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R014200_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
T-V-MNSP1 Export | V>>V_NIL_6A_R | 0.6 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL
T-V-MNSP1 Export | #R013618_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | F_MAIN++NIL_BL_R60 | 0.5 (0) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
T-V-MNSP1 Export | #R013512_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R014921_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R015041_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R013515_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/10/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R013593_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R013904_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 0.3 (0) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | #R015012_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R013512_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R013515_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/10/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R013618_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R013997_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R014103_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R014219_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTSY_1_R, Effective Date: 01/07/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R014363_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
T-V-MNSP1 Export | #T-V-MNSP1_RAMP_E_F | 0.2 (0) | T-V-MNSP1 <= MAX(0, InitialFlow - 200) (Wt=35) | Outage
T-V-MNSP1 Export | TV_410 | 0.2 (0) | Tas to Vic on Basslink upper limit of 410 MW | Outage
T-V-MNSP1 Export | #R013624_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
T-V-MNSP1 Export | #R013888_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R014409_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
T-V-MNSP1 Export | #R014763_071_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint T^V_HAPM_220_1, Effective Date: 01/10/2015, Version: 1 | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_2 | 0.1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage
T-V-MNSP1 Export | TV_450 | 0.1 (0) | Tas to Vic on Basslink upper limit of 450 MW | Outage
T-V-MNSP1 Export | V>>V_KTSY_P | 0.1 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, 3/5 parallel mode, feedback | Outage
T-V-MNSP1 Import | VT_ZERO | 628.0 (8.3) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage
T-V-MNSP1 Import | V::N_NILxxx | 618.5 (409.1) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 458.1 (479.1) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 68.4 (19.7) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 66.5 (9.9) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_6E | 65.8 (0) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 63.0 (3.2) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 56.0 (212.3) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 43.4 (148.7) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 43.4 (475.7) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) | NIL
T-V-MNSP1 Import | F_MAIN++NIL_DYN_LREG | 37.6 (1.3) | Mainland lower regulation requirement, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 34.7 (6.8) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_QNV++APD_TL_L5 | 32.7 (0) | Lower 5 min requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HYSE_V2 | 31.3 (0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 30.6 (8.1) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_QNV++HYMO_L5 | 19.8 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HWSM_V2 | 19.5 (0.5) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 18.8 (21.6) | Tasmania raise 5 minute requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_SMSC_V4 | 18.5 (2.7) | Out = 1 x South Morang Series Capacitor 330kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 18.1 (1.3) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 17.7 (158.1) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 13.9 (5.3) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_QNV++MLTR_L5 | 13.4 (0.3) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 12.8 (6.8) | Tasmania raise 6 second requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_DDSM_V2 | 12.6 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V_T_NIL_BL1 | 11.9 (382.3) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL
T-V-MNSP1 Import | T::T_NIL_2 | 11.8 (13.1) | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | NIL
T-V-MNSP1 Import | V::N_SMF2_V4 | 8.4 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | T::T_NIL_4 | 7.8 (12.2) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 6.8 (0) | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_EPMB_V4 | 6.8 (0) | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_BUDP_V4 | 6.7 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HYTR_V4 | 6.5 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V:T_SHGT_BL_1 | 6.5 (0) | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 6.1 (0) | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_X_2SVC_V4 | 6.1 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 5.8 (0) | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_KGRC_S2 | 5.8 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_S1 | 5.3 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | V::N_HYSE_V1 | 5.0 (1.9) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L5 | 4.4 (1.2) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V2 | 4.3 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | VTBL_ROC | 4.3 (10.5) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Import | V::N_DDWO_V2 | 4.2 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_BUDP_V3 | 4.0 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++APD_TL_L60 | 3.8 (0) | Lower 60 sec requirement for a Qld, NSW and Vic Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_GTSH_EXP_3H | 3.7 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage
T-V-MNSP1 Import | F_QNV++HYMO_L60 | 3.6 (0.4) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BUDP_V1 | 3.4 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_VF | 3.4 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 3 | Outage
T-V-MNSP1 Import | V::N_X_HWSM_ROTX_S1 | 3.3 (0) | Out = Hazelwood to South Morang 500kV line and Rowville (A) TX, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | V::N_BAHO_V4 | 3.2 (0) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++LREG_0120 | 3.1 (0) | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 3.1 (0.4) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 2.9 (0.8) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_QNV++MLTR_L60 | 2.7 (2.0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_HAPM_EXP_3H | 2.7 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | F_QNV++HYMO_L6 | 2.6 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_ROSM_V2 | 2.6 (0) | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_MLSY_V1 | 2.5 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_S2 | 2.4 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++LREG_0400 | 2.3 (0) | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HWSM_V3 | 2.3 (0.2) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_X_MLSM_EMTT_S2 | 2.3 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLTR_L6 | 2.0 (0.6) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_KGRC_V2 | 1.9 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_MLSM_ET_V2 | 1.8 (0) | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 1.7 (1.0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_BUDP_V2 | 1.7 (0.5) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HYSE_Q1 | 1.7 (0.4) | Outage = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_DDWO_S2 | 1.6 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HYTR_Q4 | 1.6 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_DDWO_SD | 1.5 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_KTSY_V2 | 1.5 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 1.3 (0.5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_SMF2_V2 | 1.2 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_SD | 1.1 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_X_2SVC_V3 | 1.1 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++ML_L6_0400 | 1.0 (0) | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HORC_V4 | 1.0 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_VE | 0.9 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
T-V-MNSP1 Import | V::N_MLMO_V2 | 0.9 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_MLTR_V4 | 0.9 (0.1) | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_BAHO_V2 | 0.8 (0) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_ESTN_HYSE_VD | 0.8 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | V::N_X_MLSM_EMTT_SD | 0.8 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L60 | 0.8 (0.3) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | #R014883_005_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015058_015_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | V::N_MLMO_V4 | 0.7 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HORC_SD | 0.6 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | T::T_GTSH_2 | 0.5 (0) | Out = George Town to Sheffield 220 kV line, prevent transient instability for fault and trip of a Farrell to Sheffield line, Tamar Valley CCGT out of service, Basslink importing | Outage
T-V-MNSP1 Import | V::N_X_MLSM_EMTT_V2 | 0.5 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | VT_300 | 0.5 (0) | Vic to Tas on Basslink upper limit of 300 MW | Outage
T-V-MNSP1 Import | #R013579_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013590_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013592_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013607_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013613_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013647_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013666_024_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013700_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013776_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/03/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014173_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014184_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014252_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014313_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014602_004_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014672_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014692_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014729_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014729_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014921_005_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014923_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014973_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015039_007_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015060_014_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015060_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | V::N_MLSY_Q1 | 0.4 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | #R013544_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013544_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013557_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013568_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013590_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013592_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013596_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013649_024_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013939_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014266_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014463_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014560_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014665_014_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014680_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014763_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R014789_009_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014858_030_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014864_030_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014878_023_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014878_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014880_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015002_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015031_014_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_S2, Effective Date: 16/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | V::N_DDWO_V4 | 0.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | #R013559_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013559_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013567_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013578_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013596_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013778_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014037_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014061_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014099_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014184_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014221_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014252_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014680_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014728_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014789_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014867_015_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014879_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014883_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014903_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014915_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014915_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014921_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014964_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015028_014_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_S2, Effective Date: 16/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015028_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015031_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015058_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HYTR_Q4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | V::N_HORC_V2 | 0.3 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HYMO_V2 | 0.3 (0) | Out = Heywood to Mortlake (HYTS-MOPS) No.2 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R013557_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013567_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013600_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013612_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013614_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013663_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013667_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R014241_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014241_010_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014477_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014477_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014602_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014763_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R014858_028_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014858_030_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014864_030_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014879_003_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014880_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014923_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014964_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014980_015_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 02/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014999_003_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014999_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 03/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015002_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015002_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 02/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015035_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015058_015_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.2 (0.4) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 0.2 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 0.2 (4.9) | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | T>>T_GTSH_EXP_3FH | 0.2 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown and Palmerston to Sheffield 220 kV line for trip of Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overloads. | Outage
T-V-MNSP1 Import | V::N_HYTR_S4 | 0.2 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Basslink VIC to TAS. Yallourn W Unit 1 on 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
T-V-MNSP1 Import | #R013613_022_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013614_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013617_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
T-V-MNSP1 Import | #R013812_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014167_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BAHO_S4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014207_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014221_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014266_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014313_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014484_011_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014560_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014570_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLMO_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014570_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014665_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014672_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014692_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014728_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014804_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYMO_Q1, Effective Date: 07/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014867_015_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
T-V-MNSP1 Import | #R014870_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014878_022_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014879_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014903_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_S2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014915_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014942_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 28/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R014964_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
T-V-MNSP1 Import | #R015028_016_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 0.1 (3.8) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++LREG_0250 | 0.1 (0) | Qld, NSW and Vic Lower Regulation Requirement greater than 250 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++ML_L5_0400 | 0.1 (0) | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_S2 | 0.1 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_Q2 | 0.1 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_HYSE_S1 | 0.1 (0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_MLSY_V2 | 0.1 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 879.1 (853.7) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-S-MNSP1 Export | V::N_NILxxx | 807.8 (977.1) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-S-MNSP1 Export | VSML_220 | 467.4 (123.2) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL
V-S-MNSP1 Export | VSML_ZERO | 299.9 (79.5) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 280.3 (31.2) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL
V-S-MNSP1 Export | V^SML_NSWRB_2 | 153.9 (72.3) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line | NIL
V-S-MNSP1 Export | V>>SML_NIL_CONT_7B | 92.5 (15.9) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Buangor to Arrarat 66kV line for loss of the Arrarat to Horsham 220kV line | NIL
V-S-MNSP1 Export | N^^V_NIL_1 | 68.8 (185.4) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
V-S-MNSP1 Export | #V-S-MNSP1_E_E | 66.2 (0) | V-S-MNSP1.ENERGY * 1 = 100 (Wt = 35) | Outage
V-S-MNSP1 Export | V>>N_DDMS_2 | 65.8 (2.9) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Dederang to Murray 330 kV line, feedback | Outage
V-S-MNSP1 Export | V>>V_BTRT_2_P | 60.5 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Parallel Mode, Feedback | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 50.1 (2.6) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-S-MNSP1 Export | V::N_HYSE_V2 | 32.0 (0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SMLBAHO4 | 31.3 (72.3) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage
V-S-MNSP1 Export | S>>NIL_HUBG-T_WEWT | 29.6 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Hummocks-Snowtown-Bungama 132kV T line (this trips Snowtown WF), Feedback | NIL
V-S-MNSP1 Export | VSML_ROC_80 | 27.2 (0) | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | NRM_VIC1_SA1 | 26.8 (0) | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | V>SML_BUDP_2 | 25.2 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage
V-S-MNSP1 Export | V>S_NWRB2_NWRB1 | 20.6 (13.8) | Out = North West Bend to Robertstown No.2 132 kV line, avoid overloading North West Bend to Robertstown No.1 132 kV line | Outage
V-S-MNSP1 Export | V>S_CB6033+6225_TX1 | 19.7 (44.0) | Out = North West Bend CB6033 and CB6225, avoid overloading North West Bend transformer #1 132/66kV transformer on trip of Monash to North West Bend #2 132kV line or North West Bend to Morgan Whyalla Pump 1 132 kV line | Outage
V-S-MNSP1 Export | V::N_HWSM_V2 | 18.1 (0.7) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_DDSM_1 | 17.9 (0) | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
V-S-MNSP1 Export | V>>SML_NIL_7B | 13.3 (32.5) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
V-S-MNSP1 Export | V::N_DDSM_V2 | 10.6 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_V4 | 7.3 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_EPMB_V4 | 6.8 (10.3) | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SMSC_V4 | 6.5 (0.5) | Out = 1 x South Morang Series Capacitor 330kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SMLMHNW2 | 6.5 (0) | Out = Monash-North West Bend # 2 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 1 132kV line | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 6.4 (2.5) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 6.3 (12.0) | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_KGRC_S2 | 6.3 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_BAHO_V4 | 6.2 (9.9) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HWSM_S1 | 6.1 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | V:SS_820_HY_TEST_DYN | 5.8 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-S-MNSP1 Export | V::N_HYSE_V1 | 5.2 (2.7) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 5.1 (8.0) | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | V::N_HWSM_V3 | 5.0 (7.4) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>V-MSUT_1 | 5.0 (0.3) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | Outage
V-S-MNSP1 Export | V>SMLHORC2 | 4.3 (0) | Out = Horsham to Redcliffs 220kV line, avoid overloading Bendigo to Kerang 220kV line for trip of Balranald to Darlington Point (X5/1) 220kV line | Outage
V-S-MNSP1 Export | V::N_HYTR_V4 | 4.2 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>SML_NIL_MLTS_N-2 | 4.2 (21.3) | Out= Nil, avoid O/L Elaine to Ballarat 220kV line section on trip of Moorabool to Ballarat and Moorabool to Terang 220kV lines, Feedback | NIL
V-S-MNSP1 Export | V::N_X_HWSM_ROTX_S1 | 3.9 (0) | Out = Hazelwood to South Morang 500kV line and Rowville (A) TX, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | V>>N_SMHTX_2 | 3.9 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | V>>SML_ARWB_6 | 3.8 (0) | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V2 | 3.7 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | N^^V_DDSM1 | 3.5 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
V-S-MNSP1 Export | S>>BRDV_RBTU_WEWT | 3.5 (0) | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_X_2SVC_V4 | 3.4 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SML_BUDP_5 | 3.4 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid O/L Ballarat to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line, feedback | Outage
V-S-MNSP1 Export | V::N_HYTR_Q4 | 3.3 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_KTSY_S2 | 2.7 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_BUDP_V1 | 2.6 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_JNWG_xxx | 2.6 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V::N_X_MLSM_EMTT_S2 | 2.6 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N_SMHTX_1 | 2.6 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | V::N_MLSY_Q4 | 2.5 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_MLSY_4BR | 1.8 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage
V-S-MNSP1 Export | V::N_HYSE_Q1 | 1.8 (0.5) | Outage = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>V_SMTXF2_6 | 1.8 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage
V-S-MNSP1 Export | V::N_KGRC_V2 | 1.7 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_ROSM_V2 | 1.7 (0) | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_MLSY_V1 | 1.6 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N-NIL_HG | 1.5 (0) | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | V>>V_NIL_8 | 1.4 (1.7) | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL
V-S-MNSP1 Export | #R014471_008_RAMP_F | 1.3 (0) | Hard Ramping constraint for constraint S>>DVBL_RBTU_WEWT, Effective Date: 31/05/2016, Version: 1 | Outage
V-S-MNSP1 Export | V::N_DDWO_S2 | 1.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_BUDP_V4 | 1.3 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_DDWO_SD | 1.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V>NWB6024_TX1 | 1.2 (0.2) | Out= North West Bend 132kV CB6024, avoid O/L North West Bend 132/66kV #1 TX on trip of Monash-NorthWest Bend #1 132kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V4 | 1.1 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_KTSY_SD | 1.1 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_X_MLSM_EMTT_SD | 1.1 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_X_2SVC_V3 | 1.0 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | N^^V_EPMB_1 | 0.9 (23.8) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
V-S-MNSP1 Export | V::N_BAHO_V2 | 0.9 (0) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HORC_V4 | 0.9 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_KTSY_V2 | 0.8 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-CNUT_HB_15M | 0.8 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line, Feedback | Outage
V-S-MNSP1 Export | V>SML_BUDP_1 | 0.8 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Bendigo to Kerang 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage
V-S-MNSP1 Export | S>>BRMN_BWPA_BRTW | 0.8 (0) | Out= Brinkworth - Mintaro (or any line section between Brinkworth and Mintaro) 132kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | #R014391_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R015058_015_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | V>>DDSH_DDGN_N-2 | 0.7 (0) | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-S-MNSP1 Export | #R013624_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014061_012_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014200_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014295_014_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>SMLKGRC2, Effective Date: 13/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | S>>BWMP_MKRB_BRTW | 0.6 (0) | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Brinkworth - Templers West 275kV on trip of Mokota - Robertstown 275kV line(this offloads Davenport-Mokota 275kV line and trips Hallet 2 windfarm), Feedback | Outage
V-S-MNSP1 Export | S>>DVBL_RBTU_WEWT | 0.6 (0) | Out= Davenport-Belalie 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_MLSY_V4 | 0.6 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | #R013618_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | S>>BGBW_TWPA_TPRS | 0.5 (4.8) | Out= Bungama - Blyth West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West- Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HYMO_V2 | 0.5 (0) | Out = Heywood to Mortlake (HYTS-MOPS) No.2 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_MLMO_V2 | 0.5 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_X_MLSM_EMTT_V2 | 0.5 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-NIL_HH | 0.5 (0) | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | #R013512_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013542_006_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>N_SMHTX_1, Effective Date: 21/12/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013579_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013590_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013592_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013607_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013613_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013647_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013666_024_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013700_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013760_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R013776_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R013781_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R013882_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R014037_013_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014173_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014184_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014193_018_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>SMLBAHO4, Effective Date: 24/11/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014252_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014313_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014348_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>S_CB6033+6225_TX1, Effective Date: 21/07/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014471_008_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint S>>DVBL_RBTU_WEWT, Effective Date: 31/05/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014657_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R014672_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014692_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014729_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014921_005_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014923_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014964_003_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014973_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015039_007_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015060_014_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015060_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | V::N_MLSY_Q1 | 0.4 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | #R013544_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013544_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013557_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013568_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013590_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013592_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013593_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013596_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013649_024_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013667_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013760_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R013939_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014266_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014463_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014560_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014602_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014665_014_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014680_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014692_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014728_009_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014729_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014864_030_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014878_023_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014878_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014879_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 08/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014880_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014903_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014915_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015002_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015028_016_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015058_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HYTR_Q4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | S>>CNDV_BLDV_WEWT | 0.3 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Belalie-Davenport 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_RBPA_WEWT | 0.3 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_MLTR_V4 | 0.3 (0.1) | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | #R013542_006_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>N_SMHTX_1, Effective Date: 21/12/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013559_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013559_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013567_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013578_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013596_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013663_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013700_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013778_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R013882_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R014037_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014061_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014099_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014221_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014463_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014510_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>S_NWRB2_NWRB1, Effective Date: 20/03/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014657_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R014680_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014728_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014789_009_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014789_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014883_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014915_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014921_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014964_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014999_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015002_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015028_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015031_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015035_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | V::N_HORC_SD | 0.3 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_KTSY_MLSM_ET_V2 | 0.3 (0) | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_MLMO_V4 | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>BABE_DDGN_N-2 | 0.3 (0) | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
V-S-MNSP1 Export | V>>SML_ARWB_5 | 0.3 (0) | Out = Ararat to Waubra 220kV line section, or multiple line sections between Ararat and Ballarat, avoid O/L Kerang to Wemen 220 kV line section on loss of Balranald to Darlington Point (X5/1) line | Outage
V-S-MNSP1 Export | V>>SML_NIL_8 | 0.3 (0.7) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
V-S-MNSP1 Export | VSML_030 | 0.3 (0) | Vic to SA on ML upper transfer limit of 30 MW | Outage
V-S-MNSP1 Export | V^SML_NIL_3 | 0.3 (0) | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW | NIL
V-S-MNSP1 Export | #R013512_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013557_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013567_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013600_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013612_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013614_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013635_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R013635_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R013666_024_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013667_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013776_022_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014185_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>SMLBAHO4, Effective Date: 24/11/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014185_018_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>SMLBAHO4, Effective Date: 24/11/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014193_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>SMLBAHO4, Effective Date: 24/11/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014241_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014241_010_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014295_014_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>SMLKGRC2, Effective Date: 13/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014477_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014477_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014510_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>S_NWRB2_NWRB1, Effective Date: 20/03/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014628_014_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>SMLHORC2, Effective Date: 13/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014858_030_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014880_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014923_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014973_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014980_015_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 02/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014999_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 03/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015002_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 02/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015031_014_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDSM_S2, Effective Date: 16/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015031_016_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-S-MNSP1 Export | F_S++ML_R6_1 | 0.2 (0) | Raise 6 sec Service Requirement for SA Generation Event, where Murraylink (Vic to SA transfer) is the largest generation risk in SA, Segment 1 | Outage
V-S-MNSP1 Export | S>>NIL_TWPA_TPRS | 0.2 (0.2) | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_HYTR_S4 | 0.2 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Basslink VIC to TAS. Yallourn W Unit 1 on 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-S-MNSP1 Export | V>>SML_NIL_1 | 0.2 (2.3) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL
V-S-MNSP1 Export | V>>SML_NIL_CONT_7A | 0.2 (0) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Ballarat North to Buangor 66kV line for loss of the Arrarat to Horsham 220kV line | NIL
V-S-MNSP1 Export | V>SMLKGRC1 | 0.2 (0) | Out = Kerang to Redcliffs 220kV line, avoid overloading Darlington Pt to Balranald (X5/1) 220kV line for trip of either Ararat to Horsham or Ballarat to Waubra to Ararat 220 kV line | Outage
V-S-MNSP1 Export | #R013613_022_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013614_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013617_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013618_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013624_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013647_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013700_018_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>SMLBAHO4, Effective Date: 24/11/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R013812_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R013812_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R013939_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014167_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BAHO_S4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014221_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014266_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014313_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014336_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>S_NWRB2_NWRB1, Effective Date: 20/03/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014342_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>S_NWRB2_NWRB1, Effective Date: 20/03/2015, Version: 1 | Outage
V-S-MNSP1 Export | #R014484_011_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014560_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014570_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLMO_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014570_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014665_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014672_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014804_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYMO_Q1, Effective Date: 07/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014858_028_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDWO_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014867_015_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-S-MNSP1 Export | #R014870_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014878_022_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014879_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014879_003_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014903_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014915_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014942_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 28/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014964_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014964_005_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014964_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R014999_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015035_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | #R015058_015_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-S-MNSP1 Export | N>>N-CNUT_HA | 0.1 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Upper Tumut to Lower Tumut (64) on trip of Upper Tumut to Yass (2) line, Feedback | Outage
V-S-MNSP1 Export | V::N_DDSM_S2 | 0.1 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_DDWO_V2 | 0.1 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HORC_V2 | 0.1 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HWSM_Q2 | 0.1 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-S-MNSP1 Export | V:SS_720_HY_TEST_DYN | 0.1 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 720 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-S-MNSP1 Export | V>>N-MSUT_2 | 0.1 (0) | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage
V-S-MNSP1 Export | V>>N-MSUT_4 | 0.1 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
V-S-MNSP1 Export | V>>SML_BABE_4 | 0.1 (0) | Out = Ballarat to Bendigo 220 kV line, avoid O/L of the Darlington Point to Balranald to Buronga (X5/1 and X5/3) 220 kV line on trip of the Shepparton to Fosterville to Bendigo 220 kV line, feedback | Outage
V-S-MNSP1 Export | V>>SML_NIL_7C | 0.1 (0) | Out = Nil, avoid O/L Ararat to Stawell 66kV line for loss of the Ararat to Horsham 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL
V-S-MNSP1 Export | V>>SML_NIL_CONT_7C | 0.1 (0) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Arrarat to Stawell 66kV line for loss of the Arrarat to Horsham 220kV line | NIL
V-S-MNSP1 Export | V>>V_KTSY_P | 0.1 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, 3/5 parallel mode, feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_4A | 0.1 (0) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. | NIL
V-S-MNSP1 Export | V>>V_NIL_5 | 0.1 (20.7) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
V-S-MNSP1 Export | VSML_160 | 0.1 (0) | Vic to SA on ML upper transfer limit of 160 MW | Outage
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 585.8 (451.8) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips | NIL
V-S-MNSP1 Import | SVML_ZERO | 159.1 (65.0) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage
V-S-MNSP1 Import | SVML_000 | 134.9 (0) | South Australia to Victoria on Murraylink upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | #V-S-MNSP1_E_E | 49.1 (0) | V-S-MNSP1.ENERGY * 1 = 100 (Wt = 35) | Outage
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 36.0 (2.2) | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>V_NWRB2_RBNW1 | 35.0 (93.8) | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage
V-S-MNSP1 Import | SVML_ROC_80 | 33.9 (0) | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | V>>V_MLSY_KTSBP_1AR | 27.0 (0) | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
V-S-MNSP1 Import | S>>CNRB_MKRB_WEMWP4 | 13.7 (0) | Out= Canowie-Robertstown 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | S>>BRMN_BWPA_HUWT | 12.3 (1.5) | Out= Brinkworth - Mintaro (or any line section between Brinkworth and Mintaro) 132kV line, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | S>>CNDV_MKRB_WEMWP4 | 12.3 (0) | Out= Canowie-Davenport 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4- Robertstown 132kV line on trip of Mokota-Robertstown 275kV line (this trips Hallet 2 windfarm), Feedback | Outage
V-S-MNSP1 Import | NRM_SA1_VIC1 | 7.3 (0) | Negative Residue Management constraint for SA to VIC flow | NIL
V-S-MNSP1 Import | S>>X_DVCN+CNRB+CB_10 | 7.3 (0) | Out= Davenport-Canowie-Robertstown 275kV and Robertstown 275kV CBs 6616 and 6571, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | CA_SPS_46954420_01 | 6.4 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-S-MNSP1 Import | S>>X_DVCN+CNRB+CB_16 | 6.0 (0) | Out= Davenport-Canowie-Robertstown 275kV and Robertstown 275kV CBs 6616 and 6571, avoid O/L Waterloo East-MWP4-RB 132kV line on trip of Mokota-Robertstown 275kV line(this offloads Belalie-Mokota 275kV line, RBTX1 and trips Hallet Hill WF), Feedback | Outage
V-S-MNSP1 Import | S>V_CB6033+6225_TX2 | 4.7 (38.0) | Out= North West Bend_CB6033 and CB6225; avoid O/L of North West Bend transformer 132/66kV #2 on trip of either Robertstown-NWB #2 132kV line or NWB-Monash #2 132kV line . | Outage
V-S-MNSP1 Import | CA_SPS_46BA5824_01 | 4.5 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-S-MNSP1 Import | S>NWCB6024+25_TX3 | 4.3 (4.3) | Out= North West Bed 132kV CBs 6024 and 6025(this offloads NWB TX2), avoid O/L North West Bend #3 132/66kV TX on trip of North West Bend- Monash #1 132kV line (this splits NWB 132kV bus), Feedback | Outage
V-S-MNSP1 Import | S>RBTX1_RBTX2_WEMWP4 | 2.2 (19.8) | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, Feedbac | Outage
V-S-MNSP1 Import | V>>V_BTRT_SMF2_KT_DR | 1.8 (0) | Out=Brunswick-Richmond 220kV cable and South Morang F2 500/330kV TX, with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypass KTS to WMTS, avoid O/L Rowville-Thomastown 220kV line on trip of Rowville A1 500/220kV TX, Radial, YWPS1 on 500kV, Feedback | Outage
V-S-MNSP1 Import | N>>V_DBUSS_1 | 1.8 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line | Outage
V-S-MNSP1 Import | V>>V_BTTT1MLSY_KT_AR | 1.4 (0) | Out = Brunswick to Thomastown #1 220kV and one Moorabool to Sydenham 500kV line, with KTS 220kV bus #1 & #2 tied and both TTS-KTS lines bypass KTS to WMTS, avoid O/L SMTS F2 txfmr on trip of ROTS A1 500/220kV txfmr, Radial Mode, YWPS1 on 500kV, Feedback | Outage
V-S-MNSP1 Import | V>>V_NIL_1B | 1.4 (0) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line | NIL
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 1.1 (1.2) | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | S>>V_NIL_WTTP_WEMW4 | 1.1 (0) | Out = Nil, avoid overloading the Waterloo East to Morgan Whyalla pump 4 132 kV line on trip of the Waterloo to Templers 132 kV line | NIL
V-S-MNSP1 Import | V>>V_NIL_1A | 1.0 (0) | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
V-S-MNSP1 Import | #R014049_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Outage
V-S-MNSP1 Import | #R014165_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R014921_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
V-S-MNSP1 Import | #R013673_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | F_S++ML_L6_1 | 0.3 (0) | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage
V-S-MNSP1 Import | #R013673_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R014165_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | S>>V_NIL_NIL_HUWT | 0.3 (0) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL
V-S-MNSP1 Import | #R014049_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint S>V_CB6033+6225_TX2, Effective Date: 21/07/2015, Version: 1 | Outage
V-S-MNSP1 Import | #R014391_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | V::N_NILxxx | 574.9 (748.7) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-SA Export | V_S_NIL_ROCOF | 391.9 (0) | Out = Nil, limit Victoria to SA on Heywood flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL
V-SA Export | V::S_NIL_MAXG_xxx | 366.3 (222.4) | Out = Nil, avoid transient instability for trip of the largest generation unit in South Australia | NIL
V-SA Export | VS_250_DYN | 232.3 (17.9) | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Export | V::S_TB_275KV_W_B_1 | 230.4 (0) | Out= Tailem Bend 275 kV West Bus; Vic to SA transient stability limit for loss of the parallel South East - Tailem Bend line (South East Capacitor Available) | Outage
V-SA Export | V::S_SETB_TBSE_1 | 149.9 (0) | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available).(NOTE: Assumed both Black Range series capacitors O/S). | Outage
V-SA Export | V>>S_NIL_KHTB2_KHTB1 | 148.1 (75.7) | Out = Nil, avoid overloading Keith to Tailem Bend #1 132 kV line on trip of Keith to Tailem Bend #2 132 kV line | NIL
V-SA Export | V::S_NIL_TBSE | 145.7 (19.7) | Out = Nil; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available) | NIL
V-SA Export | V>>S_NIL_SETB_SGKH | 125.7 (242.4) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line | NIL
V-SA Export | V:S_PA_SVC_575 | 121.6 (0) | Out= one Para SVC, Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 575 MW | Outage
V-SA Export | V::S_NIL_TBSE_2 | 101.0 (0) | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | S>>NIL_SETB_KHTB1 | 92.3 (164.1) | Out = Nil, avoid overloading Keith to Tailem Bend #1 132 kV line on trip of South East to Tailem Bend 275 kV line | NIL
V-SA Export | #V-SA_E_E | 91.1 (0) | V-SA.ENERGY * 1 <= 580 (Wt = 35) | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 76.3 (0) | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Export | S>>KHKN_SETB_SGKH | 60.2 (7.3) | Out = Keith - Kincraig 132 kV line; avoid O/L of Snuggery - Keith 132kV line on trip of either South East - Tailem Bend 275 kV line | Outage
V-SA Export | V::S_XKHTB1+2_MAXG | 52.2 (86.5) | Out = both Keith to Tailem Bend 132 kV lines, avoid transient instability for trip of the largest generation unit in South Australia | Outage
V-SA Export | V:S_600_HY_TEST | 47.8 (0) | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Export | V>>S_KNPW_SETB_SGKH | 47.4 (16.3) | Out= Kincraig - Penola West 132kV line, avoid O/L Snuggery - Keith 132kV on trip of one South East - Tailem Bend 275kV line, Feedback | Outage
V-SA Export | V::S_BLKRG_TBSE_2 | 44.9 (0) | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V^S_HYCP | 35.8 (32.3) | Out = NIL, maintain adequate post contingent voltages for loss of the Heywood to Mortlake 500 kV line. | NIL
V-SA Export | S>>NIL_TBCG_TBTU_1 | 34.7 (0) | Out= Nil, avoid O/L Tailem Bend-Tungkillo 275kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | NIL
V-SA Export | V^^S_MLSY_3 | 34.6 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | S>>MOTB_TBTU_TBCG | 32.9 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V^S_NIL_SA_RECLASS | 32.2 (0) | Out = Nil, limit generation in SA to prevent flow on Heywood interconnector exceeding 700 MW following reduction in MW output from multiple generating units in SA. | NIL
V-SA Export | V_S_ROCOF | 31.8 (14.3) | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage
V-SA Export | V::S_BLKRG_MAXG_2 | 30.8 (0) | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | S>>X_TB-EBUS+CGTB_3 | 27.9 (0) | Out = Tailembend 275kV East Bus (i.e. and associated CBs) + Cherry Gardens-Tailembend 275kV line +Tailembend CBs 6535 & 6536 O/S, avoid O/L TB-MO #1 132kV line on trip of SE-TB #2 275kV line (this offloads SE-TB #1 275kV & TB-TU 275kV lines), | Outage
V-SA Export | NRM_VIC1_SA1 | 26.8 (0) | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | V^^S_TB_275KV_E_SETB | 23.3 (0) | Out= Tailembend 275kV East Bus(i.e. CBs 6594, 6535 and 6597 OPEN with Tailembend 275/132kV TX4 & C64 O/S); Vic to SA Long Term Voltage Stability limit for loss of one South East-Tailembend 275kV line (NOTE: NPS and Playford assumed to be O/S) | Outage
V-SA Export | V::S_MOTB_MAXG | 17.1 (8.1) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V::S_HYSE | 14.7 (3.1) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of the remaining South East - Heywood 275 kV line. | Outage
V-SA Export | S>>X_CGTB+TB35+36_08 | 11.8 (0.1) | Out= Cherry Gardens- Tailembend 275kV line & Tailembend 275kV CBs 6536 & 6535, avoid O/L Snuggery-Keith 132kV line on trip of South East -Tailembend 275kV #2 line(this offloads South East -Tailembend 275kV #1 line), Feedback | Outage
V-SA Export | S>>NIL_SETB_SETB_1 | 11.0 (0) | Out= Nil, avoid O/L one South East-Tailem Bend 275kV on trip of other South East-Tailem Bend 275kV line, feedback | NIL
V-SA Export | S>>X_CGTB+TB35+36_13 | 10.7 (0.5) | Out= Cherry Gardens- Tailembend 275kV line & Tailembend 275kV CBs 6536 & 6535, avoid O/L Tailembend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line(this offloads Tailem Bend 275/132kC TX4), Feedback | Outage
V-SA Export | V^^S_TBCPTX_MAXG | 10.6 (0) | Out= Tailem Bend 275/132kV transformer and Tailem Bend 100Mvar Cap Bank; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage
V-SA Export | V::S_NIL_SETB_SECP | 10.2 (0.3) | Out = Nil; Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | V::S_XKHTB1+2_SETB | 10.1 (101.3) | Out = both Keith to Tailem Bend 132 kV lines, avoid transient instability for trip a South East to Tailem Bend 275 kV line | Outage
V-SA Export | V^^S_XPAVC_SETB_2 | 10.0 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps) O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | F_ESTN++HYMO_L60 | 9.8 (1.3) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
V-SA Export | V^^S_MLSY_2 | 9.8 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | F_ESTN++HYMO_L5 | 9.7 (0.2) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V^^S_BLKRG_TBSE_2 | 8.8 (0) | Out = both Black Range series capacitors O/S; Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V::N_HWSM_V2 | 8.4 (0.4) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HYSE_V2 | 8.2 (0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_500_HY_TEST_DYN | 8.1 (0) | VIC to SA on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Export | V::N_SMF2_V4 | 7.7 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_BUDP_V4 | 7.0 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_EPMB_V4 | 6.3 (10.3) | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V>>S_NIL_PWKN_SGKH | 5.9 (44.8) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL
V-SA Export | V::S_BLKRG_TBSE_3 | 5.8 (0) | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V>S_460_DYN | 5.8 (1.8) | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Export | F_ESTN++MLTR_L5 | 5.6 (0.5) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | V:S_X-PA_S+P_525 | 5.4 (0) | Out= One Para SVC and other Para SVC POD O/S (Note: with both Black Range Series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 525 MW. | Outage
V-SA Export | VS_350 | 5.3 (0) | Victoria to SA on VicSA upper transfer limit of 350 MW | Outage
V-SA Export | V::N_HWSM_V3 | 4.9 (6.8) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V^^S_XPACP_MAXG | 4.8 (0) | Out = Para C61 and C62 capacitor banks (both capacitors) O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V:S_500_HY_TEST | 4.5 (0) | VIC to SA on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Export | V::N_BAHO_V4 | 4.3 (11.6) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_KGRC_S2 | 4.3 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | S>>NIL_TBTU_TBMO_1 | 4.2 (0) | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | V:S_550 | 3.9 (0) | Maintain maximum transfer limit of 550 MW on Heywood IC from Vic to SA to avoid oscillatory instability | Outage
V-SA Export | V::N_BUDP_V3 | 3.8 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V>>S_KHTB1_SETB_KHTB | 3.7 (26.6) | Out = Keith - Tailem Bend #1 132 kV line, avoid O/L on Keith - Tailem Bend #2 line for trip of either South East - Tailem Bend lines. | Outage
V-SA Export | V::S_SETB_SETB | 3.6 (52.2) | Out = South East to Tailem Bend 275 kV line, avoid transient instability for loss of the parallel South East to Tailem Bend 275 kV line | Outage
V-SA Export | V::N_HYSE_V1 | 3.5 (2.0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V>>V_MLSY_4BR | 3.4 (0) | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Export | V>S_460 | 3.3 (259.9) | VIC to SA on Heywood upper transfer limit of 460 MW | Outage
V-SA Export | V::N_X_HWSM_ROTX_S1 | 3.3 (0) | Out = Hazelwood to South Morang 500kV line and Rowville (A) TX, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | V::N_BUDP_V1 | 3.0 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_SMSC_V4 | 2.8 (1.5) | Out = 1 x South Morang Series Capacitor 330kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::S_NIL_TBSE_1 | 2.8 (0) | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | F_ESTN++MLTR_L60 | 2.7 (0.3) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_QNV++HYMO_L5 | 2.7 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_JNWG_xxx | 2.6 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | V::N_KTSY_S2 | 2.6 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | SA_HYSE1 | 2.4 (0.2) | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW | Outage
V-SA Export | V::N_X_MLSM_EMTT_S2 | 2.4 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_570_DYN | 2.3 (0) | Out = NIL, VIC to SA on Heywood upper transfer limit of 570 MW based on oscillatory stability, dynamic headroom, DS formulation only. | NIL
V-SA Export | F_ESTN++MLMO_L5 | 2.2 (0.2) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | F_ESTN++MLMO_L60 | 2.2 (0.5) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_BUDP_V2 | 2.1 (0.1) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::S_X_KHTB1+SG_SETB | 2.1 (0) | Out = Keith-Tailem Bend #1 132kV & Keith-Snuggery 132kV; Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage
V-SA Export | V::S_BNMT_MAXG_2 | 2.0 (0) | Out= Blanche - Mt Gambier 132kV line; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage
V-SA Export | V::S_KHTB1_SETB | 1.9 (0) | Out= Keith - Tailem Bend #1 132 kV line; Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line. | Outage
V-SA Export | V^^S_XPAVC_MAXG_2 | 1.9 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps) O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V::N_HYTR_Q4 | 1.7 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | S>>NIL_SETB_KHTB2 | 1.5 (29.2) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL
V-SA Export | V>>S_MOTB_TBCG_TBTU | 1.4 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V^^S_PWSE_SETB | 1.4 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | S>>PWSE_SETB_SETB_2 | 1.3 (0) | Out= Penola West - South East 132 kV line (Note: with both Black Range series caps O/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage
V-SA Export | V::N_ESTN_HYSE_VF | 1.3 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 3 | Outage
V-SA Export | V::N_MLSY_Q4 | 1.3 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | #R013750_002_RAMP_F | 1.3 (0) | Hard Ramping constraint for constraint V>>S_TB6125+28_KHTB1, Effective Date: 21/12/2015, Version: 1 | Outage
V-SA Export | V::N_DDWO_S2 | 1.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_DDWO_SD | 1.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_SMF2_V2 | 1.3 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_X_MLSM_EMTT_SD | 1.2 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_BYPASS_HW_SY_V4 | 1.1 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_KTSY_V2 | 1.1 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_QNV++HYMO_L60 | 1.0 (1.3) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | S>>NIL_TBTU_TBMO | 1.0 (112.0) | Out= Nil, avoid overloading Tailem Bend to Mobilong 132 kV line on trip of Tailem Bend to Tungkillo 275 kV line | NIL
V-SA Export | V::N_KTSY_SD | 1.0 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_X_2SVC_V3 | 1.0 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V:S_570 | 1.0 (0) | Out = NIL, VIC to SA on Heywood upper transfer limit of 570 MW based on oscillatory stability. | NIL
V-SA Export | V::N_DDWO_V2 | 0.9 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_ARDM_560 | 0.9 (0) | Maintain maximum transfer limit of 560 MW on Heywood IC from VIC to SA to avoid oscillatory instability | Outage
V-SA Export | V::N_HORC_V4 | 0.8 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V_HYMO2_1 | 0.8 (0) | Out = Heywood to Mortlake No.2 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage
V-SA Export | #R013676_007_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>S_KHTB1_SETB_KHTB, Effective Date: 23/04/2014, Version: 1 | Outage
V-SA Export | #R014328_006_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>S_MOTB_TBCG_TBTU, Effective Date: 18/07/2016, Version: 1 | Outage
V-SA Export | CA_MQS_473FDF2B_01 | 0.8 (0) | Constraint Automation, O/L TABSES_2 @S_EAST for CTG LSIC on trip of T_BEND-S_EAST 275KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage
V-SA Export | V::S_NIL_SETB_SECP_2 | 0.8 (0) | Out = Nil(Note: with both Black Range series capacitors O/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | V_HYML1_4 | 0.8 (0.9) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage
V-SA Export | #R014883_005_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
V-SA Export | F_QNV++MLTR_L5 | 0.7 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_BAHO_V2 | 0.7 (0) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_HYTR_V4 | 0.7 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::S_TBCP1_SETB_2 | 0.7 (0) | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V:S_BLKRG_570 | 0.7 (0) | Out = both or one Black Range series capacitors O/S, VIC to SA to on Heywood upper transfer limit of 570 MW based on oscillatory stability. | Outage
V-SA Export | V:S_MSUT_560 | 0.7 (0) | Out = Murray - Upper Tumut (65) 330kV line, VIC to SA on Heywood upper transfer limit of 560 MW based on oscillatory stability. | Outage
V-SA Export | V>>DDSH_DDGN_N-2 | 0.7 (0) | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-SA Export | #R014164_004_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint S>>BNMT_SETB_SGKH, Effective Date: 02/04/2015, Version: 1 | Outage
V-SA Export | #R014890_013_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | V::S_KHKN_SETB | 0.6 (0) | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of South East - Tailem Bend 275kV line.. | Outage
V-SA Export | V::N_X_2SVC_V4 | 0.5 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | #R013579_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013590_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013592_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013607_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013613_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013647_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013666_024_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-SA Export | #R013700_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013776_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-SA Export | #R014026_006_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::S_PAVC_SETB, Effective Date: 18/03/2015, Version: 1 | Outage
V-SA Export | #R014108_003_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint S>>KHKN_SETB_SGKH, Effective Date: 18/06/2014, Version: 1 | Outage
V-SA Export | #R014164_004_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint S>>BNMT_SETB_SGKH, Effective Date: 02/04/2015, Version: 1 | Outage
V-SA Export | #R014173_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014184_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014223_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::S_TB_275KV_W_B_1, Effective Date: 21/06/2016, Version: 1 | Outage
V-SA Export | #R014252_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014259_017_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::S_X_KHTB1+SG_SETB, Effective Date: 21/04/2015, Version: 1 | Outage
V-SA Export | #R014268_006_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::S_SETB_TBSE_1, Effective Date: 17/06/2016, Version: 1 | Outage
V-SA Export | #R014268_006_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::S_SETB_TBSE_1, Effective Date: 17/06/2016, Version: 1 | Outage
V-SA Export | #R014269_006_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::S_SETB_TBSE_1, Effective Date: 17/06/2016, Version: 1 | Outage
V-SA Export | #R014388_020_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014803_003_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014923_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | #R014964_003_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014973_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | #R015039_007_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R015052_003_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::S_BLKRG_MAXG_2, Effective Date: 12/10/2016, Version: 1 | Outage
V-SA Export | #R015058_015_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | #R015060_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | V::N_MLMO_V4 | 0.4 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V^^S_MOTB_MAXG | 0.4 (0) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V^^S_SETB_SETB | 0.4 (0.4) | Out= South East - Tailem Bend 275 kV line; Vic to SA Long Term Voltage Stability limit for loss of the parallel South East - Tailem Bend line. | Outage
V-SA Export | #R013544_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013544_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013557_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013568_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013592_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013596_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013649_024_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-SA Export | #R013667_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013700_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013775_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::S_XKHTB1+2_MAXG, Effective Date: 21/04/2015, Version: 1 | Outage
V-SA Export | #R013939_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014008_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint S>>X_TB-EBUS+CGTB_2, Effective Date: 15/02/2016, Version: 1 | Outage
V-SA Export | #R014037_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014108_003_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint S>>KHKN_SETB_SGKH, Effective Date: 18/06/2014, Version: 1 | Outage
V-SA Export | #R014258_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::S_KHTB1_SETB, Effective Date: 02/04/2015, Version: 1 | Outage
V-SA Export | #R014259_017_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::S_X_KHTB1+SG_SETB, Effective Date: 21/04/2015, Version: 1 | Outage
V-SA Export | #R014463_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014560_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014680_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014729_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014753_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014822_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014858_030_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014864_030_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014879_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 08/11/2016, Version: 1 | Outage
V-SA Export | #R014921_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014954_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014999_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 03/11/2016, Version: 1 | Outage
V-SA Export | #R015002_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
V-SA Export | #R015010_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R015060_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | F_QNV++MLMO_L5 | 0.3 (0.9) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+MLSY_L60 | 0.3 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_DDWO_V4 | 0.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_HYMO_V2 | 0.3 (0) | Out = Heywood to Mortlake (HYTS-MOPS) No.2 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HYSE_Q1 | 0.3 (0) | Outage = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_KTSY_MLSM_ET_V2 | 0.3 (0) | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_MLSY_V4 | 0.3 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_X_MLSM_EMTT_V2 | 0.3 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_NIL_SETB_SECP_1 | 0.3 (0) | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | V^^S_TBCB94_35_SETB | 0.3 (0) | Out= Tailem Bend 275kV CB6594 OR CB6535 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | #R013559_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013559_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013567_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013578_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013663_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013676_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>S_KHTB1_SETB_KHTB, Effective Date: 23/04/2014, Version: 1 | Outage
V-SA Export | #R013778_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-SA Export | #R014037_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014061_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014061_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014099_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014189_020_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014221_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014258_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::S_KHTB1_SETB, Effective Date: 02/04/2015, Version: 1 | Outage
V-SA Export | #R014266_017_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014266_017_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014442_006_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V:S_PA_SVC_575, Effective Date: 06/07/2016, Version: 1 | Outage
V-SA Export | #R014463_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014477_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014495_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014570_015_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014570_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014602_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014680_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014728_009_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014728_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014753_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014789_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014821_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014822_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014867_015_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014878_022_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
V-SA Export | #R014878_022_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
V-SA Export | #R014883_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
V-SA Export | #R014890_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014899_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014903_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014921_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014964_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R015010_003_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R015035_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | #R015058_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HYTR_Q4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | F_QNV++HYMO_L6 | 0.3 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++MLTR_L60 | 0.3 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L5 | 0.3 (0.1) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L60 | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_BYPASS_HW_SY_V2 | 0.3 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_ESTN_HYSE_VD | 0.3 (0.3) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
V-SA Export | V::N_KGRC_V2 | 0.3 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_PA_SVC_550 | 0.3 (0) | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage
V-SA Export | #R013557_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013567_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013590_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013600_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013612_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013614_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013667_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R014061_019_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014155_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint S>>BNMT_SETB_SGKH, Effective Date: 02/04/2015, Version: 1 | Outage
V-SA Export | #R014241_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014241_010_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014252_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014266_010_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014269_006_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::S_SETB_TBSE_1, Effective Date: 17/06/2016, Version: 1 | Outage
V-SA Export | #R014346_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint S>>PWSE_SETB_SETB_2, Effective Date: 25/07/2016, Version: 1 | Outage
V-SA Export | #R014346_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint S>>PWSE_SETB_SETB_2, Effective Date: 25/07/2016, Version: 1 | Outage
V-SA Export | #R014367_004_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V_S_ROCOF, Effective Date: 07/01/2015, Version: 1 | Outage
V-SA Export | #R014477_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014531_015_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014602_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014602_019_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014821_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014858_028_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014858_030_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014864_030_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014878_023_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
V-SA Export | #R014880_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
V-SA Export | #R014890_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014899_009_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014915_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014915_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014923_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | #R015002_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
V-SA Export | #R015002_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 02/12/2016, Version: 1 | Outage
V-SA Export | #R015039_007_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R015052_003_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::S_BLKRG_MAXG_2, Effective Date: 12/10/2016, Version: 1 | Outage
V-SA Export | #R015058_015_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | F_QNV++MLMO_L60 | 0.2 (1.6) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+HYMO_L5 | 0.2 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_ESTN_HYSE_VE | 0.2 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
V-SA Export | V::S_NIL_TBSE_3 | 0.2 (0) | Out = Nil(Note: with only one Black Range series capacitor I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | V::S_SEVC_MAXG | 0.2 (8.1) | Out= South East one SVC (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V:S_XPAVC_540 | 0.2 (0) | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), VIC to SA to on Heywood upper transfer limit of 540 MW based on oscillatory stability. | Outage
V-SA Export | V>>S_KH_X_SETB_SETB | 0.2 (15.4) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East - Tailembend 275kV on trip of one South East - Tailembend 275kV line, Feedback | Outage
V-SA Export | #R013523_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>S_TB6125+28_KHTB1, Effective Date: 21/12/2015, Version: 1 | Outage
V-SA Export | #R013596_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013613_022_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013614_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013617_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013647_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
V-SA Export | #R013666_024_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-SA Export | #R013666_025_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWGVF_R, Effective Date: 01/07/2015, Version: 1 | Outage
V-SA Export | #R013767_018_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V_S_ROCOF, Effective Date: 07/01/2015, Version: 1 | Outage
V-SA Export | #R013767_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V_S_ROCOF, Effective Date: 07/01/2015, Version: 1 | Outage
V-SA Export | #R013775_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::S_XKHTB1+2_MAXG, Effective Date: 21/04/2015, Version: 1 | Outage
V-SA Export | #R013812_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-SA Export | #R013812_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
V-SA Export | #R014061_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014138_005_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::S_KHTB1_SETB, Effective Date: 02/04/2015, Version: 1 | Outage
V-SA Export | #R014167_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BAHO_S4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014167_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014196_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>S_KNPW_SETB_SGKH, Effective Date: 08/10/2013, Version: 1 | Outage
V-SA Export | #R014207_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014223_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::S_TB_275KV_W_B_1, Effective Date: 21/06/2016, Version: 1 | Outage
V-SA Export | #R014388_020_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Outage
V-SA Export | #R014413_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V:S_PA_SVC_575, Effective Date: 06/07/2016, Version: 1 | Outage
V-SA Export | #R014477_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014484_011_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014490_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V:S_ARDM_560, Effective Date: 03/02/2016, Version: 1 | Outage
V-SA Export | #R014490_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V:S_ARDM_560, Effective Date: 03/02/2016, Version: 1 | Outage
V-SA Export | #R014495_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014531_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014560_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014570_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLMO_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014777_018_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V:S_MSUT_560, Effective Date: 06/09/2016, Version: 1 | Outage
V-SA Export | #R014867_015_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
V-SA Export | #R014870_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
V-SA Export | #R014878_023_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
V-SA Export | #R014879_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 08/11/2016, Version: 1 | Outage
V-SA Export | #R014879_003_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
V-SA Export | #R014903_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014942_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 28/11/2016, Version: 1 | Outage
V-SA Export | #R014954_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250_DYN, Effective Date: 17/08/2016, Version: 1 | Outage
V-SA Export | #R014964_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014964_003_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
V-SA Export | #R014967_005_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>S_460, Effective Date: 07/12/2015, Version: 1 | Outage
V-SA Export | #R014980_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 02/12/2016, Version: 1 | Outage
V-SA Export | #R014980_016_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWO_SD, Effective Date: 02/12/2016, Version: 1 | Outage
V-SA Export | #R014999_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
V-SA Export | #R014999_003_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
V-SA Export | #R015035_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
V-SA Export | #R015046_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::S_TBCP1_SETB_2, Effective Date: 26/09/2016, Version: 1 | Outage
V-SA Export | #R015046_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::S_TBCP1_SETB_2, Effective Date: 26/09/2016, Version: 1 | Outage
V-SA Export | F_ESTN++HYTR_L60 | 0.1 (1.3) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_QNV+HYMO_L6 | 0.1 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLSY_L6 | 0.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | S>TB6123+29_KHTB2 | 0.1 (0) | Out= Tailem Bend CB 6123 and/or CB 6129 (both or either CB), avoid O/L Keith - Tailem Bend 132kV #2 line on trip of Tailem Bend 275/132kV transformer, Feedback | Outage
V-SA Export | V::N_DDWO_Q2 | 0.1 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-SA Export | V::N_HORC_SD | 0.1 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_HORC_V2 | 0.1 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HWSM_Q2 | 0.1 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-SA Export | V::N_HWSM_S1 | 0.1 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | V::N_HYSE_S1 | 0.1 (0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_MLSY_V2 | 0.1 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_MLTR_V4 | 0.1 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_ROSM_V2 | 0.1 (0) | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::S_MOTB_SETB | 0.1 (0) | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage
V-SA Export | V:SS_820_HY_TEST_DYN | 0.1 (0) | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Export | V>>S_SETB_SETB_SGKH | 0.1 (0.2) | Out= one South East to Tailem Bend 275kV line, avoid O/L Snuggery to Keith line on trip of the remaining South East to Tailem Bend line. | Outage
V-SA Export | V>S_NIL_HYSE | 0.1 (6.2) | Out = NIL, avoid O/L either Heywood to South East 275 kV line on trip of parallel circuit, flow VIC to SA, feedback | NIL
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 945.3 (872.3) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-SA Import | V>>V_ROTS_TX_2A_R | 98.0 (0.2) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Import | V>>V_BTRT_2A_R | 90.3 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 500kV, Feedback | Outage
V-SA Import | V>>V_BTRT_2_P | 71.5 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Parallel Mode, Feedback | Outage
V-SA Import | V>>V_KTS_TX_A2_2A_R | 54.0 (2.7) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | V>>V_KTSY_1_R | 38.1 (1.4) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Import | #V-SA_E_E | 31.8 (0) | V-SA.ENERGY * 1 <= 580 (Wt = 35) | Outage
V-SA Import | SV_000 | 29.5 (0) | SA to Victoria on VicSA upper transfer limit of 0 MW | Outage
V-SA Import | V>>V_MLSY_KTSBP_1AR | 28.1 (0) | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
V-SA Import | F_S++HYSE_L6_1 | 23.7 (81.3) | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | S_V_000_HY_DYN | 21.5 (0) | SA to VIC on Heywood upper transfer limit of 0 MW, dynamic headroom, DS formulation only. | Outage
V-SA Import | S>>V_NIL_SETX_SETX1 | 15.2 (0) | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | NIL
V-SA Import | S>>V_NIL_SETX_SETX | 12.2 (56.2) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer | NIL
V-SA Import | V>>V_CBTS_TX_2A_R | 11.5 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-SA Import | F_S++HYSE_L60 | 10.8 (19.5) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
V-SA Import | V>>V_BTRT_2B_R | 10.3 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 220kV, Feedback | Outage
V-SA Import | V::N_DDSM_V2 | 10.3 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | CA_SPS_46545836_02 | 7.9 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-SA Import | V>>V_KTS_TX_A3_2A_R | 7.1 (2.1) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | S::V_TBSE_TBSE | 6.7 (0) | Out = one Tailembend-South East 275kV line; SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | CA_SPS_46BA5824_01 | 6.6 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-SA Import | CA_SPS_46954420_01 | 6.4 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-SA Import | NRM_SA1_VIC1 | 6.1 (0) | Negative Residue Management constraint for SA to VIC flow | NIL
V-SA Import | S>>V_KNPW_SETX_SETX | 4.3 (1.2) | Out = Kincraig to Penola West 132 kV line, avoid overloading the remaining South East 275/132kV transformer on trip of one South East 275/132kV transformer | Outage
V-SA Import | SA_HYSE2 | 3.6 (0) | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage
V-SA Import | S_V_NIL_ROCOF | 3.3 (0) | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. | NIL
V-SA Import | S::V_TBSE_TBSE_1 | 2.3 (0) | Out = one Tailembend-South East 275kV line; SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | V>>V_BTRT_SMF2_KT_DR | 2.2 (0) | Out=Brunswick-Richmond 220kV cable and South Morang F2 500/330kV TX, with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypass KTS to WMTS, avoid O/L Rowville-Thomastown 220kV line on trip of Rowville A1 500/220kV TX, Radial, YWPS1 on 500kV, Feedback | Outage
V-SA Import | V>>V_BTTT1MLSY_KT_AR | 1.4 (0) | Out = Brunswick to Thomastown #1 220kV and one Moorabool to Sydenham 500kV line, with KTS 220kV bus #1 & #2 tied and both TTS-KTS lines bypass KTS to WMTS, avoid O/L SMTS F2 txfmr on trip of ROTS A1 500/220kV txfmr, Radial Mode, YWPS1 on 500kV, Feedback | Outage
V-SA Import | #R013811_001_RAMP_F | 1.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | V>>V_NIL_6A_R | 1.1 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL
V-SA Import | S>>MOTB_SETX2_SETX1 | 0.9 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L South East 132/275kV TX1 on trip of South East 132/275kV TX2(for TX component SECS assumed O/S), Feedback | Outage
V-SA Import | #R013888_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | #R014363_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | S>>NIL_NIL_SETX12 | 0.8 (0) | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL
V-SA Import | #R013997_001_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | #R013624_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013878_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R014200_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | #R013618_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013904_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R013512_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013781_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | #R013918_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R014921_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
V-SA Import | #R015041_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
V-SA Import | #R013515_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/10/2015, Version: 1 | Outage
V-SA Import | #R013593_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013830_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R013904_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R015028_016_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-SA Import | #R015031_016_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-SA Import | CA_SPS_46545836_01 | 0.3 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-SA Import | S:V_PA_SVC_420 | 0.3 (0) | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | #R015012_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Outage
V-SA Import | #R015028_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-SA Import | #R015031_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
V-SA Import | #V-SA_RAMP_I_F | 0.3 (1.6) | V-SA >= MIN(-37, InitialFlow + 50) (Wt=35) | Outage
V-SA Import | S>>NIL_TBSE_TBKH1 | 0.3 (0) | Out= Nil, avoid O/L Tailem Bend - Keith #1 132kV on trip of either Tailem Bend - South East 275kV line, Feedback | NIL
V-SA Import | S>>V_KHTB1_TBSE_TBKH | 0.3 (0) | Out = Keith - Tailem bend #1 132 kV line; avoid Tailem Bend - Keith #2 line OL on trip of either one of Tailem Bend - South East 275 kV lines. | Outage
V-SA Import | V>>BABE_DDGN_N-2 | 0.3 (0) | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
V-SA Import | #R013512_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013515_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/10/2015, Version: 1 | Outage
V-SA Import | #R013618_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013997_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | #R014103_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R014211_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint S>>V_KNPW_SETX_SETX, Effective Date: 30/03/2016, Version: 1 | Outage
V-SA Import | #R014219_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTSY_1_R, Effective Date: 01/07/2016, Version: 1 | Outage
V-SA Import | #R014363_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | S:V_500_HY_TEST_DYN | 0.2 (0) | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | #R013624_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
V-SA Import | #R013863_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R013870_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R013873_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
V-SA Import | #R013888_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | #R014211_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint S>>V_KNPW_SETX_SETX, Effective Date: 30/03/2016, Version: 1 | Outage
V-SA Import | #R014409_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
V-SA Import | S:VS_X-PA_S+P_380 | 0.1 (0) | Out= One Para SVC and other Para SVC POD O/S (Note: with both Black Range Series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 380 MW | Outage
V-SA Import | S>>SETB_TBSE_TBKH2_1 | 0.1 (0) | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend-Keith #2 132kV Line on trip of other Tailem Bend-South East 275kV line, Feedback | Outage
V-SA Import | V>>V_KTSY_P | 0.1 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, 3/5 parallel mode, feedback | Outage
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 957.1 (873.1) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
VIC1-NSW1 Export | V::N_NILxxx | 941.7 (1045.5) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
VIC1-NSW1 Export | V>>N-NIL_HA | 312.8 (33.5) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | NIL
VIC1-NSW1 Export | V>>V_ROTS_TX_2A_R | 98.3 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V>>SML_NIL_CONT_7B | 92.6 (16.3) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Buangor to Arrarat 66kV line for loss of the Arrarat to Horsham 220kV line | NIL
VIC1-NSW1 Export | V>>V_BTRT_2A_R | 78.0 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 500kV, Feedback | Outage
VIC1-NSW1 Export | V>>N_DDMS_2 | 65.9 (2.9) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Dederang to Murray 330 kV line, feedback | Outage
VIC1-NSW1 Export | V>>V_BTRT_2_P | 65.1 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Parallel Mode, Feedback | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2A_R | 54.3 (2.6) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V>>N-BUDP_2N | 50.7 (0) | Out= Buronga-DarlingtonPt(X5), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | V>>V_KTSY_1_R | 37.5 (1.4) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, radial mode, YWG1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V::N_HYSE_V2 | 32.1 (0) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>SML_NIL_7B | 30.2 (32.3) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
VIC1-NSW1 Export | V>>V_MLSY_KTSBP_1AR | 26.9 (0) | Out= One Moorabool to Sydenham 500kV line with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypassing KTS to WMTS, avoid O/L South Morang F2 500/330kV txfmr on trip of Rowville A1 500/220kV txfmr, Radial mode, YWPS1 on 500kV, Feedback | Outage
VIC1-NSW1 Export | V>>N-DDWO_RADIAL_2 | 25.8 (0) | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | V>>V_DDSM_1 | 20.2 (0) | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_V2 | 19.3 (0.7) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMSC_V4 | 17.7 (2.7) | Out = 1 x South Morang Series Capacitor 330kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 11.8 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_CBTS_TX_2A_R | 11.2 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V>>V_BTRT_2B_R | 9.7 (0) | Out= Brunswick to Richmond 220kV line, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer, Radial Mode, YWPS unit 1 on 220kV, Feedback | Outage
VIC1-NSW1 Export | V>>N-JNWO_RADIAL_2 | 8.3 (0) | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_S1 | 8.0 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | CA_SPS_46545836_02 | 7.9 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | V::N_BUDP_V4 | 7.9 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_V4 | 7.3 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_BAHO_V4 | 7.1 (11.8) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HYTR_V4 | 7.0 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2A_R | 7.0 (2.1) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_EPMB_V4 | 6.8 (10.3) | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V-MSUT_1 | 6.7 (2.9) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to lower Tumut (66) 330 kV line | Outage
VIC1-NSW1 Export | CA_SPS_46BA5824_01 | 6.6 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | V::N_X_2SVC_V4 | 6.6 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | CA_SPS_46954420_01 | 6.4 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | V::N_KGRC_S2 | 6.3 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_V3 | 5.0 (7.4) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HYSE_V1 | 5.0 (2.7) | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N_SMHTX_1 | 4.8 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Export | N>>N-DTSS_20 | 4.3 (0) | Out = Dapto-SydneySouth(11), avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | Outage
VIC1-NSW1 Export | V>>SML_NIL_MLTS_N-2 | 4.3 (23.0) | Out= Nil, avoid O/L Elaine to Ballarat 220kV line section on trip of Moorabool to Ballarat and Moorabool to Terang 220kV lines, Feedback | NIL
VIC1-NSW1 Export | V::N_BUDP_V3 | 4.2 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-JNWO_RADIAL_1 | 4.1 (0) | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | V::N_X_HWSM_ROTX_S1 | 3.9 (0) | Out = Hazelwood to South Morang 500kV line and Rowville (A) TX, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | V>>N_SMHTX_2 | 3.9 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V2 | 3.8 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_0800 | 3.7 (0) | Discretionary Vic to NSW transfer upper limit of 800 MW | Outage
VIC1-NSW1 Export | V::N_HYTR_Q4 | 3.6 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_ROSM_V2 | 3.6 (0) | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | N::V_GRYS_2 | 3.5 (0) | out = Gullen Range to Yass (3J), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_VF | 3.5 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 3 | Outage
VIC1-NSW1 Export | N>>N-NIL_01N | 3.4 (0) | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL
VIC1-NSW1 Export | N>>N-DTKV_E_15M | 3.3 (0) | Out = Dapto-KangarooValley(18), avoid O/L Canberra to Yass(9) on trip of Lower Tumut to Yass (3) line, Feedback | Outage
VIC1-NSW1 Export | V::N_BUDP_V1 | 3.1 (0) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_S2 | 2.8 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HG | 2.8 (0) | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V::N_JNWG_xxx | 2.6 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_DDWO_V2 | 2.5 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLSY_Q4 | 2.5 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_MLSM_EMTT_S2 | 2.3 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-JNWG_RADIAL_1 | 2.3 (0) | Out = Jindera to Wagga(62), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | CA_SPS_4733E84B_01 | 2.0 (0) | Constraint Automation, O/L 9 @CANBERRA for CTG LNPY on trip of DAPTO-KANGAROO 18 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 1.9 (0.9) | Negative Residue Management constraint equation for VIC to NSW flow | NIL
VIC1-NSW1 Export | V::N_BUDP_V2 | 1.9 (0.4) | Out = Buronga to Darlington Point 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_V2 | 1.9 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | N::V_CNUT_2 | 1.8 (3.5) | Out = Upper Tumut -Canberra(01), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V::N_HYSE_Q1 | 1.8 (0.5) | Outage = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_MLSM_ET_V2 | 1.8 (0) | Out = Keilor to Sydenham & Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_SMTXF2_6 | 1.8 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage
VIC1-NSW1 Export | V::N_KGRC_V2 | 1.7 (0) | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_V2 | 1.5 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | N>>N-BYSW_B | 1.4 (0) | Out = Bannaby-Sydney West(39), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage
VIC1-NSW1 Export | V>>V_BTTT1MLSY_KT_AR | 1.4 (0) | Out = Brunswick to Thomastown #1 220kV and one Moorabool to Sydenham 500kV line, with KTS 220kV bus #1 & #2 tied and both TTS-KTS lines bypass KTS to WMTS, avoid O/L SMTS F2 txfmr on trip of ROTS A1 500/220kV txfmr, Radial Mode, YWPS1 on 500kV, Feedback | Outage
VIC1-NSW1 Export | VN_0950 | 1.3 (0) | Discretionary Vic to NSW transfer upper limit of 950 MW | Outage
VIC1-NSW1 Export | V::N_DDWO_SD | 1.2 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_MLSY_V1 | 1.2 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-CNUT_HB_15M | 1.2 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Murray to Lower Tumut (66) on trip of Murray to Upper Tumut (65) line, Feedback | Outage
VIC1-NSW1 Export | #R013811_001_RAMP_F | 1.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V4 | 1.1 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_2SVC_V3 | 1.1 (0) | Out = 2 SVCs at Rowville or South East, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_6A_R | 1.1 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL
VIC1-NSW1 Export | N::V_MNYS_2 | 1.0 (0) | Out= Marulan-Yass (4 or 5), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage
VIC1-NSW1 Export | V::N_HORC_V4 | 1.0 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_SD | 1.0 (0) | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_BAHO_V2 | 0.9 (0) | Out = Ballarat to Waubra to Horsham 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_VE | 0.9 (0) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
VIC1-NSW1 Export | V::N_MLTR_V4 | 0.9 (0.1) | Out = Moorabool to Tarrone (MLTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | #R013888_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014363_001_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | V::N_ESTN_HYSE_VD | 0.8 (0.3) | SA / ESTN separation between Heywood and South East Sub, avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, Basslink VIC to TAS, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | VN_1100 | 0.8 (0.9) | Discretionary Vic to NSW transfer upper limit of 1100 MW | Outage
VIC1-NSW1 Export | #R014994_019_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint V>>N-JNWO_RADIAL_1, Effective Date: 01/07/2016, Version: 1 | Outage
VIC1-NSW1 Export | N^^N_NIL_1 | 0.8 (0) | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL
VIC1-NSW1 Export | V::N_X_MLSM_EMTT_SD | 0.8 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | #R013997_001_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014883_005_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015058_015_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | V::N_DDWO_S2 | 0.7 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_0600 | 0.7 (0) | Discretionary Vic to NSW transfer upper limit of 600 MW | Outage
VIC1-NSW1 Export | #R013624_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013878_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014061_012_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014200_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | V::N_MLSY_V4 | 0.6 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_0900 | 0.6 (0) | Discretionary Vic to NSW transfer upper limit of 900 MW | Outage
VIC1-NSW1 Export | #R013618_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013904_001_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | N>>N-NIL__S | 0.5 (0) | Out = Nil, avoid overloading Mt Piper to Wallerawang (70) 330 kV line on trip of Mt Piper to Wallerawang (71) 330 kV line | NIL
VIC1-NSW1 Export | V::N_HYMO_V2 | 0.5 (0) | Out = Heywood to Mortlake (HYTS-MOPS) No.2 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLSY_Q1 | 0.5 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_X_MLSM_EMTT_V2 | 0.5 (0) | Out = one Moorabool to Sydenham to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HH | 0.5 (0) | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | #R013512_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013542_006_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>N_SMHTX_1, Effective Date: 21/12/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013579_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013590_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013592_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013607_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013613_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013647_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013666_024_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013700_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013776_022_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013781_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013918_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014037_013_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014173_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014184_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMB_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014252_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014313_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014602_004_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014672_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014692_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014729_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014729_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014796_026_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>N-JNWG_RADIAL_1, Effective Date: 01/07/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014878_023_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014921_005_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014921_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014923_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014964_003_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014964_003_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_SD, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014973_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015039_007_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015041_010_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V_MLSY_KTSBP_1AR, Effective Date: 12/08/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015060_014_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015060_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | V::N_HORC_SD | 0.4 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_MLMO_V2 | 0.4 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 0.4 (23.3) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
VIC1-NSW1 Export | VN_0650 | 0.4 (0) | Discretionary Vic to NSW transfer upper limit of 650 MW | Outage
VIC1-NSW1 Export | VN_0700 | 0.4 (0) | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage
VIC1-NSW1 Export | #R013515_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/10/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013544_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013544_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013557_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013568_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013590_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013592_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013593_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013596_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013649_024_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013667_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013700_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013730_026_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>N-JNWO_RADIAL_1, Effective Date: 19/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013738_026_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>N-JNWO_RADIAL_1, Effective Date: 19/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013830_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013904_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013939_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014266_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014463_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014560_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014665_014_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014680_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014692_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014728_009_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014858_030_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014864_030_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014878_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWO_SD, Effective Date: 16/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014880_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014903_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014915_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015002_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015028_016_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015031_016_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015058_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HYTR_Q4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | CA_SPS_46545836_01 | 0.3 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500 & APD POTLINES. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | N>>N-NIL_64 | 0.3 (0) | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
VIC1-NSW1 Export | V::N_DDWO_V4 | 0.3 (0) | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | #R013542_006_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>N_SMHTX_1, Effective Date: 21/12/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013559_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013559_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013567_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013578_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013596_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013663_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013778_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014037_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014061_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014099_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014184_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMB_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014221_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014252_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014463_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSM_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014680_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014728_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014789_009_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014789_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014867_015_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014879_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_S2, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014883_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014915_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_S2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014921_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014999_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015002_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_KGRC_S2, Effective Date: 02/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015012_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 11/10/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015028_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015031_016_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 16/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | V::N_HORC_V2 | 0.3 (0) | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLMO_V4 | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>BABE_DDGN_N-2 | 0.3 (0) | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
VIC1-NSW1 Export | V>>SML_NIL_8 | 0.3 (0.7) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
VIC1-NSW1 Export | VN_0750 | 0.3 (0) | Discretionary Vic to NSW transfer upper limit of 750 MW | Outage
VIC1-NSW1 Export | VN_0850 | 0.3 (0) | Discretionary Vic to NSW transfer upper limit of 850 MW | Outage
VIC1-NSW1 Export | #R013512_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013515_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/10/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013557_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013567_013_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013600_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013612_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013614_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013666_024_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWGVE_R, Effective Date: 01/07/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013667_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013776_022_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013997_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014103_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014241_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014241_010_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014363_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014477_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014477_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014602_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_MLSY_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014858_028_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014858_030_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014864_030_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014879_003_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014880_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_KTSY_V2, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014923_010_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V2, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014973_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014994_019_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>N-JNWO_RADIAL_1, Effective Date: 01/07/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014999_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HORC_V2, Effective Date: 03/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015002_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 02/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015035_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015039_007_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_KTSY_MLSM_ET_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | N>>N-NIL__B_15M | 0.2 (0) | Out= Nil, avoid O/L Upper Tumut to Canberra (01) using 15 mins rating on trip of Lower Tumut to Canberra (07) line, Feedback | NIL
VIC1-NSW1 Export | V::N_HYTR_S4 | 0.2 (0) | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Basslink VIC to TAS. Yallourn W Unit 1 on 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
VIC1-NSW1 Export | V>>SML_NIL_1 | 0.2 (2.3) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line | NIL
VIC1-NSW1 Export | V>>SML_NIL_CONT_7A | 0.2 (0) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Ballarat North to Buangor 66kV line for loss of the Arrarat to Horsham 220kV line | NIL
VIC1-NSW1 Export | VN_1200 | 0.2 (0) | Discretionary Vic to NSW transfer upper limit of 1200 MW | Outage
VIC1-NSW1 Export | #R013613_022_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDP_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013614_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013617_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013618_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013624_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 08/09/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013647_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/08/2015, Version: 1 | Outage
VIC1-NSW1 Export | #R013812_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013812_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 24/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013863_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013870_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013873_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_BTRT_2A_R, Effective Date: 05/04/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013888_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R013939_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_EPMB_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014167_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BAHO_S4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014167_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014221_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_X_2SVC_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014266_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014313_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014409_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2A_R, Effective Date: 23/03/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014484_011_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLTR_V1, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014499_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYMO_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014560_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLSY_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014570_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_MLMO_Q4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014570_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLMO_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014665_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014672_014_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V2, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014804_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYMO_Q1, Effective Date: 07/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014867_015_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMF2_V4, Effective Date: 08/04/2016, Version: 2 | Outage
VIC1-NSW1 Export | #R014870_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDWO_S2, Effective Date: 16/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014870_026_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>N-DDWO_RADIAL_1, Effective Date: 01/07/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014879_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_KTSY_SD, Effective Date: 08/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014903_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_KTSY_MLSM_ET_S2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014915_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014942_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V2, Effective Date: 28/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014964_005_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_X_MLSM_EMTT_V2, Effective Date: 17/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014980_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 02/12/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014980_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>N-JNWO_RADIAL_1, Effective Date: 01/07/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R014999_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORC_SD, Effective Date: 03/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015035_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BAHO_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | #R015058_015_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYTR_V4, Effective Date: 24/11/2016, Version: 1 | Outage
VIC1-NSW1 Export | N>>N-CNUT_HA | 0.1 (0) | Out = Upper Tumut -Canberra(01), avoid O/L Upper Tumut to Lower Tumut (64) on trip of Upper Tumut to Yass (2) line, Feedback | Outage
VIC1-NSW1 Export | N>>N-DTKV_8N | 0.1 (0) | Out = Dapto-KangarooValley(18), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage
VIC1-NSW1 Export | V::N_DDSM_S2 | 0.1 (0) | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_Q2 | 0.1 (0) | Out = Hazelwood to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, QLD accelerates. Yallourn W G1 on 500 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_MLSY_V2 | 0.1 (0) | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-MSUT_2 | 0.1 (0) | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-MSUT_4 | 0.1 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | V>>SML_NIL_7C | 0.1 (0) | Out = Nil, avoid O/L Ararat to Stawell 66kV line for loss of the Ararat to Horsham 220kV line, swamped if BATS-HOTS 66 kV tie opened, or with BGR tie splitting scheme in service | NIL
VIC1-NSW1 Export | V>>SML_NIL_CONT_7C | 0.1 (0) | Out = Nil, 66 kV line limited cyclic ratings not available, avoid O/L Arrarat to Stawell 66kV line for loss of the Arrarat to Horsham 220kV line | NIL
VIC1-NSW1 Export | V>>V_KTSY_P | 0.1 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of South Morang to Keilor 500kV line, 3/5 parallel mode, feedback | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 81.8 (211.7) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
VIC1-NSW1 Import | N^^V_MSDD2 | 9.1 (0) | Out = Dederang to Murray 330 kV line, avoid voltage collapse for trip of the remaining Dederang to Murray 330 kV line | Outage
VIC1-NSW1 Import | V>>V-JNWG_RADIAL_1A | 6.8 (0) | Outage = Jindera to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload one Murray to Dederang 330kV line for loss of the parallel 330kV line, 15 min line ratings; Feedback | Outage
VIC1-NSW1 Import | N^^V_DDSM1 | 3.9 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 3.6 (10.1) | Negative Residue Management constraint equation for NSW to VIC flow | NIL
VIC1-NSW1 Import | N^^V_DDSM2 | 3.3 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse for loss of remaining Dederang to South Morang 330 kV line | Outage
VIC1-NSW1 Import | N^^V_SMTXH1_1 | 3.3 (0) | Out = South Morang H1 or H2 500/330 kV txfmr, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V_BTRT_SMF2_KT_DR | 2.2 (0) | Out=Brunswick-Richmond 220kV cable and South Morang F2 500/330kV TX, with KTS 220kV bus #1 & #2 tied and both KTS-TTS lines bypass KTS to WMTS, avoid O/L Rowville-Thomastown 220kV line on trip of Rowville A1 500/220kV TX, Radial, YWPS1 on 500kV, Feedback | Outage
VIC1-NSW1 Import | N>>V_DBUSS_1 | 1.8 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line | Outage
VIC1-NSW1 Import | V>>V_NIL_1B | 1.8 (0) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line | NIL
VIC1-NSW1 Import | V>>V_NIL_1A | 1.2 (0) | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
VIC1-NSW1 Import | N^^V_EPMB_1 | 0.9 (24.3) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>DDSH_DDGN_N-2 | 0.7 (0) | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
VIC1-NSW1 Import | #R014304_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^^V_MSDD2, Effective Date: 07/08/2015, Version: 1 | Outage
VIC1-NSW1 Import | V>>SML_BABE_4 | 0.1 (0) | Out = Ballarat to Bendigo 220 kV line, avoid O/L of the Darlington Point to Balranald to Buronga (X5/1 and X5/3) 220 kV line on trip of the Shepparton to Fosterville to Bendigo 220 kV line, feedback | Outage
VIC1-NSW1 Import | V>>V_NIL_4A | 0.1 (0) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. | NIL

## Outages 2016
Constraint Set ID | 2016 Days (2015 Days) | Description
N-MBTE_1 | 258.1 (359.8) | One Directlink cable
N-X_MBTE_2 | 122.3 (251.4) | Two Directlink cables
I-BL_ZERO | 100.9 (0.6) | Limit Basslink to zero in either direction
N-CHKK_96H | 69.1 (1.9) | Coffs Harbour to Koolkhan (96H) 132 kV line
V-BTRT_R | 59.9 (0) | Out= Brunswick to Richmond 220kV line, Radial Mode
N-BAMB_132_OPEN | 54.9 (1.6) | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path.
S-PA_VC1 | 42.3 (0) | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
N-X_MBTE_3 | 37.0 (55.1) | All three Directlink cables
F-T-BBGT | 27.6 (6.3) | Out=One Bell Bay - Georgetown 110 kV line, all four Bell Bay GTs on remaining 110 kV line, FCAS requirements
F-I_ML_APD | 23.1 (15.0) | Out=Nil, Dymanic FCAS for APD Load Event
I-ML_ZERO | 20.3 (6.6) | Limit Murraylink to zero in either direction
T-GTSH | 14.8 (0.1) | Out = One George Town to Sheffield 220kV line
V-ROTX_R | 14.7 (1.8) | Outage = Rowville 500/220kV (A) transformer, Radial
F-ESTN_ISLE | 13.4 (0.0) | Eastern separation between Heywood and South East (HYTS - SESS) - FCAS Requirements
I-SV_000 | 11.2 (0) | SA to Victoria on VicSA upper transfer limit of 0 MW
V-HY_500BUS | 10.6 (0) | Out = Heywood (HYTS) No. 1 or No. 2 500 kV bus.
S-TB_275KV_W_BUS | 10.5 (0) | Out= Tailembend 275kV West Bus(i.e. CBs 6596 & 6536 OPEN, and South East-Tailembend #1 275 line O/S) (NOTE: ONLY INVOKE prior to Decom. of SG-KH #1 132kV & KH-TB #1 132kV lines & prior to Com. of BlackRange Series Caps)
S-STTX | 8.9 (0.5) | Out = Snowtown 132/33kV TX or Snowtown CB4593 or Snowtown CB6265
I-SVML_000 | 8.7 (0) | SA to Vic on ML upper transfer limit of 0 MW
I-HYSE | 8.3 (28.3) | One Heywood to South East 275 kV line
V-DDMS | 7.7 (0.8) | One Dederang to Murray (67 or 68) 330 kV line
N-LSDU_9U6 | 7.1 (2.3) | Lismore to Dunoon 132 kV line
S-TBSE_1 | 6.5 (0) | Out - one South East-Tailembend 275kV line (ONLY INVOKE Post decommissioning of Snuggery-Keith 132kV line and Keith-Tailembend 132kV line)
S-PA_EAST_BUS_R | 6.4 (0) | Out= Para 275kV East bus Right Section (i.e.either SVC2 or SVC1,Tx2,CB6509, CB6512,CB6543, CB6600 O/S), (Note: with both Black Range Series caps I/S)
S-PA_WEST_BUS_R | 6.1 (4.9) | Para 275 kV West Bus Right Section
I-SV_000_DYN | 6.1 (0) | SA to Victoria on VicSA upper transfer limit of 0 MW, dynamic headroom
T-TU_MB_NN1 | 5.1 (2.4) | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line
N-NYNGANSF_051 | 4.7 (0) | Nyngan Solar Farm upper limit of 51 MW (50% capacity)
V-HWSM | 3.4 (2.9) | Hazelwood to South Morang 500 kV line
V-HYMO | 2.7 (1.9) | Heywood to Mortlake No.2 500 kV line
V-MTMERCER_ZERO | 2.2 (7.2) | Mt Mercer Windfarm upper limit of 0 MW
V-MLTR | 2.1 (0.3) | Moorabool to Tarrone No.1 500 kV line
NSA-Q_BARCALDN | 1.9 (0.4) | Clermont to Lilyvale (7153) 132 kV line, Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine This NSA constraint set is included as it is only invoked under outage conditions
I-CTRL_ISSUE_TE | 1.8 (4.9) | DC Link Control Issue Constraint for Terranora
N-ARTW_86 | 1.5 (3.5) | Armidale to Tamworth (86) 330 kV line
N-MUTW_88 | 1.4 (1.1) | Out = Muswellbrook to Tamworth (88) line
F-N-MUTW_88 | 1.4 (1.1) | Muswellbrook to Tamworth (88) 330 kV line
N-ARTW_85 | 1.4 (0.8) | Armidale to Tamworth (85) 330 kV line
N-NYNGANSF_010 | 1.2 (0) | Nyngan Solar Farm upper limit of 10 MW
I-MSUT | 1.1 (2.2) | Murray to Upper Tumut (65) 330 kV line
V-MLMO | 1.0 (2.5) | Moorabool to Mortlake 500 kV line
N-X_96H_LS_SVC | 1.0 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore SVC O/S or in reactive power control mode
N-RGSW_38 | 0.9 (13.2) | Out= Regentville - Sydney West (38)
V-HWCB4 | 0.9 (0.5) | Hazelwood to Cranbourne No.4 500 kV line
V-HWRO3 | 0.8 (0.2) | Hazelwood to Rowville No.3 500 kV line
N-X_96H_LSTX | 0.8 (0) | Out= Coffs Harbour to Koolkhan (96H) 132kV line and Lismore 330/132kV Tx
V-HYTR | 0.7 (1.0) | Heywood to Tarrone 500 kV line
F-SA_ESTN_ISLE_REG | 0.6 (0.0) | SA / Eastern separation between Heywood and South East (HYTS - SESS) - Regulation FCAS Requirements
N-LPSW30+RGSW38 | 0.5 (0.5) | Out= Liverpool-SydWest(30) + Regentville-SydWest(38) 330kV lines
N-X_RGSW_SSWW | 0.5 (0.6) | Out= Regentville to Sydney West (38) and Sydney South to Wallerawang (76) 330kV lines
N-TW_330_BUS1 | 0.5 (0.2) | Out= Tamworth No.1 330kV bus
N-X_30+38+71+ERTX | 0.5 (0) | Out= Liverpool-SydWest(30) & Regentville-SydWest(38) & Mt Piper to Wallerawang (70/71) 330kV line & Eraring 500/330kV Tie Tx
N-X_MMSW+RGSW | 0.3 (0) | Out= Munmorah-Sydney West (26) and Regentville-Sydney West (38) 330kV lines
S-X_PLN_02 | 0.3 (0) | Yadnarie to Port Lincoln line
N-KKLS_967 | 0.3 (1.2) | Koolkhan to Lismore (967) 132 kV line
V-X_HWSM_ROTX_R | 0.2 (0) | Out = Hazelwood to South Morang 500kV line and Rowville 500/220kV A1 or A2 Transformer, Radial
F-SA_ISLE | 0.2 (0.0) | SA separation between Heywood and South East - FCAS Requirements
V-MLSY_R | 0.0 (2.4) | Out = Moorabool to Sydenham 500kV line, Radial Mode, EMTT scheme armed or other credible VIC-SA separation risk

## Outage stats
TNSP | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2012 | 15 | 23 | 2 | 1
2013 | 10 | 7 | 0 | 1
2014 | 12 | 27 | 9 | 0
2015 | 27 | 60 | 8 | 2
2016 | 24 | 36 | 7 | 1
ElectraNet 2012 | 240 | 457 | 582 | 424
2013 | 200 | 435 | 874 | 136
2014 | 93 | 311 | 571 | 108
2015 | 447 | 918 | 1003 | 231
2016 | 110 | 266 | 309 | 176
Essential E 2012 | 15 | 83 | 177 | 0
2013 | 19 | 41 | 81 | 0
2014 | 6 | 39 | 82 | 4
2015 | 0 | 17 | 59 | 0
2016 | 3 | 26 | 40 | 0
Powerlink 2012 | 317 | 885 | 1219 | 26
2013 | 301 | 812 | 1183 | 96
2014 | 350 | 1143 | 1993 | 15
2015 | 1076 | 3173 | 6415 | 100
2016 | 273 | 885 | 2265 | 17
AusNet 2012 | 234 | 972 | 738 | 36
2013 | 146 | 895 | 502 | 56
2014 | 134 | 636 | 991 | 614
2015 | 161 | 678 | 1290 | 764
2016 | 170 | 876 | 695 | 97
TasNetworks 2012 | 57 | 279 | 250 | 83
2013 | 111 | 550 | 496 | 281
2014 | 179 | 778 | 473 | 38
2015 | 197 | 1119 | 918 | 86
2016 | 19 | 88 | 166 | 32
TransGrid 2012 | 198 | 533 | 900 | 629
2013 | 251 | 452 | 849 | 590
2014 | 33 | 125 | 130 | 73
2015 | 128 | 629 | 993 | 302
2016 | 116 | 472 | 973 | 506

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.