## Tasmania Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer at
http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Tasmania Summary
Changes since last update
Tamar Valley CCGT: Hydro Tasmania advises that the Tamar Valley CCGT (208 MW) has returned to service in summer 2016-17. It will be withdrawn after summer 2016-17, but available for operation with less than 3 months' notice.
Generation withdrawals
Withdrawn
None to report.
Announced withdrawals (i.e. Mothballed, Seasonal Shut down etc.)
Tamar Valley CCGT: Hydro Tasmania advises that the Tamar Valley CCGT (208 MW) will be withdrawn after summer 2016-17, but available for operation with less than 3 months' notice.
Committed projects
Coal, CCGT, OCGT, Gas other, Water, Biomass, Geo-thermal, Other : None to report.
Proposed projects
Please refer to information presented in the worksheet titled 'New Developments'.
Plant limitations
Bastyan Power Station: Hydro-Electric Corporation advises that Bastyan's available capacity will be (zero) 0 MW during summer 2020-21.
Catagunyah/Liapootah/Wayatinah Power Station: Hydro-Electric Corporation advises that Catagunyah/Liapootah/Wayatinah Power Stations will undergo the following outages:
· Liapootah Unit 1 will be unavailable during:
- summer 2016–17
· Liapootah Unit 2 will be unavailable during:
- summer 2017–18
· Liapootah Unit 3 will be unavailable during:
- summer 2018–19
· Wayatinah Unit 1 will be unavailable during:
- summer 2016–17
· Wayatinah Unit 2 will be unavailable during:
- summer 2017–18
· Wayatinah Unit 3 will be unavailable during:
- summer 2018–19
· Catagunya Unit 1 will be unavailable during:
- summer 2018–19
· Catagunya Unit 2 will be unavailable during:
- summer 2017–18
· Catagunya Unit 3 will be unavailable during:
- summer 2018–19
Devils Gate Power Station: Hydro-Electric Corporation advises that Devils Gate’s available capacity will be (zero) 0 MW during summer 2017-18 and winter 2018.
Gordon Power Station: Hydro-Electric Corporation advises that Gordon's available capacity will reduced to 354 MW (-42) MW during summer and winter due to lower storage levels. Also, the station will undergo the following outages:
· Gordon Unit 1 will be unavailable during:
- winter 2018
· Gordon Unit 2 will be unavailable during:
- winter 2019
· Gordon Unit 3 will be unavailable during:
- winter 2019
John Butters Station: Hydro-Electric Corporation advises that John Butters' available capacity will be (zero) 0 MW during summer 2024-25 and winter 2025.
Lake Echo Power Station: Hydro-Electric Corporation advises that Lake Echo's available capacity will be (zero) 0 MW during winter 2019 and 2020.
Lemonthyme/Wilmot Power Station: Hydro-Electric Corporation advises that Lemonthyme/Wilmot's available capacity will be 54 MW during summer 2018-19 and 32 MW during summer 2019-20.
Mackintosh Power Station: Hydro-Electric Corporation advises that Mackintosh's available capacity will be (zero) 0 MW during summer 2022-23.
Reece Power Station: Hydro-Electric Corporation advises that Reece's available capacity will be 116 MW during summer 2016-17 and 2023-24 due to an outage.
Tarraleah Power Station: Hydro-Electric Corporation advises that Tarraleah’s available capacity will be:
• 75 MW from winter 2022 to summer 2024-25 due to outages of Units 1, 2 and 3.
Trevallyn Power Station: Hydro-Electric Corporation advises that Trevallyn’s available capacity will be:
• 81.9 MW during summer 2019–20 due to outages of Unit 1.
• 0 MW during summer 2020–21 due to outages
Tungatinah Power Station: Hydro-Electric Corporation advises that Tungatinah’s available capacity will be:
• 104.4 MW during summer 2019-20 due to outages
• 104.4 MW during summer 2021–22 due to outages
Tribute: Hydro-Electric Corporation advises that Tribute's available capacity will be (zero) 0 MW during summer 2025-26.
Tasmania existing and potential new developments by generation type (MW)
Status | Coal | CCGT | OCGT | Gas other | Solar* | Wind | Water | Biomass | Other | Total
Existing | 0 | 208 | 178 | 0 | 0 | 308 | 2280.8 | 4.9 | 0 | 2979.7
Announced Withdrawal | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208
Existing less Announced Withdrawal | 0 | 0 | 178 | 0 | 0 | 308 | 2280.8 | 4.9 | 0 | 2771.7
Committed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 329
Withdrawn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note: Existing includes Announced Withdrawal
* Excludes rooftop PV installations.

## Change Log
Tasmania Change Log
Lists all key updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication date: | 2012-12-20
Tungatinah (Upgrade): Hydro-Electric Corporation advises the upgrade to Unit 1 is committed and scheduled to return to service in December 2012.
Publication date: | 2013-02-22
Poatina Power Station: Hydro Tasmania advises that the Poatina plant has revised its available capacity from 300 MW to 342 MW (+42 MW) in summer and winter, based on operating experience.
Musselroe Wind Farm: Hydro Tasmania Wind Operations Pty Ltd advises that Musselroe (168 MW) is now a committed project. Construction is expected be completed around June 2013.
Publication date: | 2013-06-30
Tungatinah (Upgrade): Hydro-Electric Corporation advises the upgrade to Unit 1 was completed and returned back to service on February 2013. The upgrade was a revamp of the unit where some efficiency gains are expected.
Tungatinah (Upgrade): Hydro-Electric Corporation advises an upgrade to Unit 2, a revamp of the existing unit where some efficiency gains are expected. The upgrade to be completed in November 2013.
Publication date: | 2013-11-15
Musselroe Wind Farm: Hydro Tasmania Wind Operations Pty Ltd advises that Musselroe (168 MW) project was completed in June 2013.
TasWind (King Island): Hydro Tasmania advises that the TasWind (King Island) project is publically anounced.
Publication date: | 2014-12-10
Tamar Valley OCGT (Bell Bay Three & TVPP104): Hydro-Electric Corporation advises that TVPP104 available capacity will be (zero) 0 MW during summer 2015-16, specifically between 4/9/2015 and 4/3/2016 due to a major outage.
Cethana Power Station: Hydro-Electric Corporation advises that Cethana’s available capacity will be (zero) 0 MW during summer 2014-15, specifically between 5/1/2015 and 21/9/2015 due to a major refurbishment project.
Tamar Valley Combined Cycle: AETV advises that Tamar Valley Combined Cycle's available capacity will be (zero) 0 MW during winter 2015 and winter 2016 due to winter layover (dry storage) specifically between 1/1/2015 and 19/4/2015 and then 24/4/2015 until 18/4/2016 and then again between 22/4/2016 and 31/12/2016.31/12/2015 and then again between 1/4/2016 and 31/12/2016.
Tarraleah Power Station: Hydro-Electric Corporation advises that Tarraleah’s available capacity will be:
• 45 MW during summer 2015-16 due to outages of Units 4,5 and 6, specifically between 7/9/2015 and 4/12/2015 due to a major refurbishment project.
• 45 MW during summer 2015-16 due to outages of Units 1,2 and 3, specifically between 1/2/2016 and 30/4/2016 due to a major refurbishment project.
Tungatinah Power Station: Hydro-Electric Corporation advises that Tungatinah’s available capacity will be:
• 104.4 MW during summer 2019–20 due to outages of Unit 3.
• 78.3 MW during summer 2014-15 due to outages of Unit 4 and Unit 5.
• 104.4 MW during summer 2015-16 due to outages of Unit 4, specifically between 30/11/2015-17/6/2016 due to a major refurbishment project.
Publication date: | 2015-08-13
Tamar Valley CCGT: Hydro Tasmania have advised that Tamar Valley CCGT (208 MW) unit is currently in dry lay up. On 13 August 2015, the Tasmanian Government gave approval for Hydro Tasmania to decommission and sell the combined cycle gas turbine.
Tamar Valley Peaking: Hydro Tasmania have advised that Tamar Valley Peaking (58 MW) unit is currently withdrawn and is to return back to service in June 2016.
Bell Bay Three Power Station: Hydro Tasmania have advised that Bell Bay Three Power Stations available capacity will be 75 MW (-45 MW) for Summer 2015-16, 2016-17 and Winter 2016, 2017. Hydro Tasmania also advised the power station is to be withdrawn from service from 1 January 2018 and onwards.
Publication date: | 2016-03-03
Tamar Valley CCGT: Hydro Tasmania have advised that Tamar Valley CCGT (208 MW) unit has been recommissioned and running since 19 January 2016.
Tamar Valley OCGT: Hydro Tasmania have advised that Tamar Valley Peaking (58 MW) unit is currently withdrawn and is to return back to service in April 2016.
Bell Bay Three Power Station: Hydro Tasmania have advised that Bell Bay Three Power Stations available capacity will be 105 MW (15 MW) for Summer 2015-16, 2016-17 and Winter 2016, 2017. Hydro Tasmania also advised the power station is to be withdrawn from service from 1 January 2018 and onwards.
Publication date: | 2016-04-15
Tamar Valley CCGT: Hydro Tasmania have advised that Tamar Valley CCGT (208 MW) unit has been recommissioned and running since 19 January 2016.
Tamar Valley OCGT: Hydro Tasmania have advised that Tamar Valley Peaking (58 MW) unit is currently withdrawn and is to return back to service in April 2016.
Bell Bay Three Power Station: Hydro Tasmania have advised that Bell Bay Three Power Stations available capacity will be 105 MW (15 MW) for Summer 2015-16, 2016-17 and Winter 2016, 2017. Hydro Tasmania also advised the power station is to be withdrawn from service from 1 January 2018 and onwards.
Publication date: | 2016-08-11
Bell Bay Power Station: Hydro Tasmania advises that Bell Bay Power Station (105 MW) will no longer be withdrawn from service from 1 January 2018 onwards.
Tamar Valley CCGT : Hydro Tasmania advises that Tamar Valley CCGT (208 MW) has been withdrawn from service since May 2016.
Publication date: | 2016-11-18
Tamar Valley CCGT: Hydro Tasmania advises that the Tamar Valley CCGT (208 MW) is available for operation with less than 3 months' notice and will next return to service in summer 2016-17.
Publication date: | 2017-02-27
Tamar Valley CCGT: Hydro Tasmania advises that the Tamar Valley CCGT (208 MW) has returned to service in summer 2016-17. It will be withdrawn after summer 2016-17, but available for operation with less than 3 months' notice.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Number and Nameplate Capacity (MW) | Installed Capacity (MW) | Technology Type | Fuel Type | Dispatch Type | Service Status
Bastyan | Hydro-Electric Corporation | 1 x 79.9 | 79.9 | Hydro - Gravity | Water | S | In Service
Bell Bay Three | AETV Pty Ltd | 3 x 40 | 120 | OCGT | Natural Gas Pipeline | S | In Service
Catagunya / Liapootah / Wayatinah | Hydro-Electric Corporation | 3 x 12.8 2 x 24 3 x 27.9 | 170.1 | Hydro - Gravity | Water | S | In Service
Cethana | Hydro-Electric Corporation | 1 x 85 | 85 | Hydro - Gravity | Water | S | In Service
Devils Gate | Hydro-Electric Corporation | 1 x 60 | 60 | Hydro - Gravity | Water | S | In Service
Fisher | Hydro-Electric Corporation | 1 x 43.2 | 43.2 | Hydro - Gravity | Water | S | In Service
Gordon | Hydro-Electric Corporation | 3 x 144 | 432 | Hydro - Gravity | Water | S | In Service
John Butters | Hydro-Electric Corporation | 1 x 144 | 144 | Hydro - Gravity | Water | S | In Service
Lake Echo | Hydro-Electric Corporation | 1 x 32.4 | 32.4 | Hydro - Gravity | Water | S | In Service
Lemonthyme / Wilmot | Hydro-Electric Corporation | 1 x 30.6 1 x 51 | 81.6 | Hydro - Gravity | Water | S | In Service
Mackintosh | Hydro-Electric Corporation | 1 x 79.9 | 79.9 | Hydro - Gravity | Water | S | In Service
Meadowbank | Hydro-Electric Corporation | 1 x 40 | 40 | Hydro - Gravity | Water | S | In Service
Musselroe | Woolnorth Wind Farm Holding Pty Ltd | 56 x 3 | 168 | Wind - Onshore | Wind | SS | In Service
Poatina | Hydro-Electric Corporation | 6 x 50 | 300 | Hydro - Gravity | Water | S | In Service
Reece | Hydro-Electric Corporation | 2 x 115.6 | 231.2 | Hydro - Gravity | Water | S | In Service
Tamar Valley Combined Cycle | AETV Pty Ltd | 1 x 140 1 x 68 | 208 | CCGT | Natural Gas Pipeline | S | Announced Withdrawal
Tamar Valley Peaking | AETV Pty Ltd | 1 x 58 | 58 | OCGT | Natural Gas Pipeline | S | In Service
Tarraleah | Hydro-Electric Corporation | 6 x 15 | 90 | Hydro - Gravity | Water | S | In Service
Trevallyn | Hydro-Electric Corporation | 2 x 20 2 x 26.5 | 93 | Hydro - Gravity | Water | S | In Service
Tribute | Hydro-Electric Corporation | 1 x 82.8 | 82.8 | Hydro - Gravity | Water | S | In Service
Tungatinah | Hydro-Electric Corporation | 5 x 25 | 125 | Hydro - Gravity | Water | S | In Service
Total |  |  | 2724.1

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation
Power Station | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | Dispatch Type
Bastyan | 81 | 81 | 81 | 81 | 81 | 0 | 81 | 81 | 81 | 81 | S
Bell Bay Three | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Catagunya / Liapootah / Wayatinah | 134.2 | 134.2 | 110.2 | 153.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | S
Cethana | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | S
Devils Gate | 63 | 0 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Fisher | 0 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | S
Gordon | 354 | 354 | 236 | 236 | 236 | 354 | 354 | 354 | 354 | 354 | S
John Butters | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 0 | 140 | S
Lake Echo | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | S
Lemonthyme / Wilmot | 86 | 54 | 86 | 32 | 54 | 86 | 86 | 86 | 86 | 86 | S
Mackintosh | 81 | 81 | 81 | 81 | 81 | 81 | 0 | 81 | 81 | 81 | S
Meadowbank | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | S
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS
Poatina | 342 | 342 | 342 | 342 | 285 | 285 | 285 | 285 | 285 | 342 | S
Reece | 116 | 232 | 232 | 232 | 232 | 232 | 232 | 116 | 232 | 116 | S
Tamar Valley Combined Cycle | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 75 | 75 | 90 | S
Trevallyn | 102.8 | 102.8 | 102.8 | 81.9 | 0 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | S
Tungatinah | 130.5 | 130.5 | 130.5 | 104.4 | 130.5 | 104.4 | 130.5 | 130.5 | 130.5 | 130.5 | S
Total | 2498.5 | 2357.5 | 2310.5 | 2252.6 | 2185.8 | 2236.5 | 2342.6 | 2307.6 | 2283.6 | 2291.6
The table above lists the latest Summer capacities for Tasmanian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 8.5% of the installed capacity during summer, and 4.9% during winter, based on AEMO's analysis of historical wind output over summer 2011-12 to 2015-16, and winter 2011 - 2015.
The two tables below have been included to better represent the supply availability in Tasmania, by taking into account the firm contribution by semi-scheduled generation. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the summer period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation
Power Station | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | Dispatch Type
Bastyan | 81 | 81 | 81 | 81 | 81 | 0 | 81 | 81 | 81 | 81 | S
Bell Bay Three | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Catagunya / Liapootah / Wayatinah | 134.2 | 134.2 | 110.2 | 153.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | S
Cethana | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | S
Devils Gate | 63 | 0 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Fisher | 0 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | S
Gordon | 354 | 354 | 236 | 236 | 236 | 354 | 354 | 354 | 354 | 354 | S
John Butters | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 0 | 140 | S
Lake Echo | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | S
Lemonthyme / Wilmot | 86 | 54 | 86 | 32 | 54 | 86 | 86 | 86 | 86 | 86 | S
Mackintosh | 81 | 81 | 81 | 81 | 81 | 81 | 0 | 81 | 81 | 81 | S
Meadowbank | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | S
Poatina | 342 | 342 | 342 | 342 | 285 | 285 | 285 | 285 | 285 | 342 | S
Reece | 116 | 232 | 232 | 232 | 232 | 232 | 232 | 116 | 232 | 116 | S
Tamar Valley Combined Cycle | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 75 | 75 | 90 | S
Trevallyn | 102.8 | 102.8 | 102.8 | 81.9 | 0 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | S
Tungatinah | 130.5 | 130.5 | 130.5 | 104.4 | 130.5 | 104.4 | 130.5 | 130.5 | 130.5 | 130.5 | S
Firm Wind Capacity | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | SS
Total | 2344.78 | 2203.78 | 2156.78 | 2098.88 | 2032.08 | 2082.78 | 2188.88 | 2153.88 | 2129.88 | 2137.88
Summer aggregate available semi-scheduled generation
Power Station | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | Dispatch Type
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS
Total (Wind) | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation
Power Station | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Dispatch Type
Bastyan | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | S
Bell Bay Three | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Catagunya / Liapootah / Wayatinah | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | S
Cethana | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | S
Devils Gate | 63 | 0 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Fisher | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | S
Gordon | 354 | 354 | 354 | 354 | 354 | 354 | 354 | 354 | 354 | 354 | S
John Butters | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 0 | 140 | S
Lake Echo | 30 | 30 | 0 | 0 | 30 | 30 | 30 | 0 | 30 | 30 | S
Lemonthyme / Wilmot | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | S
Mackintosh | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | S
Meadowbank | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | S
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS
Poatina | 342 | 342 | 342 | 342 | 342 | 342 | 285 | 342 | 342 | 342 | S
Reece | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | S
Tamar Valley Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 90 | 90 | 90 | 90 | 90 | 75 | 75 | 75 | 90 | 90 | S
Trevallyn | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | S
Tungatinah | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | S
Total | 2495.6 | 2432.6 | 2465.6 | 2465.6 | 2495.6 | 2480.6 | 2423.6 | 2450.6 | 2355.6 | 2495.6
The table above lists the latest Winter capacities for Tasmanian generation. Winter conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. These figures are 8.5% of the installed capacity during summer, and 4.9% during winter, based on AEMO's analysis of historical wind output over summer 2011-12 to 2015-16, and winter 2011 - 2015.
The two tables below have been included to better represent the supply availability in Tasmania, by taking into account the firm contribution by semi-scheduled generation. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm semi-scheduled generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled generation for the winter period. The total refers to the maximum amount that can be generated from the semi-scheduled generation at the winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation
Power Station | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Dispatch Type
Bastyan | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | S
Bell Bay Three | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Catagunya / Liapootah / Wayatinah | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | 177.3 | S
Cethana | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | S
Devils Gate | 63 | 0 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Fisher | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | S
Gordon | 354 | 354 | 354 | 354 | 354 | 354 | 354 | 354 | 354 | 354 | S
John Butters | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 0 | 140 | S
Lake Echo | 30 | 30 | 0 | 0 | 30 | 30 | 30 | 0 | 30 | 30 | S
Lemonthyme / Wilmot | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | S
Mackintosh | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | S
Meadowbank | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | S
Poatina | 342 | 342 | 342 | 342 | 342 | 342 | 285 | 342 | 342 | 342 | S
Reece | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | S
Tamar Valley Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 90 | 90 | 90 | 90 | 90 | 75 | 75 | 75 | 90 | 90 | S
Trevallyn | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | S
Tungatinah | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | S
Firm Wind Capacity | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | SS
Total | 2335.832 | 2272.832 | 2305.832 | 2305.832 | 2335.832 | 2320.832 | 2263.832 | 2290.832 | 2195.832 | 2335.832
Winter aggregate available semi-scheduled generation
Power Station | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Dispatch Type
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS
Total (Wind) | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168

## Existing NS Generation
Existing non-scheduled generation
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type | Service Status
Butlers Gorge | Hydro-Electric Corporation | 14.4 | Hydro - Gravity | Water | In service
Cluny | Hydro-Electric Corporation | 17 | Hydro - Gravity | Water | In service
Glenorchy | AGL | 1.69 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Hobart | AGL | 1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Lake Margaret | Hydro-Electric Corporation | 8.4 | Hydro - Gravity | Water | In service
Lower Lake Margaret | Hydro-Electric Corporation | 3.2 | Hydro - Gravity | Water | In service
Paloona | Hydro-Electric Corporation | 28 | Hydro - Gravity | Water | In service
Remount | LMS Energy Pty Ltd | 2.246 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In service
Repulse | Hydro-Electric Corporation | 28 | Hydro - Gravity | Water | In service
Rowallan | Hydro-Electric Corporation | 10.5 | Hydro - Gravity | Water | In service
Tods Corner | Hydro-Electric Corporation | 1.2 | Pump Storage | Water | In service
Woolnorth Studland Bay / Bluff Point | Woolnorth Wind Farm Holding Pty Ltd | 140 | Wind - Onshore | Wind | In service
Total |  | 255.636

## New Developments
Projects under development
Project | Owner | Unit ID | Technology Type | Fuel Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Full Commercial Use Date
Cattle Hill Wind Farm | Cattle Hill Wind Farm Pty Ltd | Unit 1-68 | Wind - Onshore | Wind | [5 empty] | Pub An | 200 | SS | TBA
Granville Harbour Wind Farm | Westcoast Wind Pty Ltd | 1-33 | Wind - Onshore | Wind | [5 empty] | Pub An | 99 | SS | TBA
Low Head Wind Farm | Low Head Wind Farm Pty Ltd | Units 1-10 | Wind - Onshore | Wind | [5 empty] | Pub An | 30 | NS | TBA
Note: if nameplate capacity is provided as a range the maximum will be used when summarising the data.

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as semi-scheduled or non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as scheduled or non-scheduled. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW, unless AEMO approves its classification as scheduled or semi-scheduled.
Generating systems greater than 30 MW must be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating of less than 5 MW may be exempted by AEMO if its generation is purchased entirely by the local retail or a customer at the generator's connection point or the generator is classified as a market generating unit by a market small generation aggregator. A generating unit with a nameplate rating between 5 MW and 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.