## Index
National Transmission Network Development Plan (NTNDP)
Electronic Material – Consolidated summary 2012 Annual Planning Report (APR) augmentations
This supplement provides:
* A consolidated summary of the augmentations proposed by each JPB in their 2012 APRs and how they relate to the NTNDP
Please note that the data format may need to be adjusted in order to view the data to the level of fidelity required. For example, you may need to format the cell to a more appropriate number of decimal places in some cases as desired.
Index Table
Tab Name | Content Description
Powerlink 2012 APR Projects | List of projects from the 2012 Powerlink APR1
TransGrid 2012 APR Projects | List of projects from the 2012 TransGrid APR2
AEMO 2012 APR Projects | List of projects from the 2012 AEMO Victorian APR3
ElectraNet 2012 APR Projects | List of projects from the 2012 ElectraNet APR4
Transend 2012 APR Projects | List of projects from the 2012 Transend APR5
1 | Powerlink. Available http://www.powerlink.com.au/About_Powerlink/Publications/Annual_Planning_Reports/Documents/2012/Annual_Planning_Report_2012_(complete_report).aspx
2 | TransGrid. Available http://www.transgrid.com.au/network/np/Documents/TRAN_219219_Annual_Planning_Report_2012_FA_web.pdf
3 | AEMO. Available http://www.aemo.com.au/~/media/Files/Other/planning/2012_Victorian_Annual_Planning_Report.ashx
4 | ElectraNet. Available http://www.electranet.com.au/assets/Uploads/2012APR.pdf
5 | Transend. Available http://www.transend.com.au/download/D12-24505

## Powerlink 2012 APR Projects
2012 APR Reference | Transmission Development | Limitation Addressed | 2012 APR Project Status | 2012 APR Anticipated Timing | 2012 APR Indicative Cost ($ million) | 2011 APR Reference | 2012 NTNDP
Section 5.2.1 | Install a 20 MVAr 132 kV capacitor bank at Turkinje | Capacitive compensation to meet increasing reactive demand in far north Queensland | Committed | Summer 2012/13 | Not specified in APR | Section 4.5.1 | Outside the scope of the 2012 NTNDP
Section 5.2.2 | Build new Strathmore-Bowen North 132 kV line | Voltage and thermal limitations in the Bowen area | Proposed | 2015/16 | 12 - 15 | Section 4.5.3 | Outside the scope of the 2012 NTNDP
Section 5.2.2 | Build second Stanwell-Broadsound 275 kV line | Increase of the central Queensland to North Queensland limit to accommodate new developments in north Queensland | Proposed | 2014/15 | 45 | Section 4.5.3 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 5.2.2 | Install new Pioneer Valley 132 kV capacitor bank | Voltage control in Proserpine area | Proposed | Summer 2015/16 | 2 - 4 | Did not appear in 2011 APR | Outside the scope of the 2012 NTNDP
Section 5.2.2 | Install new Pioneer Valley 100 MVA 132/66 kV transformer to replace existing 40 MVA 132/66 kV transformer | Supply to the Pioneer Valley area | Committed | Summer 2013/14 | Not specified in APR | Section 3.2 | Outside the scope of the 2012 NTNDP
Section 5.2.2 | Install new Mackay 132 kV capacitor bank | Voltage control in Proserpine area | Proposed | Summer 2015/16 | 3 - 5 | Did not appear in 2011 APR | Outside the scope of the 2012 NTNDP
Section 5.2.2 | Supply to Bowen Basin coal mining area Options include building: • Four 132 kV capacitors; Nebo-Broadlea 132 kV line via Moorvale; and second Strathmore transformer • Four 132 kV capacitors; Nebo-Broadlea 132 kV line; Moranbah-Northern Hub 132 kV line • Four 132 kV capacitors; Lilyvale-Broadlea via Moorvale 275 kV line; and Moorvale 275 kV Substation • Four 132 kV capacitors; Strathmore-Northern Hub 275 kV line; and Northern Hub substation | Thermal limitations in the Bowen Basin coal mining area due to potential mining growth | Under consultation | 2013/14 to 2014/15 | 119 - 182 | Section 4.5.3 | Outside the scope of the 2012 NTNDP
Section 5.2.3 | Improvement of supply within Gladstone region | Thermal limitations in the Gladstone region due to potential new generation developments | Proposed | Not within 5 years | Not specified in APR | Section 4.5.4 The limitation was previously reported to occur from summer 2016/17. | The need to reinforcement of the supply in the region was observed in the Slow Rate of Change scenario.
Section 5.2.3 | Build new Calvale-Stanwell 275 kV double circuit line | Thermal limitations on the transfer capability between Central West and Gladstone regions | Committed | Summer 2013/14 | Not specified in APR | Section 4.5.4 | Included in 2012 NTNDP studies
Section 5.2.3 | Install new Bouldercombe 275/132 kV transformer | Supply capability to the Rockhampton area | Committed | Summer 2012/13 | Not specified in APR | Section 4.5.4 | Outside the scope of the 2012 NTNDP
Section 5.2.3 | Build third Lilyvale-Blackwater 132 kV line | Supply to the Blackwater area | Committed | Summer 2012/13 | Not specified in APR | Section 4.5.4 | Outside the scope of the 2012 NTNDP
Section 5.2.4 | Build Western Down-Halys 275 kV lines and Western Down and Halys 275 kV substations | The Bulli to South West Queensland thermal limit is expected to be reached due to forecasted load growth | Committed | 2013/14 | Not specified in APR | Section 4.5.5 The estimated year of completion for these projects was reported as 2012/13 in the 2011 APR | Included in 2012 NTNDP studies
Section 5.2.4 | Build Columboola-Wandoan South 275 kV line, Columboola-Western Downs 275 kV line, Wandoan South 275 kV substation, and Columboola 275 kV substation | Thermal limitations due to new industrial load growth | Committed | Winter 2013 | Not specified in APR | Section 4.5.5 | Included in 2012 NTNDP studies
Section 5.2.4 | Install new Wondoan 132/66 kV transformer | Supply to the Wondoan area | Proposed | Winter 2014 | 5 - 8 | Did not appear in 2011 APR | Outside the scope of the 2012 NTNDP
Section 5.2.5 | Increase of central Queensland to south Queensland transfer limit Options include: • Install substation and series capacitors near the future Auburn River Substation • Install additional 275 kV transmission line between central and southern Queensland | Central Queensland to south Queensland transfer limit may be reached due to future generation developments and load growth in south Queensland | Proposed | 2016/17 | 90 - 110 170 - 410 | Section 4.5.6 The limitation was previously reported to occur from summer 2014/15 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 5.2.5 | Improvement of supply within the southern Brisbane area Options include: • Establishment of a Larapinta 275/110 kV substation • Establishment of a Nudgee 275/110 kV substation; and establishment of a Larapinta 275/110 kV substation • Establish Upper Kedron 275/110 kV substation; and Larapinta 275/110 kV Substation establishment | Due to load growth, thermal limitations in the Energex 110 kV network, followed by thermal limitations in the Rocklea 275/110 kV transformers, and 275 kV and 110 kV network supplying this area are forecast to occur | Under consultation | 2015/16 to 2017/18 | 70 - 128 | Section 4.5.6 The timing for the limitation has been deferred by one year. | Outside the scope of the 2012 NTNDP
Section 5.2.5 | Reinforcement of supply within southern Brisbane, CBD, and eastern suburbs area | Thermal limitations during unplanned outage of a line between Blackwall and Goodna substations | Proposed | Not within 5 years | Not specified in APR | Section 4.5.6 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 5.2.5 | Augment supply to the South East Queensland area by building a new 500 kV Halys-Blackwall double circuit line (initially operated at 275 kV) | Voltage and thermal limitations in the south east Queensland network | Proposed | 2017/18 | 380 - 420 | Section 4.5.6 The limitation was previously reported to occur from summer 2014/15 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 5.2.5 | Modification of transformer connection arrangements at South Pine substation | Supply to the north Brisbane area | Proposed | Summer 2016/17 | 2 - 3 | Did not appear in 2011 APR | Outside the scope of the 2012 NTNDP
Section 5.2.5 | Install two new Ashgrove West 80 MVA 110/33 kV transformers to replace existing 60 MVA 110/33 kV transformers | Supply to the Ashgrove West area | Committed | Summer 2013/14 | Not specified in APR | Section 3.2 | Outside the scope of the 2012 NTNDP
Section 5.2.5 | Install additional Loganlea 100 MVA 110/33 kV transformer | Supply to the Loganlea area | Committed | Summer 2013/14 | Not specified in APR | Section 3.2 | Outside the scope of the 2012 NTNDP

## TransGrid 2012 APR Projects
2012 APR Reference | Transmission Development | Limitation Addressed | 2012 APR Project Status | 2012 APR Anticipated Timing | 2012 APR Indicative Cost ($ million) | 2011 APR Reference | 2012 NTNDP
Section 5.2.1 | Install Armidale static VAr compensator power oscillation damper | Small signal stability limit on the QNI interconnector | Under test | 2012 | Not specified in APR | Section 5.2.1 | Included in 2012 NTNDP studies
Section 5.2.2 | Supply to the Sydney central business district and inner metropolitan | Cable thermal limit ratings in Sydney central business district | Committed | 2013/14 | Not specified in APR | Section 5.2.3 | Included in 2012 NTNDP studies
Section 5.2.3 | Install two 200 MVAr capacitors at Armidale substation | Voltage control limitations in northern NSW | Committed | 2013 | Not specified in APR | Section 5.2.3 | Included in 2012 NTNDP studies
Section 5.2.4 | Build new Williamsdale 330/132 kV substation | To meet reliability and security requirements of the ACT government | Committed | 2012 | Not specified in APR | Section 5.2.6 | Included in 2012 NTNDP studies
Section 5.2.5 | Wallerawang 132/66 kV substation replacement | The existing Wallerawang 132/66 kV Substation is approaching the end of its serviceable life and is to be replaced | Committed | 2014 | Not specified in APR | Section 5.2.9 | Outside the scope of the 2012 NTNDP
Section 5.2.6 | Upper Tumut switching station rehabilitation | Replacement of high voltage equipment and secondary systems | Committed | 2014 | Not specified in APR | Section 5.2.10 | Outside the scope of the 2012 NTNDP
Section 5.2.7 | Beaconsfield West works: install third 330/132 kV transformer, substation switch gear replacements; install new 132 kV cable connectors; install two 160 MVAr capacitors | Substation refurbishment and voltage control limitations | Committed | 2012 | Not specified in APR | Section 5.2.11 | Included in 2012 NTNDP studies
Section 5.2.8 | Supply to the Hawks Nest/Tea Gardens Area Essential Energy has completed a new single transformer 132/33 kV substation in the Hawks Nest/Tea Gardens area. TransGrid are to build short sections of 132 kV line to connect the new substation to the 963 Tomago–Taree 132 kV line. | Thermal and voltage limits in 33 kV network in the Hawks Nest/Tea Gardens area | Committed | 2012 | Not specified in APR | Section 5.2.12 | Outside the scope of the 2012 NTNDP
Section 5.2.9 | Supply to the Lower Mid North Coast • Build of short sections of single circuit and double circuit 330 kV line, to initially operate at 132 kV, between TransGrid’s Tomago 330 kV substation and the Tarro area • Build new double circuit 132 kV line between Tarro and Essential Energy’s Stroud substation • Connections to establish a new Tomago–Stroud 132 kV line and a Tomago–Brandy Hill 132 kV line. | Thermal limitations of the lower mid north coast 132 kV network | Committed | 2012/13 | Not specified in APR | Section 5.3.2 Part of the project outline in the 2011 APR has been delayed to beyond 2020 • Construction of a new single circuit 330 kV line between Stroud and Lansdowne (north of Taree) initially to be operated at 132 kV • Establishment of a new 132 kV switching station at Lansdowne • Construction of short sections of 132 kV transmission line between Lansdowne and TransGrid’s Taree–Port Macquarie 132 kV line | Included in 2012 NTNDP studies
Section 5.2.12 | Replacement of three 30MVA transformers by two 60MVA transformers at Narrabri 132/66 kV substation | Refurbishment work | Committed | 2013 | Not specified in APR | Section 5.2.15 | Outside the scope of the 2012 NTNDP
Section 5.2.12 | Replacement existing transformers with 375MVA units at Wallerawang 330/132 kV substation | Refurbishment work | Committed | Not specified in APR1 | Not specified in APR | Section 5.2.15 | Included in 2012 NTNDP studies
Section 5.2.13 | Replacement of existing No.1 and No.2 capacitor banks with 8 MVAr banks at Griffith substation | Refurbishment work and voltage control | Committed | 2012 | Not specified in APR | Section 5.2.16 | Included in 2012 NTNDP studies
Section 5.2.13 | Replacement of existing 7.5 MVAr capacitor banks with a 16 MVAr bank at Coffs Harbour substation | Refurbishment work and voltage control | Committed | 2012 | Not specified in APR | Section 5.3.8 – no significant change | Included in 2012 NTNDP studies
Section 5.2.13 | Replacement of existing 7.5 MVAr capacitor banks with a 16 MVAr bank at Port Macquarie substation | Refurbishment work and voltage control | Committed | 2012 | Not specified in APR |  | Included in 2012 NTNDP studies
Section 5.3.1 | Supply to the Far North NSW: • Uprate 96C Armidale-Coffs Harbour 132 kV line • Build Dumaresq-Lismore 330 kV line | Thermal rating of 132 kV network in far north NSW | Proposed RIT-T to be reapplied to project | Not specified in APR2 | Not specified in APR | Section 5.3.1 In the 2011 APR this transmission project had passed the RIT-T process and was planned to be completed by 2015 | The need to reinforce the 132 kV network in northern NSW was observed in the Planning scenario in the period between 2017-18 and 2021-22. This is consistent with the 2012 TransGrid APR.
Section 5.3.2 | Redevelopment of Orange 132/66 kV Substation including an additional 66 kV capacitor bank | Refurbishment and voltage control | Committed | Work to be completed progressively | Not specified in APR | Section 5.2.5 | Outside the scope of the 2012 NTNDP
Section 5.3.3 | Development of Southern Supply to the ACT • Build Wallaroo 330 kV substation and connect to the Canberra–Williamsdale 330 kV line • Install second 330/132 kV transformer at Williamsdale substation | To meet reliability and security requirements of the ACT government | Committed | Not specified in APR | Not specified in APR | Section 5.3.3 | Included in 2012 NTNDP studies
Section 5.3.4 | Supply to Tomerong / Nowra area • Build new Tomerong 330/132 kV substation • Build short section of double circuit 330 kV line from Kangaroo Valley to Capital Wind Farm • Build short sections of 132 kV line from the new Tomerong substation to Endeavour Energy’s 132 kV lines to the east | Supply to Tomerong and Nowra area | Committed | Not specified in APR | Not specified in APR | Section 5.3.4 | Included in 2012 NTNDP studies
Section 5.3.5 | Supply to Lake Munmorah and Reinforcement of Central Coast Supply • Reconstruction of Ausgrid’s existing Lake Munmorah 33/11 kV zone substation • Build 132 kV busbars at TransGrid’s Vales Point 132 kV substation and at or near Munmorah 132 kV supply point | Limitations of Ausgrid’s 33 kV network | Committed | 2012 | Not specified in APR | Section 5.3.5 | Outside the scope of the 2012 NTNDP
Section 5.3.6 | Reinforcement of Supply within Sydney Inner Metropolitan area • Ausgrid to build a 700m section of 132 kV cable between Beaconsfield West Substation and the Metro Grid cable tunnel portal • TransGrid to build a 330 kV cable in the Metro Grid tunnel to Haymarket. • Ausgrid to connect the cable to the Beaconsfield West 132 kV substation and Haymarket 132 kV substation | Inner metropolitan Sydney 132 kV cable thermal rating limitations Due to the condition and reduced rating of the 41 Sydney South–Beaconsfield West 330 kV cable, there is a need to provide additional supply capacity to the inner metropolitan area as soon as can be achieved | Committed | 2012 | Not specified in APR | Section 5.3.6 | Included in 2012 NTNDP studies
Section 5.3.7 | Uprating the Marulan-Avon, Marulan-Dapto and Kangaroo Valley–Dapto 330 kV lines | Thermal rating limitations on the Marulan-Dapto and Kangaroo Valley–Dapto 330 kV lines | Committed | 2015 | Not specified in APR | Section 5.3.7 | Included in 2012 NTNDP studies
Section 5.3.9 | Replacement and uprating of the Wallerawang–Orange 132 kV line | Condition of the Wallerawang–Orange 132 kV line 132 kV line thermal limitations | Committed | 2014 | Not specified in APR | Section 5.3.9 | Included in 2012 NTNDP studies
Section 5.3.11 | Install fourth Sydney East 330/132 kV transformer | Transformer rating limitations | Committed | 2013 | Not specified in APR | Section 5.3.10 | Included in 2012 NTNDP studies
Section 5.3.11 | Replace existing 132/33 kV transformers with two 60 MVA transformers at Yanco substation | Transformer condition | Committed | 2014 | Not specified in APR | Section 5.3.10 | Outside the scope of the 2012 NTNDP
Section 5.3.11 | Replace existing 132/33 kV transformers with three 60MVA units at Griffith substation | Transformer condition | Committed3 | 2014 | Not specified in APR | Section 5.3.10 | Outside the scope of the 2012 NTNDP
Section 5.3.14 | Install new 200 MVAr 330 kV capacitor bank at the Sydney South substation | Voltage control in Sydney area | Committed3 | 2012/13 | Not specified in APR | Section 5.3.8, 5.3.13 | Included in 2012 NTNDP studies
Section 5.3.14 | Replace and upgrade one 80 MVAr capacitor bank to 160 MVAr at the Sydney West substation | Capacitor condition and voltage control | Committed3 | 2012/13 | Not specified in APR | Section 5.3.13 | Included in 2012 NTNDP studies
Section 5.3.14 | Install new 80 MVAr capacitor bank at Regentville substation | Voltage control | Committed | Not within 3 years | Not specified in APR | Section 5.3.13 | Included in 2012 NTNDP studies
Section 5.3.13 | Replace and upgrade one 80 MVAr capacitor bank to 120 MVAr at Canberra substation | Capacitor condition and voltage control | Committed | 2013/14 | Not specified in APR | Section 5.3.13 | Included in 2012 NTNDP studies
Section 5.3.13 | Install new 80MVAr capacitor bank at the Yass substation | Voltage control | Committed | 2013/14 | Not specified in APR | Section 5.3.8 | Included in 2012 NTNDP studies
Section 6.1.1 | Supply to southern Sydney Options include: • Build an additional Kemps Creek-Liverpool 330 kV line • Build additional Kemps Creek-Sydney South 330 kV line • Increasing the ratings of the Sydney West–Liverpool 330 kV line and Kemps Creek–Sydney South 330 kV line | Line thermal limitations of the 330 kV network supplying southern Sydney | Proposed | Between 5 and 10 years | Not specified in APR | Section 6.1.1 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.1.2 | Capacity of the Snowy to Yass/Canberra 330 kV system Options include: • Install reactive support plant • New line development • Upgrading of the Upper Tumut–Yass 330 kV line and Upper Tumut–Canberra 330 kV line north of Snowy • Installation of power flow control plant • Real time line monitoring • Implementation of a system protection scheme | Thermal rating of 330 kV lines north of the Snowy region Voltage control at Yass and Canberra substations | Proposed | Within 5 years | Not specified in APR | Section 6.1.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.1.3 | Supply to the Forster/Tuncurry area Build a 132/66 kV substation in the Hallidays Point area to be supplied from the existing 963 Tomago–Taree 132 kV line together with sections of 132 kV and 66 kV lines to form connections to the new substation | Thermal limitation of the 66 kV network supplying the Forster/Tuncurry area | Proposed | Within 5 years | Not specified in APR | Section 6.1.3 | Outside the scope of the 2012 NTNDP
Section 6.1.4 | Acquisition of a network support and control ancillary service contract to control the voltage in the Snowy area Options include: • Replacement of the limiting generator transformers at Upper Tumut. • Installation of shunt reactors. • Contracting with critical generators for the absorption of VARs | High voltage at the Upper Tumut substation during periods of low system load and low power transfer between Victoria and NSW | Proposed | Within 5 years | Not specified in APR | Section 6.1.6 | Outside the scope of the 2012 NTNDP
Section 6.1.5 | Acquisition of a network support and control ancillary service contract to control the voltage at Kangaroo Valley substation | High voltage at Kangaroo Valley substation at times when there is limited generators in service in the Kangaroo Valley system and during line outages for maintenance | Proposed | Within 5 years | Not specified in APR | Section 6.1.7 | Outside the scope of the 2012 NTNDP
Section 6.1.6 | Supply to the Gunnedah, Narrabri and Moree areas. The preferred option is for the construction of a new Tamworth–Gunnedah 132 kV line | Line thermal ratings of the 132 kV network supplying the Gunnedah, Narrabri and Moree areas | Proposed | Within 5 years | Not specified in APR | Section 6.1.9 | Outside the scope of the 2012 NTNDP
Section 6.1.11 | Supply to the Sydney Inner Metropolitan Area Options include: • Install a larger series reactor on 41 Sydney South-Beaconsfield West cable at Sydney South substation • Install a phase shifting transformer on 41 Sydney South-Beaconsfield West cable • Works within the Ausgrid 132 kV network • Rearrangement of existing series reactors at Sydney South substation to increase the series reactance associated with the 41 Sydney South-Beaconsfield West 330 kV cable The preferred option to address longer term issues is to build a new Rookwood-Beaconsfield West 330 kV cable | Condition and thermal limitations of the 132 kV cables within Ausgrid’s network in the inner metropolitan area | Proposed | Not determined4 | Not specified in APR | Did not appear in 2011 APR. Recent investigations regarding the condition of the 41 cable installation resulted in a reduction of the cable’s rating. | The need to reinforce supply to the Sydney inner metropolitan area was observed in the Planning and Slow Rate of Change scenarios in the period between 2012-13 and 2017-18. This is consistent with the 2012 TransGrid APR.
Section 6.2.1 | Supply to Beryl Options include: • Install additional capacitors at Beryl or within Essential Energy’s network supplied from Beryl • Build a second Wellington–Beryl 132 kV line • Build a 330/132 kV substation near Beryl, supplied from the Wollar-Wellington 330 kV line • Demand management or local generation | During outages of the Wellington–Beryl 132 kV line at times of high load, unacceptably low voltages can occur at the Beryl substation | Proposed | Within 5 years | Not specified in APR | Section 6.2.1 | Outside the scope of the 2012 NTNDP
Section 6.2.2 | Reinforce the 132 kV supply to Mudgee | Reliability and security requirements as a result of load growth in the Mudgee area | Proposed | Within 5 years | Not specified in APR | Did not appear in 2011 APR | Outside the scope of the 2012 NTNDP
Section 6.2.3 | Supply to Tumut / Gadara Remedial works required to restore the condition of the following transmission lines: • No. 992 Burrinjuck -Tumut 132 kV line • No. 970 Burrinjuck–Yass 132 kV line • No. 993 Wagga 330–Gadara 132 kV line • No. 99P Gadara–Tumut 132 kV line | Condition and thermal ratings of 132 kV lines supplying the Tumut/Gadara region Voltage control in the Tumut/Gadara region | Proposed | Within 5 years | Not specified in APR | Section 6.2.2 | Outside the scope of the 2012 NTNDP
Section 6.2.4 | NSW to Qld transmission capacity Options include: • Series compensation of the interconnecting 330 kV lines between Armidale, Dumaresq and Bulli Creek • Line series compensation and a second Armidale static VAr compensator • Install a static VAr compensator at Armidale • Augmentations to protection systems to improve line fault clearing times • Build new 330 kV lines between Armidale and Bulli Creek • A second interconnection at 330 kV between Bayswater and the Queensland Western Downs • Build a second interconnection at 500 kV • Build a HVDC back-to-back scheme in QNI • Install a braking resistor in the Hunter Valley | The QNI interconnector connects the NSW and Queensland power systems. Its power transfer capability is governed by overall system-wide stability limitations and also by voltage control and line rating limitations in the supporting 330 kV systems. QNI can be heavily loaded depending on the dispatch of generation across the NEM. There is potential for upgrading of the interconnector capability and also for the development of new interconnecting lines. | Proposed | Within 5 years | Not specified in APR | Section 6.2.3 The proposed NSW to Qld transmission capacity project published in the 2011 APR was based on the final “Potential Upgrade of Queensland/New South Wales Interconnector (QNI)–Assessment of Optimal Timing and Net Market Benefit” report published in 2008. | No upgrades to the QNI interconnector were identified in the 2012 NTNDP
Section 6.2.5 | increase the rating of the Wallerawang-Sydney South/Ingleburn 330 kV lines | The 330 kV lines between Wallerawang and Sydney South can be heavily loaded at times of high western and northern generation | Proposed | Within 5 years | Not specified in APR | Section 6.2.4 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.2.6 | Yass–Bannaby and Yass–Marulan 330 kV Lines The preferred short-term network development option for upgrading the power transfer capability is the upgrading of the existing No. 61 Bannaby-Yass 330 kV line to higher thermal rating TransGrid’s long-term plan for the system south of Bannaby has the following components: • A 500 kV link from the Bannaby area to Yass • A 500 kV link from Yass to the Wagga area • Further interconnection development from the Wagga area to Victoria | Line thermal ratings of the 330 kV lines between Yass and Bannaby, and between Yass and Marulan | Proposed | Within 5 years | Not specified in APR | Section 6.3.1 | Limitation does not arise in the 2012 NTNDP expansion plan. However it was noted that if significant scheduled generation was to be developed in southern NSW then limitations may occur on the Yass–Bannaby and Yass–Marulan 330 kV lines
Section 6.2.8 | Reconstruction of the Tamworth and Armidale 330 kV Switchyards | Reliability of the Tamworth and Armidale 330 kV Switchyards | Proposed | Within 5 years | Not specified in APR | Section 6.3.3 | Outside the scope of the 2012 NTNDP
Section 6.2.9 | Supply to the Darlington Point Area Options include: • Development of the 330 kV network to the Darlington Point area • Reactive support • Development of the 330 kV network to the Finley area • Development of the 220 kV network from the Victorian system across the Murray River • Further development of the 132 kV system in the area • Non-network support such as load reduction at times of high load or embedded generation • Extension of the 500 kV system south from the Wagga area | Line thermal ratings and voltage control issues in the Darlington Point area | Proposed | Not determined | Not specified in APR | Was not in 2011 APR | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.3.1 | Upgrade of the Hunter Valley – Tamworth – Armidale 330 kV System Options include: • Upgrading the Liddell–Tamworth 330 kV lines to a higher design temperature • Replacing some of the single circuit 330 kV lines with double circuit 330 kV or 500 kV lines | Line thermal ratings Voltage conditions | Proposed | Not determined | Not specified in APR | Section 6.3.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.3.2 | Replace the Kemps Creek 500/330 kV fixed ratio transformers with transformers with on-load tap changing facilities | Voltage control in the Sydney area | Proposed | Not Determined | Not specified in APR | Section 6.3.4 | Outside the scope of the 2012 NTNDP
Section 6.3.3 | Strengthening the 500 kV network around the Newcastle – Sydney – Wollongong Area Options include: • A 500 kV line between Bannaby and Sydney • A 500 kV line between the Hunter Valley and the coast via the Newcastle area | Line thermal ratings Voltage conditions | Proposed | Not Determined | Not specified in APR | Section 6.3.5 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.3.4 | Convert one of the Sydney North-Sydney East 132 kV lines to its design 330 kV operation | Line thermal ratings | Proposed | Not Determined | Not specified in APR | Section 6.3.6 | Outside the scope of the 2012 NTNDP
Section 6.3.6 | NSW – Victoria Interconnection Options include: • Upgrading of Victorian lines and transformers, static VAr compensator installation and a braking resistor to improve the Victorian export capability • Reactive support in the Jindera area, line series compensation of the Lower Tumut – Wagga – Jindera system or other power flow control devices to improve the Victorian import capability • Major 330 kV line development to provide a significant increase in the Victorian import capability • Extension of the 500 kV network from Bannaby to Victoria via Yass and the Wagga area | Line thermal ratings Voltage conditions Dynamic stability | Proposed | Not Determined | Not specified in APR | Section 6.3.8 | No upgrades to the NSW – Victoria interconnection interconnector were identified in the 2012 NTNDP
Section 6.3.7 | Capacity of the Connections between the Central Coast Power Stations Rearrangement of 330 kV connections in the Central Coast system and installation of a line series reactor | Line thermal ratings | Proposed | Not Determined | Not specified in APR | Section 6.1.5 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 6.3.8 | Supply to the Albury Area Options Include: • Build an additional Jindera-Albury 132 kV line • Installation of capacitors at Albury or within Essential Energy’s 132 kV and 22 kV networks supplied from Albury • Demand management and local generation | Line thermal ratings | Proposed | Not Determined | Not specified in APR | Was not in 2011 APR | Outside the scope of the 2012 NTNDP
Section 6.3.9 | Supply to the Kew, Laurieton and Lake Cathie Areas Establishment of a 132/66 kV substation in the Kew/Laurieton area | Line thermal ratings | Proposed | Not Determined | Not specified in APR | Section 6.1.4 | Outside the scope of the 2012 NTNDP
1 | One transformer is commissioned. Second associated with refurbishment works at the 132/66 kV substation
2 | Indicative timing determined during the RIT-T process
3 | These projects are not considered committed by TransGrid but have passed the appropriate regulatory test
4 | Possibly 5 years

## AEMO 2012 APR Projects
2012 APR Reference | Transmission Development | Limitation Addressed | 2012 APR Project Status | 2012 APR Anticipated Timing | 2012 APR Indicative Cost ($ million) | 2011 APR Reference | 2012 NTNDP
Section 3.1.1 | Brunswick Terminal Station New 66 kV supply from the Brunswick Terminal Station. The proposed connection comprises three 225 MVA 220/66 kV transformers | Connection asset loading at surrounding terminal stations | Committed | End of 2014 | Not specified in APR | Section 3.8.2 Was previously a proposed project | Outside the scope of the 2012 NTNDP
Section 3.1.1 | Installation of a fifth 150 MVA 220/66 kV transformer at Keilor terminal station | Connection asset thermal loading at Keilor Terminal Station | Committed | 2012 | Not specified in APR | Section 3.8.2 Was previously a proposed project | Outside the scope of the 2012 NTNDP
Section 3.1.1 | Connection of Macarthur Wind Farm to the No.1 Moorabool-Heywood 500 kV line at Tarrone terminal station | New generation connection | Committed | In progress To be completed by January 2013 | Not specified in APR | Section 3.8.1 Proposed service date was by 2012 | Included in 2012 NTNDP studies
Section 3.1.1 | Connection of Morton’s Lane Wind Farm to one of the existing 66 kV lines between Terang terminal station and the Hamilton zone substation | New generation connection | Committed | Second half of 2012 | Not specified in APR | Section 3.8.2 Was previously a proposed project | Included in 2012 NTNDP studies
Section 3.1.1 | Connection of proposed Qenos Cogeneration plant in Altona | New generation connection | Committed | Late 2012 | Not specified in APR | Not identified in the 2011 VAPR | Outside the scope of the 2012 NTNDP
Section 3.1.1 | Installation of a fifth 150 MVA 220/66 kV transformer at Richmond terminal station. | Connection asset thermal loading at Richmond terminal station | Committed | Early 2013 | Not specified in APR | Not identified in the 2011 VAPR | Outside the scope of the 2012 NTNDP
Section 3.1.1 | Establishment of Tarrone terminal station to connect new wind farm. Tarrone terminal station will cut into the existing Moorabool-Heywood 500 kV No. 1 line approximately 65 kilometres from the Heywood terminal station | New generation connection | Committed | Completed | Not specified in APR | Section 3.8.1 Was previously a proposed project | Included in 2012 NTNDP studies
Section 3.1.1 | Build a Cranbourne-Wonthaggi Desalination Plant 220 kV cable | New load connection | Committed | End of 2012 | Not specified in APR | Section 3.8.1 Previous proposed date was late 2011 to early 2012 | Included in 2012 NTNDP studies
Section 3.1.2 | Alcoa Portland 500 kV emergency bus tie | Ensure continued Alcoa Portland Aluminium Smelter supply during Alcoa Portland – Heywood 500 kV line and circuit breaker outages | Proposed | Service date is yet to be proposed | Not specified in APR | Not identified in the 2011 VAPR | Outside the scope of the 2012 NTNDP
Section 3.1.2 | Establishment of Deer Park terminal station Includes two 150 MVA 220/66 kV transformers connecting to the existing Keilor–Geelong 220 kV No.2 line | Distribution and connection asset loading at surrounding terminal stations | Under consultation | Late 2016 | Not specified in APR | Section 5.6 Was previously a proposed project | Outside the scope of the 2012 NTNDP
Section 3.2.1 | South Australia–Victoria (Heywood) Interconnector Upgrade | South Australia–Victoria (Heywood) interconnector congestion. Uneven Heywood 500/275/22 kV transformer loadings and voltage instability (collapse) in the vicinity of Heywood and the Portland Alcoa plant. | Under consultation | Not specified in APR1 | 80 - 800 | Section 5.5.1 Identified for RIT-T assessment commencing in 2011/12 | Included in the 2012 NTNDP expansion plan
Section 3.2.2 | Eastern Metropolitan Melbourne Reactive Support Installing new capacitors in the Melbourne metropolitan region | Inadequate reactive power support in Eastern Metropolitan Melbourne. | Under consultation | Two of the augmentations, one prior to summer 2014–15 and the other prior to summer 2015–16 | 6 - 14 | Section 5.4.5 Identified for RIT-T assessment commencing in 2011/12 | Outside the scope of the 2012 NTNDP
Section 3.2.3 | Eastern Metropolitan Melbourne Thermal Capacity Options include: • Install a second 1,000 MVA 500/220 kV transformer at Cranbourne; and connecting (cut-in) the Hazelwood–Rowville 500 kV No.3 line at Cranbourne • Install a third 1,000 MVA 500/220 kV transformer at Rowville; and an underground cable between Rowville and East Rowville • Install a third 1,000 MVA 500/220 kV transformer at Rowville; and upgrading the existing East Rowville–Rowville 220 kV line • Install a third 1,000 MVA 500/220 kV transformer at Rowville • Build a new 500 kV switchyard at Ringwood terminal; and a 1,000 MVA 500/220 kV transformer at Ringwood • Build a new 500 kV substation at Templestowe terminal station | Loading relating to the Cranbourne A1 500/220 kV transformer, Rowville A2 500/220 kV transformer, and Rowville A1 500/220 kV transformer. East Rowville–Rowville 220 kV line loading | Under consultation | Not specified in APR1 | 40 - 152 | Section 5.4.5 Identified for RIT-T assessment commencing in 2011/12 | The loading of the Rowville 500/220 kV A2 transformer for an outage of the Cranbourne 500/220 kV A1 transformer (and vice versa) was identified as a limitation in the 2012 NTNDP. The limitations were observed in the 2012-13 to 2016-17 period in both the Planning and Slow Rate of Change scenarios.
Section 3.2.4 | Ringwood terminal station Supply Options include: • Connect the Rowville–Templestowe 220 kV line at Ringwood terminal station • Upgrade the existing Ringwood–Thomastown 220 kV line and replace the isolators at Ringwood terminal station | Ringwood–Thomastown 220 kV line loading. Ringwood–Rowville 220 kV line loading. | Proposed | Not specified in APR1 | 8.7 – 9.4 | Section 5.4.5 Identified for RIT-T assessment commencing in 2011/12 | The loading on the Ringwood-Thomastown 220 kV line was identified as a limitation in the 2012 NTNDP. The limitation was observed in 2017-18 to 2021-22 in the Planning scenario and in 2022-23 to 2026-27 in the Slow Rate of Change scenario.
Section 3.2.5 | Regional Victoria Reactive Support Options include: • Install one 50 MVAr 220 kV capacitor bank • Install three 15 MVAr 22 kV capacitor banks • Install two 25 MVAr 66 kV capacitor banks | Inadequate reactive power support around Bendigo in Regional Victoria. | Under consultation | Not specified in APR1 | 5.1 - 6.9 | Section 5.4.6 Identified for RIT-T assessment commencing in 2011/12 | Outside the scope of the 2012 NTNDP
Section 3.2.6 | Regional Victorian Thermal Capacity – Bendigo Supply Options include: • Install a wind monitoring scheme on the Ballarat–Bendigo 220 kV line • Uprate the Ballarat–Bendigo line to a rated conductor temperature of 82 ºC • Uprate the Ballarat–Bendigo line to a rated conductor temperature of 90 ºC • Replace the Ballarat–Bendigo 220 kV line conductor with high temperature conductor (150 ºC) • Replace the Ballarat–Bendigo 220 kV line with a new double circuit 220 kV line | Ballarat–Bendigo 220 kV line loading. | Under consultation | Not specified in APR1 | 0.6 - 170 | Section 5.4.6 Identified for RIT-T assessment commencing in 2011/12 | The loading of the Ballarat–Bendigo 220 kV line was identified as a limitation in the 2012 NTNDP. The limitation was observed in the 2012-13 to 2016-17 period in both the Planning and Slow Rate of Change scenarios.
Section 3.2.7 | Regional Victorian Thermal Capacity – Ballarat Supply Options include: • Uprate the Ballarat–Moorabool No. 1 line to 82 ºC rated conductor temperature • Uprate the Ballarat–Moorabool No. 1 line to 90 ºC rated conductor temperature • Replace the Ballarat–Moorabool No. 1 220 kV line conductor with high temperature conductor (150 ºC) • Install a third Ballarat–Moorabool 220 kV line • Replace the Ballarat–Moorabool No. 1 220 kV line with a new double circuit 220 kV line | Ballarat–Moorabool 220 kV No. 1 line loading. | Under consultation | Not specified in APR1 | 27 - 92 | Section 5.4.6 Identified for RIT-T assessment commencing in 2011/12 | The loading of the Ballarat–Moorabool 220 kV line was identified as a limitation in the 2012 NTNDP. The limitation was observed in the 2012-13 to 2016-17 period in both the Planning and Slow Rate of Change scenarios.
Section 3.2.8 | Purchase of network control and support ancillary services | Murray–Dederang 330 kV line loading (NSCAS gap identified in the 2011 NTNDP). | Under consultation | Not specified in APR1 | 35 | Limitation not identified in the 2011 VAPR | Outside the scope of the 2012 NTNDP
Section 3.3.2 | Voltage control at Heywood terminal station or near the Portland Alcoa plant Options include: • Install a switched capacitor with individual phase switching at Heywood terminal station or near Alcoa Portland • Install a static VAr compensator or a synchronous static compensator • Build additional transposition towers along the Moorabool–Heywood/Alcoa Portland 500 kV line | Moorabool–Heywood–Portland 500 kV line voltage unbalance | Proposed | Not specified in APR2 | 11.4 – 45 | Section 5.4.3 Identified for further assessment | Outside the scope of the 2012 NTNDP
Section 3.3.3 | Upgrading station control instrumentation equipment and/or a new Dederang – South Morang 330 kV line installation. Options include: • Upgrade the station control instrumentation equipment • Uprate the two existing lines between Dederang and South Morang to 82 °C (conductor temperature) operation, install series compensation • Install a new (third) 330 kV, 1,060 MVA single circuit line between Dederang and South Morang with series compensation | Dederang – South Morang 330 kV line loading | Proposed | Not specified in APR2 | 0.27 - 333 | Section 5.4.4 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 3.3.4 | Rowville–Malvern 220 kV line upgrade Options include: • Install wind monitoring facilities • Replace sections of the Rowville–Malvern circuits with high capacity (high temperature) conductor • Cut-in the No. 1 and No. 4 Rowville–Richmond 220 kV lines at the Malvern terminal station to form the No. 3 and No. 4 Rowville–Richmond–Malvern lines • Loop-in and switch the No. 1 and No. 4 Rowville–Richmond 220 kV lines at Malvern terminal station to form the No. 2 and No. 4 Rowville–Malvern 220 kV lines, and the No. 1 and No. 4 Richmond–Malvern 220 kV lines | Rowville–Malvern 220 kV line loading | Proposed | 2017–18 | 0.3 – 24 | Section 5.4.5 | Limitation was observed in the 2012 NTNDP. This was a radial line and timing depends on the point of connection load forecasts and any load transfers to nearby terminal stations.
Section 3.3.4 | A new Cranbourne–Heatherton 220 kV double circuit line or underground cable, or a new underground cable between Heatherton and Malvern Options include: • Install a special control scheme to enable automatic load shedding so the line can be loaded up to the 5-minute rating of the conductor • Install a third 220 kV line between Rowville and Springvale • Install a new overhead double circuit 220 kV line between Cranbourne and Heatherton • Install a new underground 220 kV cable between Cranbourne and Heatherton • Install a new underground 220 kV cable between Malvern and Heatherton | Rowville–Springvale–Heatherton 220 kV line loading | Proposed | Not specified in APR3 | 74 - 656 | Section 5.4.5 | Limitation was observed in the 2012 NTNDP. This was a radial line and timing depends on the point of connection load forecasts and any load transfers to nearby terminal stations.
Section 3.3.4 | A new (third) South Morang 330/220 kV transformer, or replacement of the existing ‘H’ transformers with higher-rated ones. Options include: • Install a new (third) 330/220 kV 700 MVA transformer at South Morang, and connection (cut-in) of the Thomastown–Rowville 220 kV 549 MVA line at South Morang • Install a new 500/220 kV 1,000 MVA transformer at South Morang, and connection (cut-in) of the Thomastown–Rowville 220 kV 549 MVA line at South Morang • Replace the 330/220 kV transformers at South Morang with 1,000 MVA rated transformers | South Morang H1 330/220 kV transformer loading | Proposed | Not specified in APR3 | 27 - 76 | Section 5.4.5 | The loading of the South Morang 330/220 kV transformers was identified as a limitation in the 2012 NTNDP. The limitation was observed in the 2022-23 to 2026-27 period in the Planning scenario 2032-33 to 2036-37 in the Slow Rate of Change scenario.
Section 3.3.4 | Connection of South Morang terminal station to the existing Thomastown–Rowville 220 kV line or Eildon–Thomastown 220 kV line. | South Morang–Thomastown 220 kV No. 1 line loading | Proposed | Not specified in APR3 | 8 - 10 | Section 5.4.5 | The loading of the South Morang to Thomastown 220 kV circuits was identified as a limitation in the 2012 NTNDP. The limitation was observed in the 2022-23 to 2026-27 period in the Planning scenario 2032-33 to 2036-37 in the Slow Rate of Change scenario.
Section 3.3.4 | Install additional reactive power compensating plant. | Inadequate reactive power support around Western Metropolitan Melbourne | Proposed | Not specified in APR4 | Not specified in APR | Limitation not identified in the 2011 APR | Outside the scope of the 2012 NTNDP
Section 3.3.5 | Upgrade the limiting station assets at Geelong terminal station or installing a new single circuit or double circuit Geelong–Moorabool 220 kV line. | Geelong–Moorabool 220 kV line loading | Proposed | Not specified in APR5 | 0.9 - 44 | Limitation not identified in the 2011 APR | The loading of the Geelong-Moorabool 220 kV line was identified as a limitation in the 2012 NTNDP. The limitation was observed in the 2022-23 to 2026-27 period in the Planning scenario and in the 2032-33 to 2036-37 period in the Slow Rate of Change scenario.
Section 3.3.5 | Install a third Moorabool 500/220 kV transformer | Moorabool 500/220 kV transformer loading | Proposed | Not specified in APR6 | 49 | Section 5.4.6 | Keilor (two transformers) and Moorabool 500/220 kV transformers are in parallel operation. The loading of these 500/220 kV transformers was identified as a limitation in the 2012 NTNDP. The limitation was observed in the 2022-23 to 2026-27 period in the Planning scenario 2032-33 to 2036-37 in the Slow Rate of Change scenario.
1 | The date when investment is required is being assessed as part of the consultation
2 | Further assessment of this limitation will identify the timing and preferred solution.
3 | AEMO will undertake a detailed assessment of this limitation in the next 12 months
4 | AEMO will further assess this limitation in 2012–13, which will be carried out in conjunction with the assessment of loading limitations associated with the 500/220 kV transformers at Moorabool and Keilor.
5 | AEMO will undertake a detailed assessment of this limitation in the next 12 months to further investigate the potential impact of this limitation, the timing of augmentation and the preferred augmentation option.
6 | AEMO will include this limitation in the detailed assessment of the Geelong–Moorabool line loading limitation, which will be conducted within the next 12 months
`

## ElectraNet 2012 APR Projects
2012 APR Reference | Transmission Development | Limitation Addressed | 2012 APR Project Status | 2012 APR Anticipated Timing | 2012 APR Indicative Cost ($ million) | 2011 APR Reference | 2012 NTNDP
Section 6.4.2 | Install a static VAr compensator at Davenport. | Inadequate reactive support due to high load increase in the upper north 275 kV network and possible power station retirement | Proposed | 2016 Subject to power station availabilities | 42 | Section 6.4.2 | Outside the scope of the 2012 NTNDP
Section 6.4.2 | Uprate the 275 kV Para–Templers West-- Brinkworth–Davenport line from 650C to 800C design temperature | Unplanned outage of Mid North 275 kV line overloads the Para–Templers West–Brinkworth–Davenport 275 kV line | Proposed | Not within ten years | 83 | Section 6.4.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 7.4.2 | Build Munno Para substation and install a single 225 MVA 275/66 kV transformer supplying the northern suburbs | Load growth in the metro north overloads the 66 kV network, and the 275/66 kV transformer capacity | Committed | 2014 | 43 | Section 7.4.2 | Included in 2012 NTNDP studies
Section 7.4.2 | Replace Torrens Island Power Station transformers with two 225 MVA transformers; this solution option can potentially be deferred by contracting generation in the area | An outage of one of the Torrens Island Power Station 275/66 kV transformers overloads the remaining one. Loss of Kilburn transformer overloads both Torrens Island Power Station transformers. Both transformers are reaching the end of their design life. | Proposed | 2015 | 16 | Section 7.4.2 2011 APR anticipated timing was in 2016 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Install a second 225 MVA 275/66 kV transformer at East Terrace substation. Remove the protection limits on the East Terrace-Magill 275 kV 450 MVA cable. | Load growth in the Adelaide central business district area causes the 275/66 kV transformer capacity to exceed the Electricity Transmission Code requirements | Proposed | 2017 | 23 | Section 7.4.2 2011 APR anticipated timing was in 2016 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Install a third 225 MVA 275/66 kV transformer at Morphett Vale East | An outage of one transformer at Morphettt Vale East overloads the remaining transformer. | Proposed | 2020 | 19 | Section 7.4.2 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Build a new 275/66 kV substation at Yatala Vale North with a 225 MVA transformer | Loss of either 275/66 kV transformer at Magill overloads the remaining transformer. Loss of one of the 275/66 kV transformers at Northfield overloads the remaining two transformers. Thermal and voltage limitations in the ETSA Utilities 66 kV network supplying the north eastern suburbs | Proposed | Not within ten years | 35 | Section 7.4.2 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Install one 300 MVA 275/66 kV transformer supplying the western suburbs at city west. | Thermal limitations on the Torrens Island Power Station and Kilburn 275/66 kV transformers; and the Torrens Island Power Station-New Osborne 66 kV line | Proposed | 2022 | 20 | Not in 2011 APR | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Build a 275 kV substation at Kanmantoo North; build a double circuit 275 kV line from Kanmantoo North to the Fleurieu Peninsula; install a 275/66 kV transformer at Currency Creek. | Voltage limitation on the ETSA Utilities 66 kV distribution network fed from Willunga. | Proposed | No earlier than 2020 | 210 | Section 7.4.2 2011 APR anticipated timing was between 2016 and 2022 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Build a Kingsford substation and install two 225 MVA 275/66 kV transformers | Load growth around Freeling and Roseworthy causes thermal overload on the ETSA Utilities distribution network | Proposed | Within ten years | 48 | Section 7.4.2 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Install a second 225 MVA 275/66 kV transformer at Munno Para | A Munno Para transformer outage overloads the Para transformers | Proposed | Not within ten years | 7 | Section 7.4.2 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Install a second 300 MVA 275/66 kV City West–South transformer. This project has to occur in conjunction with the second City West-Torrens Island Power Station 275 kV cable | An outage of the cable between Torrens Island Power Station and City West substation or the City West–south Adelaide transformer overloads the Happy Valley transformers | Proposed | Within ten years | 20 | Section 7.4.2 2011 APR anticipated timing was not within ten years | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Install a second City West- Torrens Island Power Station 275 kV cable. | An outage of the Torrens Island Power Station-City West 275 kV cable causes voltage collapse in the Metro South network and thermal overloading in the distribution network between City West and Happy Valley | Proposed | Within ten years | 150 | Section 7.4.2 2011 APR anticipated timing was not within ten years | Limitation does not arise in the 2012 NTNDP expansion plan
Section 7.4.2 | Install a second 300 MVA 275/66 kV transformer at City West to supply the Adelaide central region. | Outage of Magill- East Terrace cable overloads City West-Adelaide central business district transformer | Proposed | Not within ten years | 22 | Section 7.4.2 | Outside the scope of the 2012 NTNDP
Section 7.4.2 | Upgrade the section of the Happy Valley-Morphett Vale East 275 kV line with a the 800C design temperature to 1200C design temperature | With the Metro South split between Morphett Vale East and Happy Valley; loss of the Cherry Gardens-Morphett Vale East 275 kV line overloads the Happy Valley-Morphett Vale East 275 kV line. | Proposed | Not within ten years | 10 | Section 7.4.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 8.4.2 | Install a second 225 MVA 275/66 kV transformer at Mount Barker South; retire aged 132 kV assets at Mount Barker from service. | Mount Barker 132/66 kV transformers unable to meet Electricity Transmission Code service standards under the peak load outage of the Mount Barker South 275/66 kV transformer. | Proposed | 2016 | 11 | Section 8.4.2 | Outside the scope of the 2012 NTNDP
Section 8.4.2 | Rebuild Angas Creek substation with two 60 MVA transformers; install two15 MVAr 132 kV capacitor banks | An outage of an Angas Creek transformer under peak load conditions overloads the remaining unit. Unsatisfactory reactive margins exist at Angus Creek. | Proposed | 2022 | 25 | Section 8.5 | Outside the scope of the 2012 NTNDP
Section 8.4.2 | Rebuild Mobilong with two 120 MVA 132/33 kV transformers. | An outage of a 132/33 kV transformer at Mobilong overloads the remaining unit; Mobilong substation at end of technical life. | Proposed | Not within ten years | 24 | Section 8.4.2 | Outside the scope of the 2012 NTNDP
Section 8.4.2 | Install a 275/66 kV transformer at Kanmantoo North; extend the 66 kV distribution network to Kanmantoo North via Nairne. | An outage of a 275/66 kV transformer at Mount Barker South under peak load conditions overloads the remaining unit; thermal limitations on the distribution system fed from Mount Barker South Substation. | Proposed | Not within ten years | 40 | Section 8.4.2 | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Install two 25 MVA 132/33 kV transformers; and install one 15 MVAr 132 kV capacitor bank at Ardrossan West substation | Thermal overload of the remaining transformer at Ardrossan West under; inadequate voltage levels on the Yorke Peninsula under peak load contingent conditions | Committed | 2012 | 25 | Section 9.4.2 | Included in 2012 NTNDP studies
Section 9.4.2 | Install a third 60 MVA 132/33 kV transformer at Dorrien substation | Thermal overload of the remaining transformer at Dorrien | Committed | 2012 | 7 | Section 9.4.2 | Included in 2012 NTNDP studies
Section 9.4.2 | Install two 25 MVA 132/33 kV transformers and replace selected assets at Hummocks | Thermal overload of the remaining transformer at Hummocks under N-1 conditions | Committed | 2013 | 11 | Section 9.4.2 | Included in 2012 NTNDP studies
Section 9.4.2 | Rebuild Waterloo and install two 25 MVA 132/33 kV transformers | Thermal overload of a transformer at Waterloo substation; Waterloo substation at end of technical life | Committed | 2013 | 43 | Section 9.4.2 | Included in 2012 NTNDP studies
Section 9.4.2 | Install a second 200 MVA 275/132 kV transformer at Bungama | Inadequate reactive margins at Bungama, Baroota and Port Pirie connection points for the loss of the Bungama 275/132 kV transformer | Proposed | 2014 | 10 | Section 9.4.2 | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Install a second 25 MVA transformer, rebuild and reconfigure aged 132 kV bus and install a 8 MVAr 132 kV capacitor bank at Dalrymple substation | Electricity transmission code reclassification to requires transformer redundancy at Dalrymple connection point from 1 December 2016; inadequate voltage on the Yorke Peninsula under peak load contingent conditions | Proposed | 2016 | 31 | Section 9.4.2 | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Replace Baroota Substation; install second 25 MVA 132/33 kV transformer in parallel with existing 10 MVA 132/33 kV transformer | Electricity transmission code reclassification requires transformer redundancy at Baroota connection point from 1 December 2017 | Proposed | 2017 | 18 | Section 9.4.2 | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Establish a 275/132 kV substation between the West 275 kV circuit and Hummocks with a 200 MVA transformer; construct a double circuit 275 kV line from the West 275 kV circuit to the substation location, and establish a 132 kV connection to Hummocks | Inadequate voltage levels on the Yorke Peninsula for loss of the Bungama-Hummocks 132 kV line, and impending thermal overload on the remaining line for loss of either the Bungama-Hummocks 132 kV line or Waterloo-Hummocks 132 kV line | Proposed | 2019 | 191 | Section 9.4.2 Anticipated timing in 2011 APR was 2018 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 9.4.2 | Rebuild the existing 132 kV line from Bungama to Port Pirie as double circuit line and install a second 60 MVA 132/33 kV transformer at Port Pirie This development is only required if ETSA Utilities is unable to construct a distribution solution to resolve limitation | Low voltage levels on the meshed 33 kV distribution system between Port Pirie and Bungama for the loss of the Port Pirie 132/33 kV transformer or the Bungama-Port Pirie 132 kV line | Proposed | Within Ten years | 36 | Section 9.4.2 | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Establish a new 275/66 kV Jamestown connection point with two 60 MVA transformers | An increase in demand in the Peterborough area will cause low voltage levels in the 33 kV distribution network | Proposed | Within ten years | 59 | Section 9.4.2 | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Replace the two 25 MVA 132/33 kV transformers at Hummocks with two 60 MVA transformers | Thermal overload of remaining transformer at Hummocks | Proposed | Not within ten years | 36 | Not in 2011 APR | Outside the scope of the 2012 NTNDP
Section 9.4.2 | Install a second 275/132 kV transformer near Hummocks | Inadequate voltage levels on the Yorke Peninsula for loss of a 275/132 kV transformer near Hummocks | Proposed | Not within ten years | 11 | Not in 2011 APR | Limitation does not arise in the 2012 NTNDP expansion plan
Section 9.4.2 | Install a second 160 MVA 275/132 kV transformer at Templers West and establish 132 kV switchyard at Templers West; re-arrange Templers and Templers West 132 kV line connections | Inadequate voltage levels at Dorrien connection point for an outage of the Templers West 275/132 kV transformer or the Templers West to Dorrien 132 kV line | Proposed | Not within ten years | 38 | Section 9.4.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 9.4.2 | Rebuild Templers connection point with two 120 MVA 132/33 kV transformers | Thermal overload of remaining transformer at Templers under N-1 condition | Proposed | Not within ten years | 40 | Not in 2011 APR | Outside the scope of the 2012 NTNDP
Section 10.4.2 | Extend 275 kV substation at Robertstown; build double circuit 275 kV line from Robertstown to Monash; build 275 kV switchyard at Monash and install 240 MVA 275/132 kV transformer; Install two 225 MVA 275/66 kV transformers at Monash; remove 132/66 kV equipment from Berri substation; remove existing 132 kV lines between Robertstown and Berri | Inadequate voltage levels at Berri connection point following loss of support from Murraylink at peak load times Depending on Murraylink performance, an outage of the Robertstown to North West Bend number 2 132 kV line may overload the Robertstown to North West Bend number 1 132 kV line and necessitate this project in an earlier year | Proposed | Not within ten years | 407 | Section 10.4.2 Anticipated timing in 2011 APR was 2018 | Limitation does not arise in the 2012 NTNDP expansion plan. The Riverland region 132 kV network limitation is driven by regional peak load in Riverland region. This limitation does not arise at the time of 10% POE SA summer maximum demand modelled in 2012 NTNDP studies.
Section 11.4.2 | Install three additional circuit breakers and associated switchgear, metering and protection works at South East substation. | Substandard circuit breaker arrangement at South East substation makes it difficult to obtain outages for maintenance and places network security at risk. | Proposed | 2015 | 8 | Not in 2011 APR | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Rebuild Kincraig substation at an adjacent site. Install two 60 MVA transformers. | Inadequate Kincraig 132/33 kV transformer capacity in 2017/2018; asset condition at Kincraig. | Proposed | 2017 | 41 | Section 11.4.2 | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Install additional circuit breakers and minor plant replacement at Tailem Bend substation. | Present layout at Tailem Bend substation poses operational issues that constrain interconnection power transfer during maintenance of circuit breakers. | Proposed | 2018 | 16 | Section 11.4.2 Scope change from 2011 APR: second 275/132 kV transformer will no longer be installed | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Rebuild Keith substation at an adjacent site. Install two 60 MVA transformers; include provision for DVAR/SVC1 | Inadequate Keith 132/33 kV transformer capacity; asset condition at Keith. | Proposed | 2019 | 31 | Section 11.4.2 Anticipated timing in 2011 APR was 2016 | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Install reactive power compensation at Keith substation. | Voltage collapse with the loss of the South East-Penola West 132 kV line. | Proposed | Within ten years | Not specified in APR | Not in 2011 APR | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Establish a new Coonalpyn West 132/33 kV connection point and install two 25 MVA transformers. | Increase of load in the area causes low voltage in the distribution network and inadequate 132/33 kV transformer capacity. | Proposed | Within ten years | 30 | Section 11.4.2 | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Install a third 160 MVA transformer at South East substation. | Loss of transformer at South East substation overloads the other transformer | Proposed | Not within ten years | 19 | Section 11.4.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 11.4.2 | Establish new Coonalpyn West or Geranium 132/33 kV connection point and install two 25 MVA transformers | Increase of load in the Meningie/ Narrung area or Lameroo/ Pinnaroo area causing under voltage in the distribution network; and overload of 132/33 kV transformer | Proposed | Not within ten years | 25-70 | Section 11.4.2 | Outside the scope of the 2012 NTNDP
Section 11.4.2 | Install a second 200 MVA transformer at Tailem Bend substation. | Loss of South East-Penola West 132 kV line overloads the 275/132 kV Tailem Bend transformer. | Proposed | Not within ten years | 14 | Section 11.4.2 | Limitation does not arise in the 2012 NTNDP expansion plan
Section 11.4.2 | Rebuild Snuggery-Blanche-Mount Gambier 132 kV lines with high capacity conductor or construct second circuit | Loss of South East-Snuggery 132 kV line results in overload of Mt Gambier-Blanche 132 kV line; and loss of Mt Gambier-South East 132 kV line results in overload of Snuggery- Blanche 132 kV line | Proposed | Not within ten years | 60 | Section 11.4.2 | Outside the scope of the 2012 NTNDP
Section 12.5.2 | Install second 25 MVA 132/66 kV transformer at Wudinna substation | Electricity transmission code reclassification requires transformer redundancy at Wudinna | Committed | 2012 | 15 | Section 12.5.2 | Included in 2012 NTNDP studies
Section 12.5.2 | Establish second Davenport-Cultana 275 kV line; install two 200 MVA 275/132 kV transformers at Cultana and reconfigure 132 kV Davenport to Whyalla lines | The outage of Cultana 275/132 kV transformer, Davenport to Cultana 275 kV line or Cultana to Whyalla 132 kV circuit leads to inadequate 132 kV voltages and thermal overloads the 132 kV lines. | Committed | 2014 | 72 | Section 12.5.2 Anticipated timing in 2011 APR was 2013 | Included in 2012 NTNDP studies
Section 12.5.2 | Reinforce the lower Eyre Peninsula: Construct a Cultana-Yadnarie- Port Lincoln 275 kV double circuit line; establish 275/132 kV substations at Yadnarie and Port Lincoln; install 100 MVAr cap bank at Yadnarie and SVC at Port Lincoln. | Thermal overload of the Middleback-Yadnarie 132 kV line under system normal conditions; Condition of the Whyalla-Port Lincoln 132 kV line | Proposed | 2016 | 548 | Section 12.5.2 Anticipated timing in 2011 APR was 2018 | Limitation does not arise in the 2012 NTNDP expansion plan. The Eyre Peninsula 132 kV network limitation is driven by regional peak load in lower Eyre Peninsula. This limitation does not arise at the time of 10% POE SA summer maximum demand modelled in 2012 NTNDP studies.
Section 12.5.2 | Rebuild Port Lincoln connection point and install two 120 MVA 132/33 kV transformers | Thermal overload of Port Lincoln transformers after loss of one Port Lincoln transformer | Proposed | 2021 | 40 | Section 12.5.2 Anticipated timing in 2011 APR was 2018 | Outside the scope of the 2012 NTNDP

## Transend 2012 APR Projects
2012 APR Reference | Transmission Development | Limitation Addressed | 2012 APR Project Status | 2012 APR Anticipated Timing | 2012 APR Indicative Cost ($ million) | 2011 APR Reference | 2012 NTNDP
Section 4.3.1 | Rosebery substation 110 kV augmentation Install a 110 kV bus coupler circuit breaker at Rosebery Substation; and protection scheme replacements at Farrell and Rosebery substations. | This will enable the Farrell–Rosebery–Queenstown 110 kV line to operate normally closed, providing firm transmission security to Rosebery Substation. | Committed | 2012-10-01 | Not specified in APR | Section 4.2.12. Was scheduled to be completed in June 2012 | Outside the scope of the 2012 NTNDP
Section 4.3.2 | George Town Substation 220 kV security upgrade Reconfiguration of part of George Town Substation and replacement of assets in poor condition. | If the bus coupler circuit breaker fails to operate in the event of a fault, it has the potential to cause system instability leading to wide spread loss of load, which could exceed 850 MW. | Committed | 2012-11-01 | Not specified in APR | Section 4.2.13. Was scheduled to be completed in January 2014 | Outside the scope of the 2012 NTNDP
Section 4.3.4 | Palmerston Substation 110 kV redevelopment | The substation redevelopment will improve the reliability, security and performance of the electricity supply by replacing assets that are in poor condition and susceptible to failure. | Committed | 2013-03-01 | Not specified in APR | Section 4.2.18. Was scheduled to be completed in April 2013 | Outside the scope of the 2012 NTNDP
Section 4.3.5 | Arthurs Lake Substation redevelopment Includes the replacement of the 110/6.6 kV transformer | Security and reliability (asset condition) | Committed | 2013-08-01 | Not specified in APR | Section 4.2.14. Was scheduled to be completed in April 2013 | Outside the scope of the 2012 NTNDP
Section 4.3.6 | Newton Substation redevelopment Includes replacement of the 110/22 kV transformer and 110/11 kV transformer | Security and reliability (asset condition) | Committed | 2013-05-01 | Not specified in APR | Section 4.2.19. Was scheduled to be completed in February 2013 | Outside the scope of the 2012 NTNDP
Section 4.3.7 | Burnie Substation 110 kV redevelopment | Security and reliability (asset condition) | Committed | 2014-04-01 | Not specified in APR | Section 4.2.17. Was scheduled to be completed in March 2013 | Outside the scope of the 2012 NTNDP
Section 4.3.8 | Creek Road Substation 110 kV redevelopment | Security and reliability (asset condition) | Committed | 2013-12-01 | Not specified in APR | Section 4.2.15. Was scheduled to be completed in June 2014 | Outside the scope of the 2012 NTNDP
Section 4.3.9 | Tungatinah Substation 110 kV redevelopment Includes: the extension of the Meadowbank-New Norfolk and Tarraleah-New Norfolk 100 kV lines to the Tungatinah substation; and replacement of the 110/22 kV transformer | Security and reliability (asset condition) | Committed | 2014-04-01 | Not specified in APR | Section 4.2.16. Was scheduled to be completed in September 2013 | Outside the scope of the 2012 NTNDP
Section 5.2.1.6.1 | Rosebery Substation supply transformer capacity Preferred option: replace the two 20/30 MVA 110/44-22 kV transformers at Rosebery Substation with two 30/60 MVA 110/66-44 kV transformers | A transformer contingency by winter 2015 could result in unserved energy in excess of 300 MWh. | Proposed | 2015-06-01 | 5.6 | Section 5.2.1.1 Was proposed to be completed in June 2013. The original project has now been split into two projects, transformer augmentation and substation augmentation | Outside the scope of the 2012 NTNDP
Section 5.2.1.6.2 | Newton and Queenstown substations transmission security The preferred option: Tee-off Farrell–John Butters 220 kV line and install a 220/110 kV transformer at Queenstown Substation, connect Farrell–Rosebery–Queenstown 110 kV line in and out of Newton substation, and dismantle Queenstown–Newton 110 kV line | Loss of the Farrell–Rosebery–Queenstown 110 kV line results in loss of supply to both substations and could interrupt more than 25 MW of load by winter 2018. In addition, by winter 2012, a transmission contingency on the Farrell–Rosebery–Queenstown 110 kV line could result in more than 300 MWh of unserved energy. | Proposed | 2017-06-01 | 12 | Section 5.2.1.2 | Outside the scope of the 2012 NTNDP
Section 5.2.3.6.1 | George Town 220 kV Substation security upgrade (stage 2) | A failure of circuit breaker Z152 at George Town 220 kV Substation could lead to a significant loss of supply to the to the area and a significant loss of generation. Under certain conditions, this could cause instability | Proposed | 2016-06-01 | 6.5 | Section 5.2.3.1 Was scheduled to be completed in 2016. | Outside the scope of the 2012 NTNDP
Section 5.2.3.6.2 | Voltage support for the George Town area The preferred option comprise of Installing 100/+100 MVAr static synchronous compensator at George Town Substation | A single asset failure of a tower could result in a double circuit failure. Under some operating scenarios, such failure could result in significant interruption to supply or, in the worst case, a system black out. A significant event could result in the loss of over 850 MW load and/or 3000 MWh of unserved energy, which would not meet the performance criteria prescribed in the ESI Regulations. | Proposed | Not specified in APR | 30 | Section 5.2.3.2 | Outside the scope of the 2012 NTNDP
Section 5.2.4.6.4 | Palmerston–Avoca–St Marys transmission security The preferred option comprise of constructing a second Palmerston–Avoca 110 kV line (double circuit construction strung one circuit) | Currently, the loss of these circuits could result in more than 300 MWh of unserved energy | Proposed | 2016-06-01 | 30 | Section 5.2.4.3. Was proposed to be completed in April 2017. The preferred option has now changed. | Outside the scope of the 2012 NTNDP
Section 5.2.5.6.1 | Kingston area augmentation The preferred option comprises the construction of a new 110 kV line from Creek Road substation. Double circuit towers are proposed to allow for future load growth. A future 110/33 kV substation at McRobies Gully would be supplied via a tee-off from the new line. | A single asset failure on the 110 kV double circuit transmission line between Chapel St Substation and tower T41 could result in more than 3000 MWh of unserved energy by winter 2014. | Proposed | 2017-06-01 | 19 | Section 5.2.5.1. This project has undergone the first phase of the RIT-T consultation process. | Outside the scope of the 2012 NTNDP
Section 5.2.5.6.4 | Waddamana–Palmerston 220 kV Transmission Security. The preferred option comprise of converting the existing Waddamana–Palmerston 110 kV line to 220 kV operation, and reconfigure the Waddamana 220 kV substation | A 220 kV tower failure would result in a major supply failure and could result in a blackout of the southern network under some scenarios. This could result in more than 3,000 MWh of unserved energy. In addition to this issue, the parallel 110 kV circuit under this contingency could create transient stability between northern and southern generators, resulting in the entire Tasmanian system becoming unstable. | Proposed | 2019-06-01 | 20 | Section 5.2.5.5. Was proposed to be completed in June 2016. | Outside the planning criteria applied in constraint assessment in the 2012 NTNDP.
Section 5.2.5.6.5 | Voltage support for the greater Hobart area Preferred option: installing two 40 MVAr 110 kV capacitor banks at Creek Road Substation (2015); and Installing -100/+100 MVAr static synchronous compensator (2018) | Investigations reveal that static reactive support is required before the winter of 2015 and thereafter additional dynamic reactive support is required before the winter of 2018. | Proposed | June 2015 and December 2018 | 34.75 | Section 5.2.5.6. | Outside the scope of the 2012 NTNDP
Section 5.2.5.6.9 | Capacity of Bridgewater 110/11 kV Supply Transformers Preferred option: Installing two 30/60 MVA 110/33 kV transformers at Bridgewater Substation complete with 110 kV and 33 kV infrastructure to supply new 33 kV sub-transmission. | The loss of a transformer could result in more than 300 MWh of unserved energy by 2022 | Proposed | Not specified in APR | 16 | Not in 2011 APR | Outside the scope of the 2012 NTNDP