## Index
National Transmission Network Development Plan (NTNDP)
Electronic Material – Consolidated summary 2015 Transmission Annual Planning Report (TAPR) augmentations
This supplement provides:
* A consolidated summary of the augmentations proposed by each TNSP in their 2015 TAPRs and how the main grid augmentations relate to the NTNDP
Please note that the data format may need to be adjusted in order to view the data to the level of fidelity required. For example, you may need to format the cell to a more appropriate number of decimal places in some cases as desired.
Index Table
Tab Name | Content Description
Powerlink 2015 TAPR Projects | List of projects from the 2015 Powerlink TAPR1
TransGrid 2015 TAPR Projects | List of projects from the 2015 TransGrid TAPR2
AEMO 2015 TAPR Projects | List of projects from the 2015 AEMO Victorian TAPR3
ElectraNet 2015 TAPR Projects | List of projects from the 2015 ElectraNet TAPR4
TasNetworks 2015 TAPR Projects | List of projects from the 2015 TasNetworks TAPR5
1 | Powerlink. Available https://www.powerlink.com.au/About_Powerlink/Publications/Transmission_Annual_Planning_Reports/Documents/2015/Transmission_Annual_Planning_Report_2015_(complete_report).aspx
2 | TransGrid. Available https://www.transgrid.com.au/news-views/publications/transmission-annual-planning-report/Documents/Transmission%20Annual%20Planning%20Report%202015.PDF
3 | AEMO. Available http://www.aemo.com.au/Electricity/Planning/~/media/Files/Electricity/Planning/Reports/VAPR/2015/2015_Victorian_Annual_Planning_Report.ashx
4 | ElectraNet. Available http://www.electranet.com.au/assets/Reports-and-Papers/2015-Transmission-Annual-Planning-Report.pdf
5 | TasNetworks. Available http://www.tasnetworks.com.au/TasNetworks/media/pdf/our-network/2015-Annual-Planning-Report.pdf

## Powerlink 2015 TAPR Projects
2015 APR Reference |  | Transmission Development | Limitation Addressed | 2015 APR Project Status | 2015 APR Anticipated Timing | 2015 APR Indicative Cost ($ million) | 2014 APR Reference | 2015 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Section 3.2 | Table 3.1 | Construct Columboola–Wandoan South 275 kV line, Columboola–Western Downs 275 kV line, Wandoan South 275 kV substation, and Columboola 275 kV substation. | Increase supply capability to the Surat Basin north west area | Commissioned | 2014-09-01 | Not stated. | Section 3.2 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable
|  | Build Western Down–Halys 275 kV lines and Western Down and Halys 275 kV substations. | Increase supply capability between Bulli and South West zones | Commissioned | 2014-09-01 | Not stated. | Section 3.2 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable
| Table 3.1 & Section 4.2.3 | Supply to Bowen Basin coal mining area. Committed Solution: 1. install two 132kV capacitors at Dysart Substation and one 132kV capacitor at Moranbah and Newlands substations by summer 2013/14; and 2. network support services between 2014 and 2016. | Voltage and thermal limitations in the Bowen Basin coal mining area due to potential mining growth. | Committed | Winter 2013 to Summer 2016/17 | Not stated. | Section 5.2.1 Section 3.2 | Local supply need based on future loads - not within the 2015 NTNDP scope. | Local Network | Potential local generation support and demand side management initiatives.
|  | Establishment of two new 132kV feeder bays at Pioneer Valley Substation to turn-in the Nebo to Mackay 132kV circuit. | Increase voltage stability in Mackay | Committed | Summer 2015/16 | Not stated. | Section 5.2.1 Section 3.2 | Local supply need based on future loads - not within the 2015 NTNDP scope. | Local Network | Not applicable (network solution being implemented
| Table 3.3 | Aurizon 132 kV rail connection (Wotonga) | New connection to supply rail load in the Bowen Basin area | Committed | winter 2015 | Not stated. | NA | Included in the 2015 NTNDP studies. | Local Network | Not applicable
|  | APLNG / GLNG Wandoan South connections | New connection for CSM/LNG compression | Committed | Winter 2015 to Summer 2015/16 | Not stated. | NA | Included in the 2015 NTNDP studies. | Local Network | Not applicable
| Table 3.4 | Collinsville to Proserpine 132 kV partial line replacement | Condition based replacement. Maintain supply reliability to Proserpine Substation. | Commissioned | 2014-10-01 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Gladstone Substation replacement Works for provision of shared network function were completed 2012. Works associated with generation connection are to be coordinated with outages at Gladstone Power Station. | Condition based replacement. Maintain supply reliability in the Gladstone zone. | Commissioned | 2014-07-01 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 3.5 | Line refit works on 132 kV transmission line between Woree and Kamerunga substations | Condition based. Maintain supply reliability in the Far North zone. | Committed | Winter 2015 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015NTNDP scope. | Asset Replacement | Not applicable
|  | Ross 275 kV 100MVAr bus reactor | Maintain supply reliability in the Ross zone. | Committed | Winter 2016 | Not stated. | NA | Included in the 2015 NTNDP studies. | Main Grid | Not applicable
|  | Garbutt to Alan Sherriff 132 kV line replacement | Condition based replacement. Maintain supply reliability in the Ross zone. | Committed | Winter 2017 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Nebo 275/132 kV transformer replacements. | Condition based replacement. Maintain supply reliability in the North zone. | Committed | Summer 203/14 to 2017/18 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Collinsville Substation replacement | Condition based replacement. Maintain supply reliability in the North zone. | Committed | Winter 2015 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Proserpine Substation replacement | Condition based replacement. Maintain supply reliability in the North zone. | Committed | Summer 2015/16 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Moranbah 132/66 kV transformer replacement | Condition based replacement. Maintain supply reliability in the North zone. | Committed | Summer 2016/17 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Mackay substation replacement. | Condition based replacement. Maintain supply reliability in the North zone. | Committed | Summer 2017/18 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Nebo primary plant replacement. | Condition based replacement. Maintain supply reliability in the North zone. | Committed | Summer 2019/20 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Rockhampton substation replacement. | Condition based replacement. Maintain supply reliability in the Central West zone. | Committed | Winter 2016 | Not stated. | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Blackwater substation replacement. | Condition based replacement. Maintain supply reliability in the Central West zone. | Committed | Summer 2016/17 | Not stated. | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Moura substation replacement. | Condition based replacement. Maintain supply reliability in the Central West zone. | Committed | Summer 2016/17 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Callide A substation replacement. | Condition based replacement. Maintain supply reliability in the Central West zone. | Committed | Summer 2017/18 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Swanbank B Substation replacement | Condition based replacement. Maintain supply reliability in the Moreton zone. | Committed | Summer 2015/16 | Not stated. | Section 3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission line between Sumner Tee and Richlands Substation | Condition based. Maintain supply reliability in the Moreton zone. | Committed | Winter 2016 | Not stated. | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.1 | Table 4.2 | Line refit works on 132kV transmission line between Kareeya and Chalumbin substations | Condition based. Maintain supply reliability to Kareeya. | Possible | Summer 2017/18 | 8 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Turkinje secondary systems replacement | Condition based. Maintain supply reliability to the Far North zone. | Possible | Winter 2018 | 5 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Kamerunga substation replacement. | Condition based replacement. Maintain supply reliability in the Far North zone. | Possible | Winter 2019 | 27 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.2 | Table 4.3 | Line refit works on 132kV transmission line between Townsville South and Clare South substations | Condition based. Maintain supply reliability to the Ross zone. | Possible | Winter 2018 | 29 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Ingham South 132/66 kV transformer replacement. | Condition based replacement. Maintain supply reliability in the Ross zone. | Possible | Winter 2018 | 11 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Garbutt 132/66 kV transformer replacement. | Condition based replacement. Maintain supply reliability in the Ross zone. | Possible | Summer 2018/19 | 11 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Dan Gleeson Secondary Systems replacement | Condition based replacement. Maintain supply reliability in the Ross zone. | Possible | Summer 2020/21 | 7 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.3 | Table 4.4 | Line refit works on 132kV transmission line between Collinsville North and Proserpine substations | Condition based. Maintain supply reliability to Proserpine. | Possible | Summer 2017/18 | 25 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 132kV transmission line between Eton Tee and Pioneer Valley substation | Condition based. Maintain supply reliability to Mackay Region. | Possible | Summer 2019/20 | 8 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 132kV transmission line between Eton Tee and Alligator Creek substation | Condition based. Maintain supply reliability to Alligator Creek. | Possible | Summer 2018/19 | 12 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 132kV transmission line between Nebo substation and Eton Tee | Condition based. Maintain supply reliability to Mackay Region. | Possible | Summer 2020/21 | 5 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.4 | Table 4.5 | Line refit works on 132kV transmission line between Egans Hill and Rockhampton substations | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2019/20 | 6 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line replacement of the 132kV transmission line between Callide A and Moura substations | Condition based replacement. Maintain supply reliability to Biloela and Moura in the Central West zone. | Possible | Summer 2019/20 | 59 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Calvale and Callide B secondary systems replacement | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2017/18 | 12 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Dysart substation replacement. | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2019/20 | 19 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Dysart transformer replacement (two 132/66 kV transformers) | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2019/20 | 9 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Bouldercombe primary plant replacement | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2019/20 | 41 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Wurdong secondary systems replacement | Condition based replacement. Maintain supply reliability in the Gladstone zone. | Possible | Summer 2019/20 | 10 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Lilyvale primary plant replacement | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2020/21 | 12 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Lilyvale transformer replacement (two of three 132/66kV transformers) | Condition based replacement. Maintain supply reliability in the Central West zone. | Possible | Summer 2020/21 | 13 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.5 | Table 4.6 | Gin Gin substation replacement | Condition based replacement. Maintain supply reliability in the Wide Bay area. | Possible | Summer 2019/20 | 26 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.7 | Table 4.7 | Line refit works on 110kV transmission line between Belmont to Sumner Tee | Condition based. Maintain supply reliability in CBD and Moreton zone. | Possible | Winter 2016/17 | 19 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission line between South Pine to West Darra | Condition based. Maintain supply reliability in CBD and Moreton zone. | Possible | Summer 2016/17 | 13 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission line between Rocklea to West Darra | Condition based. Maintain supply reliability in CBD and Moreton zone. | Possible | Winter 2017 to Summer 2017/18 | 15 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission line between Blackstone to Redbank Plains to West Darra | Condition based. Maintain supply reliability in the Moreton zone. | Possible | Summer 2018/19 | 20 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission line between Blackstone to Abermain | Condition based. Maintain supply reliability in the Moreton zone. | Possible | Summer 2019/20 | 17 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 275 kV transmission line between Karana Tee to Bergins Hill to Belmont | Condition based. Maintain supply reliability in the Moreton zone. | Possible | Winter 2020 to Summer 2020/21 | 28 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 275 kV transmission line between South Pine to Karana Tee | Condition based. Maintain supply reliability in the Moreton zone. | Possible | Summer 2020/21 | 16 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Belmont 275 kV secondary system replacement | Condition based. Maintain supply reliability in CBD and Moreton zone. | Possible | Winter 2019 | 9 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Belmont 275/110 kV transformer replacement | Condition based. Maintain supply reliability in CBD and Moreton zone. | Possible | Summer 2019/20 | 11 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Palmwoods 275 kV Substation primary and secondary replacement | Condition based replacement. Maintain supply reliability in the Moreton zone. | Possible | Summer 2019/20 | 25 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Ashgrove West substation replacement | Condition based replacement. Maintain supply reliability in the Moreton zone. | Possible | Summer 2019/20 | 30 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Redbank Plains primary plant replacement | Condition based replacement. Maintain supply reliability in the Moreton zone. | Possible | Summer 2020/21 | 8 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Abermain secondary systems replacement | Condition based replacement. Maintain supply reliability in the Moreton zone. | Possible | Summer 2020/21 | 7 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.8 | Table 4.8 | Line refit works on 275 kV transmission line between Greenbank and Mudgeeraba substations | Condition based. Maintain supply reliability to the Gold Coast zone. | Possible | Summer 2018/19 | 53 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 275 kV transmission line between Mudgeeraba and Terranora substations | Condition based. Maintain reliable interconnection to NSW | Possible | Summer 2020/21 | 13 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Mudgeeraba 110 kV substation primary and secondary replacement. | Condition based replacement. Maintain supply reliability in the Gold Coast zone. | Possible | Summer 2017/18 | 18 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Mudgeeraba 275/110 kV transformers replacement | Condition based replacement. Maintain supply reliability in the Gold Coast zone. | Possible | Summer 2017/18 | 11 | Section 5.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.4.4 | Table 4.11 | Mt Emerald Windfarm connection point | New windfarm near Atherton | Possible | 2017/18 | NA | NA | Connection point proposal | Connection | Not applicable
|  | Clare PV connection point | New solar farm near Clare | Possible | Mid 2017 | NA | NA | Connection point proposal | Connection | Not applicable
|  | New coal mine / CSG 132 kV connections | New industrial plant connections in the Bowen Basin area | Possible | Progressively from summer 2018/19 | NA | NA | Connection point proposal | Connection | Not applicable
|  | Multiple new coal mine 132 kV connections | New industrial plant connections in the Galilee Basin area | Possible | Progressively from summer 2018/19 | NA | NA | Connection point proposal | Connection | Not applicable
|  | Multiple upstream gas compression facilities connections | Multiple new connections for coal seam methane (CSM) / LNG compression facilities in the Surat Basin north west area | Possible | Progressively from summer 2018/19 | NA | NA | Connection point proposal | Connection | Not applicable
Section 6.2.1 | NA | Supply to Bowen Basin coal mining area. Options include: • installation of a 132 kV capacitor bank at Proserpine Substation • installation of a second 275/132kV transformer at Strathmore Substation; and • turn-in to Strathmore substation the second 132 kV circuit between Collinsville North and Clare South substations • 132 kV phase shifting transformers to improve the sharing of power flow in the Bowen Basin within capability of existing transmission assts. | There have been several proposals for new coal mining, LNG and port expansion projects in the Bowen Basin area. These loads could cause voltage and thermal limitations impacting network reliability. | Possible | Timing subject to commitment of additional load. | Not stated. | Section 5.2.1 Section 6.2.1 | Local supply need based on future loads - not within the 2015 NTNDP scope. | Local Network | Potential local generation support and demand side management initiatives.
Section 6.2.2 | NA | Supply to Galilee Basin coal mine area • installation of capacitor banks at Lilyvale Substation • installation of a third 275 kV circuit between Broadsound and Lilyvale substations • staged construction of a western 275 kV transmission corridor as part of a broader development strategy | There have been several proposals for new coal mining projects in the Galilee Basin that have not reached the required development status to be included in the medium economic outlook for the 2015 TAPR. These loads could cause voltage and thermal limitations impacting network reliability. | Possible | Timing subject to commitment of additional load. | Not stated. | Section 6.2.2 | Possible future project subject to customer commitment- not captured in the 2015 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.2.3 | NA | Central Queensland to North Queensland grid section transfer limit: 1. Following the string of the second circuit of a double circuit Stanwell–Broadsound 275 kV line, voltage and thermal limitations may reoccur. Options to address the emerging limitations could vary depending on the level of load commitment. • SVC at existing northern Queensland substations • installation of series capacitors on the CQ–NQ grid sections, and/or • the construction of new transmission lines and/or series capacitors 2. An alternative is to establish a western 275kV corridor connecting Calvale and Lilyvale substations via Blackwater substation. | There have been several proposals for large mining and metal processing or other industrial loads in northern Queensland. These loads include large coal mine developments in Galilee Basin, expansion or development of coal mines and upstream liquefied natural gas (LNG) processing load in the Bowen Basin. The development status of these loads is not yet at the stage that they can be included (either wholly or in part) in the medium economic forecast of the APR. These loads could be up to 1,500MW. Thermal and voltage limitations will occur if even a portion of these new loads commit. | Possible | Timing subject to customer commitment. | Not stated. | Section 6.2.3 Appendix E | Possible future project subject to customer commitment- not captured in the 2015 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.2.4 & Section 4.4.3 (Table 4.10) | NA | Supply to the Surat Basin north west area • Installation of a capacitor banks and/or SVC; or • construction of third 275kV transmission line | There have been several proposals for additional LNG upstream processing facilities and new coal mining load in the Surat Basin north west area. These loads have not reached the required development status to be included in the medium economic forecast for this TAPR. The loads could be up to 400MW and cause voltage and thermal limitations impacting network reliability on the transmission system upstream of their connection points | Possible | Beyond 5yr Outlook | Not stated. | Section 5.2.3 | Possible future project subject to customer commitment- not captured in the 2015 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.3.1 | NA | Ross zone: A potential reconfiguration option consists of: • a line refit of Collinsville North to King Creek substations • decommission the circuit section between King Creek to Clare South substations • install a second 275/132 kV transformer at Strathmore substation • establish 275 kV injection into Clare South substation | The network between Collinsville and Townsville comprises of a 132 kV network and a 275 kV network which operate in parallel. The 132 kV lines are approaching end of technical life between 2019 and 2028, while the earliest end of technical life trigger for the 275 kV lines is beyond 10 years. | Possible | Between 5 to 10 years | Not stated. | NA | Condition based renewals - not within the 2015 NTNDP scope. | Main Grid | Not applicable
Section 6.3.2 | NA | Central West and Gladstone zones: • Decommissioning the 132 kV double circuit line between Callide and Gladstone South substations may impact reliability of supply to the Central West zone. The installation of a second 275/132 kV transformer at Calvale substation can address this impact. • The 132 kV double circuit line operates in parallel with the 275 kV Gladstone grid section. The removal of these circuits from service may therefore impact market dispatch outcomes. Recovering the lost capacity could be achieved by establishing new transmission assets between the Central West and Gladstone zones and/or investment within the Gladstone zone. | Condition based risks on the double circuit 132 kV line between Callide and Gladstone South substations. | Possible | Between 5 to 10 years | Not stated. | NA | Condition based renewals - not within the 2015 NTNDP scope. | Local Network / Main Grid | Not applicable
Section 6.3.3 | NA | Central Queensland to South Queensland grid section: Reconfiguration of the CQ - SQ coastal corridor: • Staged line refit of a sub-set of the existing circuit transmission lines between Calliope River and South Pine substations, or • An alternative is to allow the existing circuits to remain in-service until end of technical life, which would allow a staged rebuild of the coastal corridor as a new double circuit 275 kV transmission line. | Three single circuit 275 kV transmission lines operate in parallel between Calliope River and South Pine substations and form the coastal corridor of the Central QLD to South QLD grid section. These single circuit 275 kV lines will reach end of technical life in 5 to 10 years. - the 275 kV lines at the northern end of this corridor are currently tracking to a higher rate of corrosion and it's expected acceptable risk levels will be exceeded by 2022. The higher rate of corrosion is due to the proximity to the coast. | Possible | Between 5 to 20 years | Not stated. | NA | Condition based renewals - not within the 2015 NTNDP scope. | Main Grid | Not applicable

## TransGrid 2015 TAPR Projects
2015 APR Reference |  | Transmission Development | Limitation Addressed | 2015 APR Project Status | 2015 APR Anticipated Timing | 2015 APR Indicative Cost ($ million) | 2014 APR Reference | 2015 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Section 5.3.1 |  | Redevelopment of Orange 132/66 kV Substation | Condition based replacement of Orange 132/66 kV Substation | Committed | 2017-04-01 | 34.578 | 6.2.11 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Strategic Land Acquisition at Riley Street | For replacement of Haymarket substation around 2041 | Committed | NA | 20.8485 | 7.2.2.3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Upper Tumut Switching Station Rehabilitation | Replacement of the secondary systems is programmed for completion progressively through to January 2015 | Committed | 2015-12-01 | 46.782 | 6.2.2.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Cooma Substation Replacement | A new Cooma 132/66 kV Substation will be established in close proximity to the existing substation. The existing Cooma Substation will be transferred to Essential Energy and converted to a 66/11 kV substation. | Committed | 2015-11-01 | 40.68 | 6.2.2.3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Yanco Substation Refurbishment | The majority of the substation’s equipment is nearing the end of its serviceable life and will be replaced to maintain reliability of supply. | Committed | 2015-09-01 | 19.323 | 6.2.2.4 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Implement dynamic line ratings based on information obtained from weather stations | This is a market driven project which aims to capture market benefits arising from increased line ratings should favourable weather conditions occur. | Committed | mid 2016 | 6.102 | 6.3.3.1 | No impact on 2015 NTNDP studies | Main Grid | Not applicable
|  | Quality of Supply Monitoring | This project is so that they can measure, record and analyse aspects of the quality of supply at these customer connection points. | Committed | 2016-12-01 | NA | 6.3.3.3 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
|  | Replace circuit breakers of shunt capacitor banks with point-on-wave closing control. | This project is needed to avoid the mal-operation or failure of customer equipment | Committed | 2018-01-01 | 5.085 | 6.3.3.4 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 5.3.2 | Table 5.5 | Provision of a 66 kV Line Switch bay at Beryl 132/66 kV Substation | Essential Energy plans to reinforce its network supplying Dunedoo and Coonabarabran. | Committed | 2015-09-01 | 1.017 | 7.2.2.9 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
|  | Provision of a 66 kV Transformer switch bay at Molong 132/66 kV Substation | The old Molong 66/11 kV substation needs to be retired due to its condition. | Committed | 2015-12-01 | 1.017 | 7.2.2.10 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
|  | Provision of a new 132 kV Line switch bay at Vineyard 330/132 kV Substation | The new precinct at Marsden Park does not have an existing electricity supply. Endeavour Energy has determined that a new 132 kV feeder from Vineyard is the preferred option to provide supply to a new area. | Committed | 2015-12-01 | 2.034 | 7.2.2.11 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
| Table 5.6 | Replacement of equipment at Sydney West 330/132 kV substation to ensure that the 132 kV fault rating is at least 38 kA | The existing fault level at Sydney West 132 kV switchyard is approaching the design fault level rating. | Committed | 2015-12-01 | 5.085 | 7.2.2.12 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 5.7 | Beaconsfield Transformer No 1 & No 2 replacement | Condition based replacement of one transformer, the other will not be replaced | Committed | Expected completion 2018 | 37.629 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
|  | Buronga 220 kV Substation - Replacement of X2 220 kV Reactor | Condition based replacement | Committed | summer 2015/16 | 5.085 | 6.3.9 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Broken Hill 220/22 kV Substation - Replacement of No 1 and No 2 Reactors | Condition based replacement | Committed | winter 2016 | 9.153 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 5.8 | Orange 132/66 kV Substation Capacitors - Additional 66 kV capacitor bank | To be provided as part of condition based replacement works. | Committed | 2017-04-01 | NA | 6.2.6 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
| Table 5.9 | Armidale 330/132 kV substation: SVC control system replacement | Condition based replacement | Committed | late 2015 | NA | 6.2.7 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Tamworth 132/66 kV substation: substation rebuild | Condition based replacement; the new substation is to be constructed on an adjacent site with two 120 MVA 132/66 kV transformers and with no 132 kV busbar initially | Committed | 2017-03-01 | NA | 6.2.7 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Kangaroo Valley 330 kV substation: Secondary System Replacement | Condition based replacement | Committed | 2016-02-01 | 6.102 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Sydney West 330/132 kV substation | Condition based replacement; replacement of the secondary systems | Committed | 2015-12-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Sydney North Secondary System Replacement | Condition based replacement | Committed | late 2018 | 42.714 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Sydney South 330 kV Substation - Replacement of all 415 V AC auxiliary supply systems | Condition based replacement | Committed | 2015-11-01 | 6.102 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Haymarket 330 kV substation - removal of SICAM (control and monitoring system) from GIS | Condition based removal | Committed | 2017-04-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Albury 132/22 kV substation: Secondary Systems Replacement | Condition based replacement | Committed | late 2016 | 11.187 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Burrinjuck to Yass 132 kV Transmission Line 970 Pole Replacements & installation of OPGW) | Condition based replacement | Committed | Expected completion 2016 | 13.221 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 5.4.1 |  | Replacement of the Vales Point 330/132 kV substation | The replacement of Vales Point Substation is driven by the condition of the substation and its assets. The asset condition is based on assessments and testing carried out on the physical assets. A reduction in load would not defer the retirement dates. | Proposed | Expected completion: 2018 | 44.748 | 7.2.2.7 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
|  | Development of southern supply to the ACT: - Condition of licence is to provide two geographically separate 330 kV supplies to the ACT - The first of which is the existing Canberra 330/132 kV substation - Establishment of a switching station at a suitable site together with associated 330 kV line connections - After review by the ACT gov, a site near Stockdill Drive is preferred | Jurisdictional reliability requirement | Proposed | Required by 2020 | Not Available |  | Local Area Limitation - Not within scope of NTNDP | Main Grid | Not applicable
|  | Wagga 132/66 kV substation: - replacement of No 1 and 3 132/66 kV 60 MVA transformers with 132/66 kV 120 MVA transformers - remove existing No 2 transformer - replace equipment identified as nearing end of serviceable life | Asset Condition – Condition assessments of Wagga 132 kV Substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed. This includes the No 2 and No 3 132/66/11 kV transformers. | Proposed | Expected completion: 2018 | 52.884 | 7.2.3.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
|  | Supply to Beryl/Mudgee area: The provision of additional reactive support at Beryl substation by the addition of a 66 kV capacitor | voltage stability limitation in the network supplying Beryl is expected to emerge by summer 2015/16 | Proposed | Indicative date: summer 2016/17 | 2.034 | 7.2.2.6 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 5.5.1 | Table 5.10 | Taree Substation 33 kV Switchyard Condition | Condition based replacement | Proposed | 2017-09-01 | 9.153 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Taree 132/66/33 kV Substation: Secondary Systems Condition | Condition based replacement | Proposed | 2017-09-01 | 26.442 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Haymarket 330 kV Substation Secondary Systems Replacement | Condition based replacement | Proposed | Expected completion: 2018 | 9.153 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Cooma – Munyang 132 kV Line 97K Rehabilitation | Condition based replacement | Proposed | Indicative date: 2018 | 15.255 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Coffs Harbour – Koolkhan 132 kV transmission line: pole replacements - Line 96H | Condition based replacement | Proposed | Indicative date: 2017 | 14.238 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 6.2.1 |  | Installation of a Phase Shifting Transformer in the Tamworth-Gunnedah line 969 | Thermal constraints on 969 line when there is an outage of 968 line | Proposed | possible within 5 years | 15 | 7.2.1.1 | Local Area Limitation - Not within scope of NTNDP | Local Network | Potential local generation support and demand side management initiatives.
Section 6.2.2 |  | Replacement of the Tamworth No 2 330/132 kV transformer with a 375 MVA unit (reduce Tamworth Tx from 3 to 2)` | Condition based replacement; No 2 330/132 kV 150 MVA transformer is nearing the end of its serviceable life. | Proposed | Indicative date: 2019 | 11 | 7.2.1.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 6.2.3 |  | Sydney South - Beaconsfield capacity: - preferred option is to perform a detailed assessment of the cable installation by testing oil samples at a large number of points along the entire cable route, installing soil property and condition monitors. | Recent investigations into the condition of cable 41 have found that the cable backfill has degraded, reducing the thermal performance of the cable | Proposed | Within 5 Years | 0.5 - 3 (Montoring System only) | 7.2.2.2 | Due to the noted cable degradation issues, it is likely that there is a need to monitor cable performance to secure supply to the Sydney metropolitan area. | Main Grid | It is not expected that the required levels of demand management would be available to cover the loss of cable 41 capacity, particularly as this would be required in addition to demand management being sought to compensate for the expected 132 kV cable retirements.
Section 6.2.4 |  | Connection of Ausgrid’s new sub transmission substation in the Munmorah/Doyalson area | Supply to Munmorah/Doyalson once the present 33 kV supply from Munmorah power station is no longer available | Proposed | Indicative date: 2017 | NA | 7.2.2.5 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 6.2.5 |  | Replacement of the Munmorah 330/132 kV substation in piecemeal fashion | Condition assessment of Munmorah Substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed. | Proposed | Indicative date: 2020 | 9 | 7.2.2.6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 6.2.6 |  | Replacement of Canberra 330/132 kV substation in piecemeal fashion | Asset Condition – Condition assessments of Canberra Substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed | Proposed | Indicative date: 2019 | 30 | 7.2.3.3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 6.2.7 |  | Condition of Burrinjuck 132/11 kV substation: - connect line 970, line 992 and the Burrinjuck power station in a tee-connection, and decommission the portion of the Burrinjuck substation owned by TransGrid | Asset Condition – Condition assessments of Burrinjuck substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed. | Proposed | Indicative date: 2017 | 7 | 7.2.3.4 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 6.2.8 |  | Complete the communication link works and commission the NSW-Muraylink runback scheme | Reliability issues in northern Victoria and South Australia | Proposed | Indicative date: 2015 | NA | 7.2.3.2 | No impact on 2015 NTNDP studies | Main Grid | Not applicable
Section 6.2.9 |  | Implement a combination of SCADA and protection optimised multiple contingency schemes to protect the NSW power system from potential cascading failure | This is a regulatory obligation driven project. This project mitigates the impact of multiple contingency events which result in voltage instability. | Committed | 2020/2021 | 9.3 | 6.3.3.2 | No impact on 2015 NTNDP studies | Main Grid | Not applicable
Section 6.2.10 | Table 6.1 | Provision of a New 132 kV switch bay at Williamsdale 330/132 kV Substation | When the Googong town load grows sufficiently, it will require a second 132 kV supply | Proposed | Indicative date: 2018 | 1.017 | 7.2.3.6 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 6.2.11 | Table 6.2 | Sydney North – Tuggerah Line 21 Tower Life Extension | Condition based replacement | Proposed | Indicative: 2017 | 5 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | 959/92Z Sydney North – Sydney East 132 kV transmission line : tower life extension | Condition based replacement | Proposed | Indicative date: 2019 | 8.5 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Deniliquin 132/66 kV substation: Secondary Systems Replacement | Condition based replacement | Proposed | Indicative date: 2019 | 10 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | ANM 132 kV substation: Secondary System Replacement | Condition based replacement | Proposed | Indicative date: 2019 | 6 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | 1 and 2 Snowy – Yass/Canberra 330 kV transmission lines remediation | Condition based replacement | Proposed | Indicative date: 2019 | 29 | 7.2.3.1 and 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Low Span Northern Tower Lines Remediation - Central Coast Hunter Valley Northern NSW | Remedial works to restore conductor clearances on 137 spans across 12 330 kV transmission lines in the northern region | Proposed | Indicative date: 2018 | 4 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Low Span Northern Pole Lines Remediation - Central Coast Hunter Valley Northern NSW | Remedial works to restore conductor clearances on 263 spans across 14 132 kV transmission lines in the northern region | Proposed | Indicative date: 2018 | 8 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Low Span Central Tower Lines Remediation - NSW metropolitan area | Remedial works to restore conductor clearances on 151 spans across 13 330 kV transmission lines in the central region | Proposed | Indicative date: 2019 | 2 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Low Span Central Pole Lines Remediation - Central West NSW | Remedial works to restore conductor clearances on 152 spans across 10 132 kV transmission lines in the central region | Proposed | Indicative date: 2019 | 3.7 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Low Span Southern Tower Lines Remediation - Southern NSW | Remedial works to restore conductor clearances on 45 spans across 11 330 kV transmission lines in the southern region | Proposed | Indicative date: 2019 | 3 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Low Span Southern Pole Lines Remediation - Southern NSW | Remedial works to restore conductor clearances on 150 spans across 14 132 kV transmission lines in the southern region | Proposed | Indicative date: 2019 | 5 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Sydney North to Vales Point 330 kV Transmission Line Tower Life Extension | Condition based replacement | Proposed | Indicative date: 2017 | 9 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Murrumburrah 132 kV Substation Secondary Systems Replacement | Condition based replacement | Proposed | Indicative date: 2020 | 5 | 7.2.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
|  | Hume 132 kV substation secondary systems replacement in Southern NSW | Replacement of the secondary systems | Proposed | Indicative date: 2019 | 7 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 6.3.1 |  | Upgrade Queensland – NSW Interconnector (QNI) Transmission Capacity | This is a market benefit driven project | Regulatory consultation completed | Limitation will be reviewed in 5 - 10 years | 72.207 | 7.1.1 | The least cost modelling does not identify the need to increase the NSW-QLD transfer capability. | Main Grid | Not applicable
Section 6.3.2 |  | Develop new breaker and a half switch yards for Tamworth and Armidale 330/132 kV substations | This project is market benefit driven and is contingent on QNI being upgraded | Proposed | Between 5 to 10 years | NA | 7.3.1.1 | No impact on 2015 NTNDP studies | Main Grid | Not applicable
Section 6.3.3 |  | Hunter Valley - Tamworth - Armidale 330 kV system: Upgrade the capacity of the 330 KV transmission lines between Liddell and Tamworth through uprating lines or building new 330 kV transmission lines | This project is market benefit driven and is contingent on QNI being upgraded and new generation being connected in northern NSW. | Proposed | Between 5 to 10 years | NA | 7.3.1.2 | The need to increase the capacity of the Hunter Valley – Tamworth – Armidale 330 kV lines does not arise during the NTNDP outlook period. | Main Grid | Not applicable
Section 6.3.4 |  | Install new capacitors in northern NSW at Dumaresq, Armidale, and Tamworth or an SVC in the area. | This project is market benefit driven and is contingent on QNI being upgraded | Proposed | Between 5 to 10 years | NA | 7.3.1.3 | The least cost modelling does not identify the need to increase the NSW-QLD transfer capability. | Main Grid | Not applicable
Section 6.3.5 |  | Powering Sydney's Future: preferred option is to establish two new 330 kV cables between Rookwood Road and Beaconsfield West connected and operated at 132 kV, in conjunction with Ausgrid’s replacement of the 132 kV cables supplying the Surry Hills area | Limitations in supplying the inner Sydney area : - Retirement of Ausgrid 132 kV cables - De-rating of 330 kV cable 41 - De-rating of 132 kV cables - Sydney Load growth | Proposed | limitation is not expected to arise for 5 - 10 years | 70.173 | 7.2.2.1 | Limitation was identified within first 5 years of NTNDP study. The limitation is sensitive to changes in local demand and network capability. The timing of the limitation will change if there is a material change to local demand and network capability. | Main Grid | demand management to defer or, if possible, avoid one or both of these cables would be implemented if practical and cost-effective.
Section 6.3.6 |  | Rebuild Newcastle Substation: The preferred network option is to rebuild Newcastle substation in a piecemeal fashion. | Condition of Newcastle Substation. The need date to address the condition issues at Newcastle is 2020. The substation is required to meet the present and future demand in the area, and provide a focal point for seven 330 kV connections. | Proposed | Between 5 to 10 years | NA | 7.3.2.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 6.3.7 |  | Capacity of the Snowy to Sydney network: Increasing line ratings of line 01, 39, 4 and 5 to 100°C Installing a phase shifting transformer on line 39 Replacing terminal equipment on line 11 at Dapto and Sydney South | Development of new generation in Southern NSW may lead to the 330 kV network between the Canberra/Yass area and Sydney becoming congested | Proposed | Constraint expected to arise in 5 - 10 years | 81.36 | 7.2.3.1 | The need to increase capacity of the network to import power from the Snowy region, or Uranquinty, or from Victoria does not arise in the NTNDP outlook period. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.3.8 |  | Capacity of the Marulan – Avon, Marulan – Dapto and Kangaroo Valley – Dapto lines: Increasing line ratings of line 18 to 100°C operating temperature | Development of new generation in Southern NSW may lead to the 330 kV network between the Canberra/Yass area and Sydney becoming congested | Proposed | Between 5 to 10 years | NA | 7.3.3.1 | The need to increase rating of Marulan – Avon, Marulan – Dapto and Kangaroo Valley – Dapto Lines does not arise during the NTNDP outlook period. | Main Grid | Implementing a special protection scheme (SPS) - generation runback scheme
Section 6.3.9 |  | Provision of capacitor banks at Panorama and Orange 132/66 kV Substations and Orange North 132 kV Switching Station; • Provision of a 132 kV series reactor on the 94X Wallerawang – Panorama 132 kV line and later on the 949 Mt Piper – Orange North 132 kV; and • replacement of 944 line | Condition of Wallerawang-Orange line 944 | Proposed | No preferred option for the long term | 15.255 | 7.2.2.8 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 6.3.10 | Table 6.3 | Beryl 132/66 kV substation: secondary systems replacement | Condition based replacement | Proposed | Indicative date: 2020 | 6 | 7.3.5 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
|  | Armidale Secondary System Replacement | Condition based replacement | Proposed | Deferred to 2021 | 1 | 7.2.5 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
|  | Forbes No 1 and No 2 132/66 kV transformer replacement | Condition based replacement | Proposed | Indicative date: 2021 | 8 | 7.2.5 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
|  | Yanco – Griffith 132 kV Line 99J Rebuild | Condition based replacement | Proposed | Indicative date: 2022 | 18 | 7.2.5 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 6.4.1 |  | Reinforce supply to the Halidays Point area by either: • Local generation and/or demand management • Reinforcing the existing Essential Energy network by providing an additional line from Taree or uprating the existing lines, or • The construction of a 132/66 kV substation in the Hallidays Point area. | The load in the Forster/Tuncurry area is approaching the capacity of Essential Energy’s 66 kV network supplying the area from Taree | Proposed | Limitation not expected within 10 years | Not Available | 7.3.1.4 | Local Area Limitation - Not within scope of NTNDP | Local Network | Potential local generation support and demand side management initiatives.
Section 6.4.2 | Table 6.4 | Lismore - two 132 kV switch bays | Distributor requirements | Proposed | Beyond 2024 | Not Available | 7.3.4 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
|  | Tamworth 132/66 kV substation - one 66 kV switch bay | Distributor requirements | Proposed | Beyond 2024 | Not Available | 7.3.4 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
|  | Tumut 132/66 kV substation - one 66 kV switch bay | Distributor requirements | Proposed | Beyond 2024 | Not Available | 7.3.4 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable

## AEMO 2015 APR Projects
2015 APR Reference |  | Transmission Development | Limitation Addressed | 2015 APR Project Status | 2015 APR Anticipated Timing | 2015 APR Indicative Cost ($ million) | 2014 APR Reference | 2015 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Chapter 2 | Section 2.1 | Options include: • Cut-in the Rowville–Richmond 220 kV No.1 and No.4 circuits at Malvern terminal station to form the Rowville–Richmond–Malvern No.3 and No.4 circuits | Thermal capacity of the Rowville–Malvern 220 kV No.1 and 3 circuits | Monitored (refer Section 1.1 & DSN Limitation Detail Workbook supplementary information) | Beyond 10 year outlook | $10.4 million | Section 3.2.6 | Existing control scheme for post-contingent load reduction and new wind monitoring scheme are modelled. | Main Grid | Demand management or new generation at Malvern Terminal Station as an alternative to existing operational arrangement of post-contingent load reduction.
| Section 2.1 | Options include: • Install a third 220 kV line between Rowville and Springvale. | Thermal capability of Rowville–Springvale and Springvale–Heatherton 220 kV circuits. | Monitored (refer Section 1.1 & DSN Limitation Detail Workbook supplementary information) | Beyond 10 year outlook | $52 million | Section 3.2.6 | Existing control scheme for post-contingent load reduction and new wind monitoring scheme are modelled. | Main Grid | Demand management or new generation at Springvale and/or Heatherton terminal stations as an alternative to existing operational arrangement of post-contingent load reduction.
| Section 2.1 | Options include: • Install a phase angle regulating transformer on the Bendigo–Fosterville–Shepparton 220 kV line. • Replace the existing Dederang–Glenrowan 220 kV lines with a new double circuit line. • Replace the existing Dederang–Shepparton 220 kV line with a new double circuit line. | Thermal capacity of Dederang–Shepparton 220 kV line | Monitored (refer Section 1.1 & DSN Limitation Detail Workbook supplementary information) | Beyond 10 year outlook | $44.2 million - $253 million | Section 3.2.6 | Not identified | Main Grid | Demand management or new generation at Shepparton Terminal Station
| Section 2.1 | Options include: • Install a second 500/220 kV 1000 MVA transformer at Cranbourne. | Thermal capacity of Rowville A1 500/220 kV transformer loading | Monitored (refer Section 1.1 & DSN Limitation Detail Workbook supplementary information) | Beyond 10 year outlook | $38 million | Section 3.2.6 | Not identified | Main Grid | Demand management or new generation in eastern or south-eastern Metropolitan Melbounre area.
| Section 2.2 | Installation of a wind monitoring scheme on the Ballarat–Bendigo 220 kV line. | Thermal capacity limitations on the Ballarat–Bendigo 220 kV line | Completed | Febuary 2015 | NA | Section 3.2.2 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
| Section 2.3 | South Australia–Victoria (Heywood) Interconnector Upgrade Installation of a third 500/275 kV transformer and 500 kV bus-tie at Heywood terminal station | Thermal capacity limitations of the Heywood transformers. | Committed | mid 2016 | NA | Section 3.2.2 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
| Section 2.3 | Installation of a new Moorabool-Ballarat 220 kV circuit on the existing tower | Thermal capacity limitations on Moorabool–Ballarat 220 kV circuits | Committed | early 2017 | NA | Section 3.2.2 | Included in the 2015 NTNDP studies. | Main Grid | RIT-T completed.
| Section 2.3 | Install three 220/66 kV 225 MVA transformers at Brunswick Terminal Station. | Thermal capacity of 220/66 kV transformers at Richmond and West Melbourne terminal stations. | Committed | late 2016 | NA | Section 3.2.2 | Included in the 2015 NTNDP studies. | Local Network | RIT-T completed.
| Section 2.3 & Section 2.4 | New 220 kV Deer Park terminal station with installation of two 225MVA 220/66 kV transformers and connection to Keilor-Geelong 220 kV No.2 circuit. | Thermal capacity limitations on Keilor 220/66 kV transformers. Offload Altona, Brooklyn, and Keilor terminal stations due to increased demand in the area. | Committed | late 2017 | NA | Section 3.2.3 | Included in the 2015 NTNDP studies. | Local Network | RIT-T completed.
| Section 2.3 | An automatic bus-splitting control scheme at Challicum Hills 66 kV substation | Constraints on the Ballarat - Horsham 66 kV (distribution) lines for outage of Horsham-Waubra-Ballarat or Horsham-Red Cliffs 220kV lines: • Assessed line ratings reduced in 2014. They have now been reassessed as higher than originally, however they still have a market impact. | Monitored (refer Section 1.1 & DSN Limitation Detail Workbook supplementary information) | 2015 to 2016 | <$0.3 million | Section 3.2.6 | NA | Local Network | NA
| Section 2.3 | Implementing a 5-minute rating on the Keilor - Deer Park - Geelong 220 kV line or contestable non-network solutions | Constraints on the Keilor - Deer Park - Geelong 220 kV lines: • Customer demand in surrounding areas is forecast to exceed network capacity under peak demand scenarios from early 2020. | Proposed | 2017 to 2020 | NA | Section 3.2.6 | Included in the 2015 NTNDP studies. | Main Grid | Contestable non-network solutions
| "DSN Limitation Detail" Supplementary Information Workbook: Eastern Corridor | A new 500/220 kV transformer at Hazelwood with an estimated cost of $35.3 million plus any fault level mitigation works. Upgrade the 220 kV Hazelwood–Rowville or Yallourn–Rowville lines. | Rowville - Yallourn loading when significant new generation is connected to the Latrobe Valley 220 kV transmission network and/or when there is significant capacity increase in the Hazelwood or Yallourn power stations. | Monitored | post 2024 | see "Transmission Development" column | NA | The NTNDP did not identify this limitation, as no scenario modelled significant capacity increases in either the Hazelwood or Yallourn power stations. | Main Grid | Not applicable.
|  | A new 500/220 kV transformer at Hazelwood with an estimated cost of $35.3 million plus any fault level mitigation works. Upgrade the 220 kV Hazelwood–Rowville or Yallourn–Rowville lines. | Hazelwood 500/220 kV transformer rating when significant new generation is connected to the Latrobe Valley 220 kV transmission network and/or when there is significant capacity increase in the Hazelwood or Yallourn power stations. | Monitored | post 2024 | see "Transmission Development" column | NA | The NTNDP did not identify this limitation, as no scenario modelled significant capacity increases in either the Hazelwood or Yallourn power stations. | Main Grid | Not applicable.
| "DSN Limitation Detail" Supplementary Information Workbook: South West Corridor | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland with an estimated cost of $13.3 million. A static VAr compensator (SVC) or a synchronous static compensator (STATCOM) at an estimated cost of $31 million. Additional transposition towers along the Moorabool–Heywood–Alcoa Portland 500 kV line at an estimated cost of $35.2 million. | Moorabool - Heywood - Portland 500kV line voltage unbalance [1] Sectionalising the Moorabool–Heywood–Alcoa Portland 500 kV line to connect new generation potentially introduces voltage unbalance along the line when a line section is switched out. The impact of voltage unbalance levels increases in proportion to power flow magnitude and direction, new generation connection points, and output generated. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | New dynamic reactive compensation (for example, static VAr compensation) at Heywood or Alcoa Portland with an estimated cost of $31 million. | Voltage instability or collapse during a prior outage of the Heywood–Alcoa Portland 500 kV No.1 line, or for Vic–SA interconnector capacity upgrade to more than 650 MW. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | A new Moorabool–Mortlake/Tarrone–Heywood 500 kV line with an estimated cost of $520 million. | Inadequate South-West Melbourne 500kV thermal capacity when significant wind generation and/or GPG (over 2,500 MW in addition to the existing generation from Mortlake) is connected to the transmission network. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
| "DSN Limitation Detail" Supplementary Information Workbook: Northern Corridor | Installing a new (third) 1,060 MVA 330 kV line between Murray and Dederang with an estimated cost of $173 million (excluding easement costs) or a new (second) 330 kV line from Dederang to Jindera at an estimated cost of $143 million (excluding easement costs). | Murray–Dederang 330 kV line rating with Iincreased NSW import and Murray generation. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Up–rating the two existing lines 82 ºC (conductor temperature) operation and series compensation at an estimated cost of $15.9 million. Installing a new (third) 330 kV, 1,060 MVA single circuit line between Dederang and South Morang with 50% series compensation to match the existing lines, at an estimated cost of $230 million (excluding series capactior cost, easement costs, and subject to obtaining the necessary easement) | Dederang–South Morang 330 kV line rating with Iincreased NSW import and export. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installing a wind monitoring scheme with an estimated cost of $514k or up-rating the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82 ºC, at an estimated cost of $11.7 million. | Dederang–Mount Beauty 220 kV line rating with Iincreased NSW import and export. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installing a wind monitoring scheme at an estimated cost of $514k or up-rating the Eildon–Thomastown 220 kV line, including terminations to 75 ºC operation, at an estimated cost of $42 million. | Eildon–Thomastown 220 kV line rating with Iincreased NSW import and export. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installing a fourth 330/220 kV transformer at Dederang at an estimated cost of $20.4 million. | Dederang 330/220 kV transformer rating Aat times of over 2,500 MW of imports from NSW and Murray generation (with the DBUSS transformer control scheme is active). | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Installing additional capacitor banks and/or controlled series compensation at Dederang and Wodonga terminal stations. | Voltage collapse at South Morang, Dederang, Wodonga, and Jindera with Iincreased NSW import and export. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
| "DSN Limitation Detail" Supplementary Information Workbook: Greater Melbourne and Geelong | New 500/330 kV transformer at South Morang, a Braking resistor at Loy Yang, and uprating of the South Morang–Dederang 330 kV lines. The total cost of these upgrades is expected to be approximately $80 million. The first two components are expected to be contestable. | The South Morang 500/330 kV F2 transformer rating, interconnected system transient stability performance, and the South Morang–Dederang thermal rating jointly limit the export capability from Victoria to New South Wales. | Monitored (refer also Section 2.3) | post 2024 | see "Transmission Development" column | NA | Included in the 2015 NTNDP studies. | Main Grid | Possible non-network solution applicable
|  | Cut-in the Rowville-Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits at an estimated cost of $10.4 million. | Rowville–Malvern 220 kV line rating limits Lload growth or additional loads connected to Malvern Terminal Station. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Connection of a Rowville–Springvale third circuit with an estimated cost of $52 million. | Rowville–Springvale–Heatherton 220 kV line rating limits load growth or additional loads connected to Springvale and Heatherton Terminal Station. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installation of a second 500/220 kV 1,000 MVA transformer at Cranbourne with an estimated cost of $39 million. | Rowville A1 500/220 kV transformer rating limits increased demand in Eastern Metropolitan Melbourne. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Connection of Ringwood Terminal Station to the existing Rowville–Templestowe 220 kV line. | Rowville–Ringwood 220 kV line rating limits load growth or additional loads connected to Ringwood Terminal Station. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | New (third) 500/220 kV transformer at Rowville, with an estimated cost of $39 million, plus any fault level mitigation works. | Ringwood–Thomastown 220 kV line rating limits load growth or additional loads connected to Ringwood Terminal Station. AEMO's Connection Point Forecast indicates that the loading on this line may decrease in the 10 year planning period. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Cut-in the Thomastown–Ringwood 220 kV line at Templestowe, or a new (third) 500/220 kV transformer at Rowville, with an estimated cost of $39 million, plus any fault level mitigation works. | Templestowe–Thomastown 220 kV line rating limits load growth around the Melbourne Metropolitan area. AEMO's Connection Point Forecast indicates that the loading on this line may decrease in the 10 year planning period. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Replacement of the existing (South Morang H1 330/220 kV) transformer with a higher rated unit in conjunction with AusNet Services’ asset replacement program. | South Morang H1 330/220 kV transformer rating limits increased demand in Metropolitan Melbourne and/or increased import from NSW. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | New (third) 500/220 kV transformer at Rowville, with an estimated cost of $39 million, plus any fault level mitigation works. | South Morang–Thomastown No.1 and No.2 220kV line rating limits load growth around the Melbourne Metropolitan area and/or increased export to NSW. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Install a fourth Keilor 750 MVA 500/220 kV transformer at an estimated cost of $38 million. | Keilor 500/220 kV A2 transformer rating limits demand growth in Geelong and the Western Melbourne Metropolitan area. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | A new 500/220 kV transformer at Cranbourne Terminal Station with an estimated cost of $38 million. | Cranbourne A1 500/220 kV transformer rating limits load growth around the Eastern Melbourne Metropolitan area. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
| "DSN Limitation Detail" Supplementary Information Workbook: Regional Victoria | Automatic post-contingent bus splitting scheme at Challicum Hills for outage of the Horsham–Red Cliffs or Ballarat–Horsham 220 kV lines. The total cost of this scheme is estimated to be less than $300k and is being actively pursued by AEMO. | Ballarat–Horsham 66 kV line rating. Preliminary analysis indicates that the Ararat–Challicum Hills 66 kV line section may exceed its emergency cyclic thermal rating for outages on the Horsham–Red Cliffs or Ballarat–Horsham 220 kV lines. The level of overload is dependent on various factors including generation levels, demand and interconnector flows. Other Ballarat–Horsham 66 kV line sections are also being investigated for potential limitations. | proposed | post 2024 | see "Transmission Development" column | NA | NA | Local Network | Not applicable.
|  | Staged installation of additional reactive power support in Regional Victoria. Load reduction or new generation in Regional Victoria, such as Bendigo, Kerang, Fosterville, Red Cliffs and Wemen Terminal Station. | Inadequate reactive power support due to increased demand and/or decrease in power factor in Regional Victoria. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Install a phase angle regulating transformer on the Bendigo–Fosterville–Shepparton 220 kV line at an estimated cost of $44.2 million, or up-rate the existing conductor from 82 ºC to 90 ºC at an estimated cost of $57.6 million. | Bendigo–Fosterville–Shepparton 220 kV line rating may limit increased demand in Regional Victoria and/or increased import from NSW. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Install a phase angle regulating transformer on the Bendigo–Fosterville–Shepparton 220 kV line at an estimated cost of $44.2 million; or replace the existing Dederang–Glenrowan 220 kV lines with a new double circuit line (project cost will be established in 2014–15); or replace the existing Dederang–Shepparton 220 kV line with a new double circuit line at an estimated cost of $253 million. | Dederang–Glenrowan 220 kV line rating may limit increased demand in Regional Victoria and/or increased import from NSW. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Replace the existing Bendigo–Kerang–Wemen–Red Cliffs 220 kV line with a new double circuit 220 kV circuit line at an estimated cost of $570 million. | Kerang–Wemen–Red Cliffs 220 kV line rating may limit significant load growth at the Kerang Terminal Station. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Replace switchgear with plant with higher fault–level capabilities, install series reactors to limit the fault–level contribution of new and existing plant and, if reliably and economically feasible, un–mesh the transmission network. | Increase in fault levels beyond network plant capability. Fault levels are location-based and driven by increased demand and impedance changes from connecting new network plant and generation. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Non-network solution and/or uprate Ballarat-Bendigo 220 kV line at an estimated cost of $42.5 million. | Ballarat–Bendigo 220 kV line rating may limit increased demand in Regional Victoria. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was identified in the NTNDP | Main Grid | Possible non-network solution applicable
| Section 2.4 | Establish a new terminal station at Ararat with possible cut-in to Ballarat - Waubra - Horsham 220 kV line. Approximately 85km from Horsham. | Generation connection of Ararat Wind Farm (242 MW). | Proposed | 2016-07-01 | NA | NA | Included in the 2015 NTNDP studies. | Main Grid | NA
| Section 2.4 | Establish a new substation at Mt Gellibrand with possible line cut-in to Terang - Geelong 66 kV network. | Generation connection of Mt Gellibrand Wind Farm (132 MW) | Proposed | TBA | NA | NA | NA | Local Network | NA
| Section 2.4 | Establish a new terminal station at Stockyard Hill with possible line cut-in to Moorabool - Heywood/Portland 500 kV No.1 or No.2 line. | Generation connection of Stockyard Hill Wind Farm (392.5 MW) | Proposed | TBA | NA | NA | NA | Main Grid | NA
| Section 2.4 | Establish a new terminal station at Crowlands with possible line cut-in to Ballarat - Waubra - Horsham 220 kV line. | Generation connection of Crowlands Wind Farm (123 MW) | Proposed | TBA | NA | NA | NA | Main Grid | NA
Chapter 3 | Section 3 | Moorabool Terminal Station - Replace 500kV and 220kV circuit breakers. | Condition based replacement. | Proposed | 2020 | $8 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| Section 3 | Heatherton Terminal Station - Replace all three 150MVA 220/66 kV transformers, two 220 kV minimum oil CBs, eleven 66 kV bulk old CBs and associated protection and control systems | Condition based replacement. | Committed | 2017 | $59 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution need to be investigated
| Section 3 | Richmond Terminal Station - Replace existing infrastructure with three 225 MVA 220/66 kV transformers, three breaker-and-half 220 kV GIS switchbays, four 66 kV GIS busses, 22 kV switchboard and associated protection and control systems. | Condition based replacement. | Committed | 2018 | $175 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Not applicable (network solution being implemented)
| Section 3 | South Morang Terminal Station - Stage 1 - Replace the H2 transformer with a new 750 MVA 330/220 kV transformer and retain the existing H2 FERRANTI 330/220kV transformer as a cold spare transformer. | Condition based replacement. | Committed | 2018 | $34 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| Section 3 | Fishermans Bend Terminal Station Stage 1- Replace one minimum oil 220 kV CB, six 66kV bulk oil and three 66kV minimum oil CBs. | Condition based replacement. | Committed | 2018 | $17 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 3 | Fishermans Bend Terminal Station Stage 2- Replace B1 and B3 transformers with two 150 MVA 220/66 kV transformers. | Condition based replacement. | Proposed | 2020 | $37 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 3 | Templestowe Terminal Station - Replace B2 220/66 kV transformer, two 66 kV minimum oil CBs and thirteen 66 kV bulk oil CBs, and install new protection and control systems. | Condition based replacement. | Proposed | 2020 | $34 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 3 | West Melbourne Terminal Station - Replace three 150 MVA 220/66 kV transformers (B1, B2 & B3), seven 220 kV switch bays, 16 x 66 kV switch bays, 22 kV switch boards and all protection and control systems with GIS located in buildings. | Condition based replacement. | Committed | 2021 | $119 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 3 | Springvale Terminal Station - Replace B1, B2 and B3 220/66 kV transformers, five 220 kV minimum oil CBs and selected 66 kV CBs. | Condition based replacement. | Proposed | 2021 | $77 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| AusNet Services Asset Renewal Plan | DDTS - Replace the H1 ACEC 225/340MVA 330/220kV transformer | Condition based replacement. | Committed | 2015 | $17 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Latrobe Valley - Replace copper cable with Optical Ground Wire (OPGW) and miscellaneous communication works. XA76 - Replace Copper Supervisory Cables with OPGW - HWPS, MPS, MWTS, JLTS, HWTS and YPS. XA22 - Install OPGW YPS-YWPS 1/2, YPS-YWPS 3/4 and between YWPS Comms Building, X864 - Install 58km of OPGW HWTS-LYPS. | Condition based replacement. | Committed | 2015 | $13 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | MWTS - Replace B2 ASEA transformer with a 150MVA 220/66kV transformer and replace four 66kV single phase CVTs | Condition based replacement. | Committed | 2015 | $8 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| AusNet Services Asset Renewal Plan | RWTS - Replace nine 220kV bulk oil CBs and provide new CB management system | Condition based replacement. | Committed | 2015 | $21 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HWPS - Replace eleven bulk oil CBs | Condition based replacement. | Committed | 2016 | $8 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | YPS - Replace seven minimum oil 220kV CBs and the associated oil CTs | Condition based replacement. | Committed | 2016 | $21 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Transmission conductor replacement - 80km of ground-wire and conductor | Condition based replacement. | Committed | 2017 | $7 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Transmission line insulator replacement on Priority 2 insulators (4385 strings from selected lines with 20mm pins and the rest of 16-mm pin insulators) | Condition based replacement. | Committed | 2017 | $5 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HWPS - Replace the remaining seven 220kV Bulk Oil CBs and install remote operated isolators | Condition based replacement. | Proposed | 2018 | $24 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | RWTS - Replace B4 220/66kV transformer and six 66kV bulk oil CBs | Condition based replacement. | Proposed | 2018 | $16 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| AusNet Services Asset Renewal Plan | Line - Replace glass and porcelain insulator strings and components with composite insulators. | Condition based replacement. | Proposed | 2020 | $6 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | LYPS - Replace 500kV circuit breakers | Condition based replacement. | Proposed | 2021 | $4 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HWTS - Replace 500kV circuit breakers | Condition based replacement. | Proposed | 2021 | $6 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HYTS - Replace two 500kV and two 275 kV CBs | Condition based replacement. | Proposed | 2018 | $8 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | WBTS-HOTS Line - Install 141km of Optical Ground Wire (OPGW) on WBTS-HOTS Line | Condition based replacement. | Proposed | 2022 | $14 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Replace ground wire on selected transmission lines | Condition based replacement. | Proposed | 2022 | $18 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | RCTS-HOTS Line - Install 277km of Optical Ground Wire (OPGW) on RCTS-HOTS Line | Condition based replacement. | Proposed | 2024 | $28 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
Note on D15: [1] Voltage unbalance monitoring equipment is now installed in the area. The data from the equipment will be used to review the magnitude of the limitation and possibly calibrate the simulation model to review the existing constraints. AEMO expects to conduct this review in 2015.
Note on C39: pwoodall: need to add non-network solution (although not in VAPR 2015 for this item).

## ElectraNet 2015 APR Project
2015 APR Reference |  | Transmission Development | Limitation Addressed | 2015 APR Project Status | 2015 APR Anticipated Timing | 2015 APR Indicative Cost ($ million) | 2014 APR Reference | 2015 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Section 3.4 | Table 3-4 | Strengthen Riverland transmission corridor: Rebuild Robertstown – North West Bend – Berri as 275 kV AC double circuit line to increase capacity by >400 MW. Extend network into Victoria or New South Wales, AC or HVDC options available | Reduce losses, support renewable generation, improve export/import capability and enhance reliability to the Riverland in South Australia and Western Victoria. | Potential | Subject to market benefit assessment | 200-400 | Table 7-15 | Limitation may arise during times of high renewable generation in NSA zone. | Main Grid | Not applicable
| Table 3-5 | Strengthen Mid North 275 kV network: Various line uprating and dynamic line ratings dependent on generator developments. | Increase in renewable generation in the Mid North or Eyre Peninsula. Capacity increase depending on the location of generation and local network capability. | Potential | Subject to market benefit assessment | <5 | Table 7-16 | Limitation may arise during times of high renewable generation in NSA zone. | Main Grid | Not applicable
| Table 3-5 | Tie Davenport–Robertstown 275 kV at Belalie substation. | Increased renewable generation on the Mid North network. Capacity increase depending on the location of generation and local network capability. | Potential | Subject to market benefit assessment | 10-20 | Table 7-16 | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
| Table 3-5 | Tie Robertstown–Para 275 kV at Tungkillo substation. | Increased renewable generation on the Mid North network. Capacity increase depending on the location of generation and local network capability. | Potential | Subject to market benefit assessment | 5-10 | Table 7-16 | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
| Table 3-5 | Davenport - Brinkworth - Para 275 kV: Rebuild Davenport–Brinkworth–Para 275 kV as a high capacity 275 kV AC double circuit line with twin conductors. | Increase in renewable generation and loads in the Mid North or Eyre Peninsula. 1200 MW capacity increase. | Potential | Subject to market benefit analysis | 300-400 | Table 7-16 | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
Section 7.9 | Table 7-6 | Munno Para 275 kV Injection: Establish Munno Para substation and install a single 225 MVA 275/66 kV transformer supplying into the Northern Suburbs. | Load growth in the Northern Suburbs overloads SA Power Networks’ 66 kV network. | Committed | June 2015 | 30-35 (ElectraNet costs only) | Table 7-12 | Included in the 2015 NTNDP studies. | Local Network | Not applicable (this project has been completed)
| Table 7-6 | Uprate the Robertstown – North West Bend #1 132 kV line to 100 ˚C line clearances | Robertstown-North West Bend #1 132 kV line overloaded for loss of Robertstown-MWP3-MWP2-MWP1 - North West Bend #2 132 kV line at high demand times, as Western Victorian 220 kV network is unable to support Murraylink transfer into South Australia at times of high Victorian demand | Committed | 2015 | <3 | Table 7-12 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable (network solution being implemented)
| Table 7-6 | Heywood Interconnector Upgrade: Install series compensation on the South East-Tailem Bend 275 kV lines; reconfigure existing 132 kV transmission system between Snuggery, Keith and Tailem Bend; remove rating restrictions from South East 275 kV and 132 kV lines, implement a runback control scheme for Lake Bonney Wind Farm to manage light load and high wind conditions. SP AusNet to install a third 500/275 kV transformer at Heywood. Will raise nominal transfer limits from ±460 MW to ±650 MW. | Heywood Interconnector transfer limitations due to system stability and thermal constraints. | Committed | July 2016 | 40-50 (ElectraNet costs only) | Table 7-12 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
| Table 7-6 | Dalrymple Substation: Install a second 25 MVA 132/33 kVtransformer, extend and reconfigure 132 kV bus. | ETC reclassification to Category 2 required N-1 transformer redundancy at Dalrymple connection point from 1 December 2016 | Pending (RIT-T completed) | Nov 2016 | 14-16 (ElectraNet costs only) | Table 7-12 | Included in the 2015 NTNDP studies. | Local Network | Not applicable ( network solution being implemented)
| Table 7-6 | Weather Stations for Dynamic Line Rating Install modern weather stations at various monitoring locations to facilitate the future implementation of dynamic line ratings on critical circuits | Deterministic line ratings in various parts of the network can cause constraints at times of high demand or high wind generation. | Pending | 2016 | <5 | Table 7-12 | Local supply/network need - not modelled in NTNDP studies. | Local Network | Potential local generation support and demand side management initiatives.
| Table 7-6 | Reactive Plant Control Systems Install a coordinated control scheme to better utilise existing reactive plant and voltage control facilities to minimise system constraints whilst managing system voltage levels | Difficulty with manually controlling the increasing number of reactive plant and voltage control facilities across the Main Grid effectively | Proposed | 2018 | <5 | Table 7-12 | Reactive power support - not modelled in NTNDP studies. | Main Grid | Not applicable
| Table 7-6 | Complete roll out of weather stations at monitoring locations across the network and complete validation of real-time line ratings on specific circuits | Deterministic line ratings in various parts of the network can cause constraints at times of high demand or high wind generation | Proposed | 2018-2023 | <5 | NA | Limitation may arise in various part of transmission network at times of high wind generation. | Main Grid and Local Network | Not applicable
| Table 7-6 | Reinforce the Eyre Peninsula by constructing a double-circuit 275 kV line from Cultana to a location near Yadnarie, initially strung only on one side; establish a 275/132 kV substation near Yadnarie; provide supply to the new mining load(s) via 275 kV and 132 kV supplies from the new substation | Subject to connection of a new large mining load on the Eyre Peninsula, at high demand times the Middleback – Yadnarie 132 kV line will be overloaded under normal conditions and one Cultana 275/132 kV transformer will be overloaded for an outage of the other. | Potential (under SA Mining Growth Scenario) subject to load connection application. | Subject to step load connection | 150-300 | Table 7-12 | Possible future project subject to load connection - not captured in the 2015 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
| Table 7-6 | Reinforce the Yorke Peninsula by constructing a single circuit 275 kV line from Blyth West to Hummocks and install a single 200 MVA 275/132 kV transformer at Hummocks substation | Subject to connection of a new large mining load on the Yorke Peninsula, at high demand times when either the Bungama – Hummocks or the Waterloo – Hummocks 132 kV line is out of service, the other line may be overloaded and it may not be possible to maintain adequate voltage levels on Yorke Peninsula. | Potential (under SA Mining Growth Scenario) subject to load connection application. | Subject to step load connection | 40-55 | Table 7-12 | Possible future project subject to load connection - not captured in the 2015 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
| Table 7-6 | Apply Dynamic Line Ratings to Davenport to Robertstown 275 kV Lines Increase the capacity of the 275 kV lines between Davenport and Robertstown by upgrading various items of plant (e.g. remove line traps, replace current transformers, change current transformer ratios) and apply dynamic line ratings to these lines. | Subject to connection of new wind farms to the 275 kV lines between Davenport and Robertstown, those 275 kV lines may be overloaded at times of high wind generation | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | <5 | NA | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
| Table 7-6 | Increase the capacity of the Robertstown 275/132 kV transformers by upgrading various items of plant and apply short term loading limits to the Robertstown 160 MVA 275/132 kV transformers. | Subject to connection of new wind farms to the 275 kV lines between Davenport and Robertstown, one of the Robertstown 160 MVA 275/132 kV transformers may be overloaded for an outage of the other transformer | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | <5 | NA | Possible future project subject to wind farm development. Not captured in the 2015 NTNDP. | Main Grid | Not applicable
| Table 7-6 | Implement a control scheme that will reconfigure the Mid North 132 kV network at times of high wind farm generation by opening and closing 132 kV circuit breakers as required to target reduced congestion under various operating conditions | Subject to connection of new wind farms to the Mid North 132 kV lines or the 275 kV lines between Davenport and Para (the “East” and “West” circuits), the thermal rating of various 132 kV lines in the Mid North may constrain wind farm generation dispatch, based on the need to avoid overloading lines following a single credible contingency | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | <5 | Table 7-16 | Limitation may arise during times of high renewable generation in NSA zone. | Main Grid | Not applicable
| Table 7-6 | Increase the capacity of the 275 kV lines between Tungkillo and Heywood by upgrading various items of plant (e.g. remove line traps, replace current transformers, change current transformer ratios) and apply dynamic line ratings to these lines | Subject to the connection of new wind farms in South Australia, increased congestion on the 275 kV network between Tungkillo and Heywood is forecast to limit exports from South Australia to Victoria | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections / market benefit assessment | <5 | NA | Possible future project subject to wind farm development. Not captured in the 2015 NTNDP. | Main Grid | Not applicable
| Table 7-6 | Increase the capacity of the Tungkillo to Tailem Bend 275 kV corridor by stringing the vacant 275 kV circuit between Tungkillo and Tailem Bend (and establish a third 275 kV circuit between Para and Tungkillo) | Subject to the connection of new wind farms in South Australia, increased congestion on the 275 kV network between Tungkillo and Tailem Bend is forecast to restrict exports from South Australia to Victoria across the Heywood interconnector | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections / market benefit assessment | 25-50 | Table 7-15 | Limitation may arise during times of high VIC-SA (Heywood) interconnector transfer.. | Main Grid | Not applicable
| Table 7-6 | Uprate the Robertstown –North West Bend #2 and the North West Bend-Monash #2 132 kV lines to 100 ˚C line clearances and install two switched 15 MVar 132 kV capacitor banks at Monash | Subject to the connection of new wind farms in South Australia, increased congestion on the 132 kV network between Robertstown and Monash is forecast to restrict exports from South Australia to Victoria across the Murraylink interconnector | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | 10-18 | NA | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. Line uprating is modellled in 2015 NTNDP, but not the capactors. | Main Grid | Not applicable
| Table 7-7 | South East circuit breaker (CB) upgrade Install additional circuit breakers and associated switchgear, metering and protection at South East substation. | Substandard circuit breaker arrangement at South East substation constrains the Heywood Interconnector and places network security and reliability at risk. | Committed | 2015 | 5-10 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Tailem Bend Substation Upgrade Extend the Tailem Bend substation to accommodate an additional 275 kV diameter, with two circuit breakers, associated plant, secondary systems and rearrange 275 kV line exits. | Substandard circuit breaker arrangement at South East substation constrains the Heywood Interconnector and places network security and reliability at risk. | Committed | 2016 | 10-18 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Upper North Voltage Control Scheme Install automated regional voltage control schemes for Eyre Peninsula and Upper North regions. | Changing generation patterns have resulted in complex voltage interactions on the Eyre Peninsula and Upper North regions leading to potential violations of voltage limits stipulated in the Rules and connection agreements. | Committed | 2016 | <5 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Raise spans on the Bungama to Baroota 132 kV line to maintain the required rating of 49˚C using Australian clearance standards | The Bungama to Baroota 132 kV line was constructed to British clearance standards applicable at the time and does not meet Australian clearance standards. | Proposed | 2018 | <5 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Install, upgrade or replace transformer oil containment systems and associated equipment at various sites, where assessment indicates a clear need. | Transformer oil containment systems need refurbishment to maintain compliance with environment protection regulations. | Proposed | 2018 | 5-10 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-7 | Regional Control Scheme Install integrated control scheme(s) at strategic locations in the network to ensure compliance to the 'next contingency' Rules security requirements and allow higher utilisation of the network under system normal conditions as well as provide the opportunity to do more network maintenance as required. | Compliance with Rules chapter 4 security provisions becoming operationally difficult, with opportunities to do critical network maintenance and construction work reduced to very restrictive windows. | Proposed | 2018 | 5-10 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Install Eyre Peninsula islanding control scheme to minimise interruptions to customers | Shutdown of regionally important substations required during outages of Cultana to Yadnarie 132 kV transmission line | Proposed | 2018 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Redesign and replace the Murraylink Control Scheme | Outages and constraints on the Murraylink Interconnector | Proposed | 2018 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Create a high voltage switching training facility to improve training standards across all aspects of high voltage switching | High voltage switching training conducted on live network results in network and asset performance impacts and training limitations | Proposed | 2018 | 5-10 | NA | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Install additional 275 kV circuit breaker at Kilburn to complete the mesh. | Substandard circuit breaker arrangement at Kilburn substation places network security and reliability at risk. | Proposed | 2018-2023 | <5 | Table 7-13 | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Additional 275 kV switched reactors at Para: Install two switched 50 Mvar 275 kV reactors at Para | Following a single contingency of an in-service generator, steady-state voltage levels on the South Australian transmission system may breach 110% during the 2018 -2023 period. | Proposed | 2018 - 2023 | 5-10 | NA | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Install a 275 kV circuit breaker and associated equipment on the Robertstown exit at Canowie substation | Hallett wind farm generation constrained during outages of the Canowie to Robertstown 275 kV transmission line | Proposed | 2018-2023 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Uprate the Snuggery to Blanche to Mt Gambier 132 kV transmission line and associated low-rated primary plant | Significant constraint on wind generation on outage of Snuggery to South East 132 kV transmission line | Proposed | 2018-2023 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Install an additional 132 kV circuit breaker and associated equipment at Blanche substation | Generation constraints and/or loss of load during plant outages at Blanche substation | Proposed | 2018-2023 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Install a meshed 132 kV bus with four exits and associated primary and secondary equipment at or adjacent to the existing Murray Bridge - Hahndorf pumping station #3 site | Loss of load at Back Callington, Kanmantoo and Murray Bridge - Hahndorf pumping stations #2 and #3 during an outage of the Mount Barker to Mobilong 132 kV transmission line | Proposed | 2018-2023 | 10-15 | NA | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Install a single 275 kV circuit breaker and associated equipment between the 275 kV busses at Robertstown substation | Either Murraylink interconnection or generation north of Robertstown must be constrained during scheduled maintenance of centre breakers or associated plant at Robertstown substation | Proposed | 2018-2023 | 5-10 | NA | For security and compliance - not within the 2015 NTNDP scope. | Main Grid | Not applicable
| Table 7-7 | Implement full single pole reclosing capability on the 132 kV circuits in the Mid North region | Both Mintaro and Angaston generators are constrained off during 132 kV outages that result in these generators being radialised | Proposed | 2018-2023 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-7 | Implement full single pole reclosing capability on the 132 kV circuits in the South East region | Both Ladbroke Grove and Snuggery generators are constrained off during 132 kV outages that result in these generators being radialised | Proposed | 2018-2023 | <5 | NA | For security and compliance - not within the 2015 NTNDP scope. | Local Network | Not applicable
| Table 7-8 | Replace all end-of-life revenue meters. Alternative option: replace revenue meters as they fail. | Revenue meters at various connection points are at end-of-life, with increasing failure rates and no longer supported by manufacturer Note that this project previously addressed instrument transformers that are non-compliant with NEC metering requirements, but this limitation is now being addressed by ElectraNet’s unit asset replacement program | Committed | 2015 | <5 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Mt Gunson 132/33 kV connection point Replacement: Replace selected end-of-life plant at Mt Gunson substation with modern-day equipment and install a new 10 MVA 132/33 kV transformer. Alternative option: rebuild entire substation adjacent to existing substation. | Mount Gunson substation plant at end of technical life; 132/33 kV transformer condition assessment indicates replacement is required. | Committed | 2015 | 6-8 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Brinkworth to Mintaro Line Refurbishment Replace all porcelain disc insulators on Brinkworth to Mintaro 132 kV line, achieving a 15-year life extension. Alternative option: assess and replace insulators on sample-based testing results. | Porcelain disc insulators on Brinkworth to Mintaro 132 kV line at end of life, leading to high failure rate and fire start risk | Committed | 2015 | 5-7 | Table 7.2.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Neuroodla 132/33 kV Connection Point Replacement: Rebuild Neuroodla substation within the existing substation site, installing a new 10 MVA 132/33 kV transformer and modern-day equipment. Alternative options: replace selected substation plant based on condition or rebuild entire substation adjacent to existing substation. | Neuroodla substation at end of technical life; 132/33 kV transformer condition assessment indicates replacement is required. | Committed | 2015 | 6-8 | Table 7.2.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Tailem Bend to Keith No.2 Line Refurbishment Replace all porcelain disc insulators on Tailem Bend to Keith #2 132 kV line, achieving a 15-year life extension. Alternative option: assess and replace insulators on sample-based testing results. | Porcelain disc insulators on Tailem Bend to Keith #2 132 kV line at end of life, leading to high failure rate and fire start risk | Pending | 2015 | 5-10 | Table 7.2.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Para Unit Asset Replacements: Replace the 275 kV, 132 kV and 66 kV secondary systems, associated telecommunications systems, control buildings and selected primary plant at Para substation. The project scope and schedule have been extended to include unit asset replacements required in the 2014-2018 period. Alternative options: refurbish individual assets, replace assets on failure, or rebuild substation. | Some primary plant and most secondary systems at Para substation are in poor condition, not to modern-day standards and are a security and reliability risk. The structural integrity of the existing control building is of concern. | Committed | 2016 | 48-52 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Morgan to Whyalla pumping station #2 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Morgan to Whyalla pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2016 | 15-20 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Morgan to Whyalla pumping station #1 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Morgan to Whyalla pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2016 | 12-16 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Morgan to Whyalla pumping station #3 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Morgan to Whyalla pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2016 | 10-15 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Morgan to Whyalla pumping station #4 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Morgan to Whyalla pumping station #4 primary plant at end of technical life; site not aligned with current environmental practices and company practices | Pending | 2016 | 10-15 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Mannum to Adelaide pumping station #2 supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Mannum to Adelaide pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2017 | 8-12 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Mannum to Adelaide pumping station #3 supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Mannum to Adelaide pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2017 | 8-12 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Rebuild the Mannum to Adelaide pumping station #1 supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Mannum to Adelaide pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2017 | 10-15 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Millbrook Pump Station Rebuild the Millbrook supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. Alternative options: replace selected primary plant based on condition or replace all plant without applying improved standardisation with other sites. | Millbrook pumping station primary plant at end of technical life; site not aligned with current environmental practices and company policies | Pending | 2017 | 10-15 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Para to Davenport Line Hazard Mitigation Replace load releasing cross arms and all porcelain disc insulators on Para-Brinkworth-Davenport 275 kV line, achieving a 15-year life extension. Alternative options: rebuild 275 kV line in an adjacent easement and retire old line; or replace load releasing cross arms with standard cross arms (and also strengthen the towers) and assess and replace insulators on samplebased testing results. | Load releasing cross arms on Para-Brinkworth-Davenport 275 kV line are a safety risk and inadequate for access and maintenance. Porcelain disc insulators at end of life, leading to high failure rate and fire start risk | Pending | 2018 | 40-60 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Para SVC Secondary System Replacement Replace the existing SVC thyristor valves, thyristor valve cooling, protection and control systems for both SVCs at Para substation with modern-day equipment. Alternative options: replace individual components that are reaching end of life; or replace control systems only. | Condition of the existing Para SVCs secondary systems and the lack of spare parts make maintenance impossible and manufacturer support is largely withdrawn. Failure would severely constrain interconnector transfer capacity | Proposed | 2016 | 12-20 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Baroota Substation Upgrade Replace plant in poor condition at Baroota substation and implement flood mitigation measures. Retain only the existing single 10 MVA 132/33 kV transformer. This option depends on reaching agreement with ESCOSA to vary the requirement for category 2 reliability from 1 December 2017 at Baroota. Alternative options: replace plant in poor condition and install a second 10 MVA 132/33 kV transformer to meet category 2 reliability standard; replace plant in poor condition and engage nonnetwork service provider to meet category 2 reliability standard; or replace plant in poor condition and engage nonnetwork service provider to implement non-continuous generation support to provide a net market benefit to consumers;. | The majority of the primary equipment at Baroota substation is in poor condition | Proposed | 2017 | 5-10 (ElectraNet costs only) | Table 7-12 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace AC auxiliary supply equipment, switchboards and cabling at 13 substations. | AC auxiliary supplies at older substations are not compliant with current Australian standards and have some safety hazards and operational deficiencies | Proposed | 2018 | <5 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Planned replacement program to remove battery chargers from service and replace with modern, fit-for-purpose equipment. Alternative option: replace battery chargers on failure | A number of substation battery charger units have reached the end of their practical life. Also, spare parts are not available | Proposed | 2018 | <5 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Various Unit Asset Replacements: Program to replace individual unit assets, such as circuit breakers, voltage transformers, current transformers or protection relay sets that have reached end of life, at 34 substations. Alternative option: replace individually selected assets on failure. | Substation assets have been identified with high failure rates, safety risks or assessed to be at the end of their technical and economic lives. | Committed | 2013-2018 | 50-60 | Table 7.2.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace obsolete online asset condition monitoring equipment. Alternative option: continue corrective maintenance program only. | Many items of online condition monitoring equipment are nearing the end of their usable lives (12-20 years old) and are exhibiting high failure rates | Proposed | 2018-2023 | 8-12 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace substation lighting and associated infrastructure at sites where hazards exist. | Review of substation lighting identified compliance issues and safety hazards with some existing lighting systems. Cost and risks assessments were undertaken for the various lighting functions to determine the optimal solution to meet the requirements under the WHS Act and Australian Standards | Proposed | 2018-2023 | 4-8 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Program of transmission line refurbishment to renew line asset components and extend line life. Alternative option: replace individual components or sections on failure; or full line replacement. | Transmission line asset components at end of life, leading to high failure rate and fire start risk | Proposed | 2018-2023 | 100-130 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Program of unit asset replacements at various substations. Alternative option: replace assets on failure. | Substation assets have been identified with high failure rates, safety risks or assessed to be at the end of their technical and economic lives | Proposed | 2018-2023 | 20-30 | Table 7-14 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace 400-500 protection scheme relay assets. Alternative option: replace assets on failure. | Various individual substation protection systems have been assessed to be at the end of their technical and economic lives. Increased risk of failure could cause safety and reliability issues | Proposed | 2018-2023 | 30-40 | Not applicable | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace the existing reactors with two new 33 kV reactors at Leigh Creek Coalfield substation. Alternative option: replace assets on failure. | Leigh Creek Coalfield reactors 1 and 2 have been assessed to be at the end of their technical lives and at high risk of failure | Proposed | 2018-2023 | 10-15 | Not applicable | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace the existing transformers with two new 132/33 kV transformers at Leigh Creek Coalfield substation. Alternative option: replace assets on failure. | Leigh Creek Coalfield transformers 1 and 2 have been assessed to be at the end of their technical lives and at high risk of failure | Proposed | 2018-2023 | 10-15 | Not applicable | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace the existing transformers with two new 132/33 kV transformers at Leigh Creek South substation. Alternative option: replace assets on failure. | Leigh Creek South transformers 1 and 2 have been assessed to be at the end of their technical lives and at high risk of failure | Proposed | 2018-2023 | 10-15 | Not applicable | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace the existing transformers with two new 132/33 kV transformers at Mannum substation. Alternative option: replace assets on failure. | Mannum transformers 1 and 2 have been assessed to be at the end of their technical lives and at high risk of failure | Proposed | 2018-2023 | 10-15 | Not applicable | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
| Table 7-8 | Replace the existing 50 MVA transformer with a new 25 MVA 132/33/11 kV transformer at Mount Gambier substation. Alternative option: replace assets on failure. | Mount Gambier transformer 1 has been assessed to be at the end of its technical life and at high risk of failure | Proposed | 2018-2023 | 4-8 | Not applicable | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable

## TasNetworks 2015 TAPR Projects
2015 APR Reference |  | Transmission Development | Limitation Addressed | 2015 APR Project Status | 2015 APR Anticipated Timing | 2015 APR Indicative Cost ($ million) | 2014 APR Reference | 2015 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable) | 2013 APR Reference | 2014 NTNDP
6.2.2.1 | Table 1-1 | Rosebery Substation transformer augmentation: Installation of cooling fans on the transformers, which will increase the continuous firm capacity of the substation from 30 MVA to 36 MVA. (2014 APR: Replace existing 30 MVA transformers with new 60 MVA units in Rosebery Substation.) | Thermal capacity of existing 110/44-22 kV transformers at Rosebery Substation. | Committed | End 2015 | 6.2037 | Section 6.3.6.1 | Local supply issue - not within the 2015 NTNDP scope. | Local Network | Demand side management and/or additional generation at Rosebery Substation | Section 5.2.1.6.1 | Local supply
6.2.3.5 | Table 6-2 | Decommissioning the Queenstown–Newton 110 kV transmission line and providing a connection to the existing Farrell–Rosebery–Queenstown 110 kV transmission circuit to create a Farrell–Rosebery– Newton–Queenstown 110 kV transmission circuit. | Transmission line condition: Queenstown - Newton 110 kV | Proposed | 2017-06-01 | 4.5 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable | NA | Local supply
6.3.2.1 |  | Sheffield Substation 220 kV K and L bay upgrades | Increase the rating of the Sheffield– George Town 220 kV transmission circuits, allowing more power to be transferred through this corridor | Committed | 2016-06-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | NCIPAP | Not applicable | NA | NCIPAP
6.3.2.2 |  | Burnie Substation 110 kV redevelopment. | Condition of existing 110 kV circuit breakers, current transformers, protection and control equipment. | Completed | 2014-10-01 | NA | Section 5.3.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. | Not applicable | Section 4.3.3 | Condition based renewals
6.4.2.1 |  | George Town Substation 110 kV redevelopment. | Condition based asset replacement. | Committed | 2015-08-01 | NA | Section 5.3.4 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. | Not applicable | Section 4.3.6 | Condition based renewals
6.4.2.1 |  | George Town to Comalco 220 kV line rating upgrade | NCIPAP project | Comitted | 2016-03-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | NCIPAP |  | NA | NCIPAP
6.4.3.6 | Table 6-2 | Asset renewal at Palmerston Substation to replace the 23 type DR1 and DR2 disconnectors, the associated earth switches, and the protection on the three Poatina–Palmerston 220 kV transmission lines. | Condition of disconnectors, earth switches and some protection and control equipment. | Proposed | 2017-06-01 | 7.4 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. | Not applicable | NA
6.5.2.1 |  | installation of remote monitoring equipment on the transformers at Boyer Substation | The maximum demand at Boyer Substation exceeds the firm ratings of the supply transformers. | Committed | 2015-12-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | NCIPAP | Not applicable | NA
6.5.2.2 |  | Tungatinah Substation redevelopment and extension of the 110 kV transmission circuits that connect Meadowbank and New Norfolk Substations from Tarraleah Switching Station to Tungatinah Substation. | Condition based asset replacement. | Completed | 2015-04-01 | NA | Section 5.3.2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. | Not applicable | Section 4.3.4 | Condition based renewals
6.5.2.2 |  | Meadowbank Substation 110 kV redevelopment. | Condition of existing 110 kV circuit breakers, current transformers, protection and control equipment. | Completed | 2015-01-01 | NA | Section 5.3.3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. | Not applicable | Section 4.4.1 | Condition based renewals
6.5.3.5 | Table 6-2 | Replace 1 MVA transformer with a 5 MVA unit at Gretna Zone Substation | Condition of supply transformers. The Substation maximum demand is forecast to exceed capacity by summer 2017. | Proposed | 2017-06-01 | 1 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. Distribution transformer | Not applicable | NA
6.5.3.6 | Table 6-2 | Replace four 2.5 MVA transformers with three 5 MVA units at New Norfolk Zone Substation | Condition of supply transformers. Substation demand is forecast to exceed 7.5 MVA rating by winter 2019. | Proposed | 2017-06-01 | 1.7 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. Distribution transformer | Not applicable | NA
6.5.3.7 | Table 6-2 | Replace Butlers Gorge-Derwent Bridge transmission line with 22 kV feeder and backup diesel generation | High maintenance and refurbishment cost of the existing Butlers Gorge-Derwent Bridge 110 kV transmission line | Proposed | 2017-06-01 | 1.2 | Section 6.7.6.4 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement. | Not applicable | Section 5.2.5.6.4 | Local supply
6.6.2.1 | Table 1-1 | Establishment of Rosny Park Zone Substation. | Strengthen the network on Hobart's eastern shore. | Committed | 2016-05-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | Local Network - distribution | Not applicable | NA
6.6.3.7 | Table 6-2 | Replace two 22.5 MVA transformers with two 25 MVA units at Claremont Zone Substation | Condition of supply transformers | Proposed | 2018-06-01 | 3 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement - distribution | Not applicable | NA
6.6.3.10 | Table 6-2 | Replace two 22.5 MVA transformers with two 25 MVA units at Derwent Park Zone Substation | Condition of supply transformers. The substation demand is forecast to exceed the continuous firm rating from winter 2020 | Proposed | 2018-06-01 | 3 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement - distribution | Not applicable
6.6.3.11 | Table 6-2 | Replace the 11 kV switchboards at North Hobart Substation with new 12 kV air-insulated switchboards (operated at 11 kV) that have sufficient circuit breakers to enable one feeder to be connected per circuit breaker. | Condition of 11 kV switchboards | Proposed | 2018-06-01 | 5.1 | Section 6.7.6.3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement - distribution | Not applicable | NA
6.6.3.12 | Table 6-2 | Replace two 110/33 kV 45MVA transformers with two 110/33 kV 60MVA units at Lindisfarne Substation | Condition of supply transformers. Maximum demand at substation exceeded the continuous firm rating of the transformers in 2014. | Proposed | 2019 | 7.2 | Section 6.12.1 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable | Section 5.5.1
6.6.3.13 | Table 6-2 | Replace two 22.5 MVA transformers with two 25 MVA units at Bellerive Zone Substation | Condition of supply transformers | Proposed | 2020 | 3 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement - distribution | Not applicable
6.6.3.14 | Table 6-2 | Replace two 22.5 MVA transformers with two 25 MVA units at Geilston Bay Zone Substation | Condition of supply transformers | Proposed | 2020 | 3 | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement - distribution | Not applicable
6.7.2.2 |  | Upgrade distribution network in the east coast to transfer load from Avoca and St Marys Substations to Derby, Palmerston, and Triabunna Substations following an outage the Palmerston-Avoca-St Marys 110 kV line | Loss of the Palmerston-Avoca-St Marys 110 kV line results in loss of supply to Avoca and St Marys (single contingency) | Completed | 2015-03-01 | NA | Section 5.3.5 | Condition based renewals - not within the 2015 NTNDP scope. | Local Network. | Not applicable - committed project | Section 5.2.4.6.2 | Local supply
6.7.3.5 | Table 6-2 | Replace supply and regulating transformers at Richmond Zone Substation | Condition of supply and regulating transformers | Proposed | 2018-06-01 | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement - distribution | Not applicable | NA
6.7.3.7 | Table 6-2 | Replace the 41 Kay poles on the Triabunna Spur transmission line with new steel poles. | Condition of transmission line support structure. | Proposed | 2019 | 3.7 | Section 6.12.3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable | NA
6.8.2.1 |  | Castle Forbes Bay Tee Switching Station disconnector upgrade: Replacement of the manuallyoperated disconnector with a remotely-operable unit | A manually operated disconnector is located at Castle Forbes Bay Tee to facilitate the disconnection and reconnection of the Huon Valley Spur transmission line to the Knights Road–Kermandie 110 kV transmission circuit. This presents operational and reliability issues for supply to Huon River and Kermandie substations. | Committed | Febuary 2016 | NA | NA | Local supply issue - not within the 2015 NTNDP scope. | NCIPAP | Not applicable | NA
6.8.2.1 |  | Dynamic rating of Knights Road Substation supply transformers | The maximum demand at Knights Road Substation is approaching the continuous firm rating of the transformers | Committed | Febuary 2016 | NA | NA | Local supply issue - not within the 2015 NTNDP scope. | NCIPAP | Not applicable | NA
6.8.2.1 |  | Line fault indicator communications program (Castle Forbes Bay Tee Switching Station) | Following a fault on the Knights Road–Huon River– Kermandie 110 kV transmission circuit, crews are required to travel to the line fault indicator at Castle Forbes Bay Tee Switching Station to establish which section of the line received the fault. | Committed | 2015-07-01 | NA | NA | Local supply issue - not within the 2015 NTNDP scope. | NCIPAP | Not applicable | NA
6.9.2.4 | Table 6-2 | Asset renewal of Waddamana - Bridgewater Junction 110 kV transmission line: • circuit re-arrangement to create Waddamana– Bridgewater–Lindisfarne transmission circuit | Condition of transmission line | Proposed | 2019-06-01 | 1.9 | Na | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
6.9.2.5 | Table 6-2 | Upper Derwent 110 kV network: Alternate options to maintaining the existing network could include transferring all the generation in the area onto the 220 kV network, rationalising the supply through the 110 kV network, or a combination of these. | Condition of transmission lines in the Upper Derwent 110 kV network. | Proposed | 5-10 years | NA | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable | NA
6.9.2.6 | Table 6-2 | Transportable substation: 110 kV to 22 and 11 kV, rated 25 MVA | •Risk of substation failure; a portable substation may allow supply restoration to communities following an extended interruption to supply. • Enable time efficient customer connection. Such situations include mine site developments, where rapid deployment is required. | Proposed | 2019 | 8 | NA | Local supply issue - not within the 2015 NTNDP scope. | Local Network | Not applicable | NA
Note on G1: Kiet Lee: where no 2015 costs available, escalate by 1.7%