## Information
Transmission Augmentation Information
About
This workbook is released by the Australian Energy Market Operator (AEMO). This workbook contains information for National Electricity Market (NEM) transmission projects that have a material impact on AEMO’s Integrated System Plan (ISP), Electricity Statement of Opportunities (ESOO) and Inputs, Assumptions and Scenarios Report (IASR). This workbook only contains transmission augmentation projects that are: - committed, - anticipated, - actionable ISP projects or - future ISP projects with preparatory activities. A transmission augmentation project is a project to enlarge the transmission system or to increase its capacity to transmit electricity. AEMO expects to update this workbook every 6 months. This workbook and the reports it relates to can be accessed via https://aemo.com.au/energy-systems/electricity/national-electricity-market-nem/nem-forecasting-and-planning/forecasting-and-planning-data/transmission-augmentation-information.
Worksheet index
Worksheet | Description
Change log | This page keeps track of project-specific changes between releases.
Transmission augmentations | This pages summarises all committed, anticipated, actionable projects and future ISP projects with preparatory activities.
Field name descriptions
Field Name | Explanation/Definition
Region | A region in the NEM is an area determined by the Australian Energy Market Commission (AEMC) as being an area served by a particular part of the transmission network containing one or more major load centres or generation centres or both. The current regions in the NEM are largely based on Australian jurisdictional boundaries - New South Wales, Queensland, Tasmania, Victoria and South Australia. This field will outline all affected regions by the project.
Project type | This field can include values: augmentation, interconnector, new transmission, uprate transmission, or detail the specific equipment type the project will construct.
Project name | This field will correspond to the project name that has been referred to in other AEMO documents.
Proponent(s) | The Transmission Network Service Provider(s) (TNSP(s)) or authoritie(s) responsible for the delivery and/or development of the project. There may be more than one proponent for interconnector projects. In some cases, unique jurisdictional regulatory arrangements may mean that a project proponent is not a TNSP.
Project status | Committed | Committed project means a project that meets the following criteria: - the proponent has obtained all required planning consents, construction approvals and licenses, including completion and acceptance of any necessary environmental impact statement; - construction has either commenced or a firm commencement date has been set; - the proponent has purchased/settled/acquired land (or commenced legal proceedings to acquire land) for the purposes of construction; - contracts for supply and construction of the major components of the necessary plant and equipment (such as generators, turbines, boilers, transmission towers, conductors, terminal station equipment) have been finalised and executed, including any provisions for cancellation payments; and - the necessary financing arrangements, including any debt plans, have been finalised and contracts executed.
| Anticipated | A project which does not meet all the criteria of a committed project as defined above and is in the process of meeting at least three of the criteria for a committed project.
| Actionable ISP | An actionable ISP project as defined in NER chapter 10 as a project: - that relates to a transmission asset or non-network option the purpose of which is to address an identified need specified in an ISP and which forms part of an optimal development path, and - for which a project assessment draft report is required to be published in the ISP that identifies that project.
| Future ISP - preparatory activities requested | A future ISP project for which an ISP has specified that preparatory activities must be carried out in accordance with NER clause 5.22.6(c). A future ISP project is defined in NER clause 5.10.2 as a project: - that relates to a transmission asset or non-network option the purpose of which is to address an identified need specified in an ISP and which forms part of an optimal development path, and - that is forecast in the ISP that identifies the project, to be an actionable ISP project in the future. Preparatory activities are defined in NER clause 5.10.2
These are the project status definitions used in the Integrated System Plan (ISP) and reliability assessments conducted for the Electricity Statement of Opportunities (ESOO). For non-RIT-T and government projects, AEMO works with the project proponent to determine the project status definition that best aligns with those projects.
Project description | A brief outline of the in-scope works for the project.
Increased network capacity | This field will include how the transmission project will affect the local capacity of the network.
Preparatory activities completion date | If the project required/requires preparatory activities, the completion date will be specified here. The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
Funding approval | The stage of the project's funding approval. Options include: - PSCR complete - Project Specification Consultation Report complete - PADR complete - Project Assessment Draft Report complete - PACR complete - Project Assessment Conclusion Report complete - RIT-T complete - Regulatory Investment Test for Transmission complete, which will come after the dispute period - ISP Feedback Loop complete - CPA lodged - Contingent Project Application lodged - CPA complete - Contingent Project Application complete - Other - funding pending - Other - funding approved - Other - funding process has not started The "Other - funding pending" and "Other - funding approved" options will be selected if a project goes through a funding process that is not the RIT-T or CPA, for example a NSW project may progress under the Electricity Infrastructure Investment Act 2020 (NSW) instead. The RIT-T process is a public economic cost benefit analysis administered by the Australian Energy Regulator (AER) that TNSPs may apply to potential prescribed (regulated) investments in the transmission network that exceed an AER prescribed cost threshold. It is a staged process consisting of three documents: 1. The Project Specification Consultation Report (PSCR), 2. The Project Assessment Draft Report (PSCR), 3. Project Assessment Conclusion Report (PACR) In addition to the above submissions, the TNSP may request written confirmation from AEMO that the preferred augmentation option from RIT-T project aligns with the optimal development path in the most recent ISP. This process is referred to as the “ISP feedback loop”.
Construction stage | The stage of the project's construction. Options include: - Construction has not started - Construction started - Construction complete - Commissioning started - In service - partial capacity available - In service - full capacity available
Early works completion date | This field provides an indication of timing for early works to be complete if applicable. Early works are activities undertaken by the proponent to address project uncertainties and reduce project risk. This can include a number of activities including stakeholder engagement, land planning, detailed engineering design, project development and regulatory approvals.
In service date | This field provides an indication of timing for construction and commissioning to be complete and equipment is in-service.
Capacity release date | This field provides an indication of timing for the full capacity of the project to become available in the NEM. The capacity release of the project requires the successful completion of inter-network testing where necessary, which may require certain conditions in the NEM. A project will only have this field populated if the capacity release date has been used as an input to the ESOO or ISP for modelling. If a project is not yet actionable or the forecasted release date has not been used in network modelling this field is not applicable.
Source | This field will outline where the information in that row has come from.
Disclaimer
AEMO publishes this Transmission Augmentation Information workbook for the purpose of transparently providing information to stakeholders about committed, anticipated, actionable and future projects with preparatory activities as inputs for the Integrated System Plan (ISP) and Electricity Statement of Opportunities (ESOO). This information workbook and the information in it has been prepared by AEMO using information available to it at the time of publication and may be subsequently updated or amended. This Transmission Augmentation Information workbook contains data, information and forecasts provided by or collected from third parties, and conclusions, opinions, assumptions or forecasts that are based on that data. AEMO has made every reasonable effort to ensure the quality of the information in this information workbook but cannot guarantee that the information, forecasts and assumptions in it are accurate, complete or appropriate for your circumstances. This information workbook does not include all of the information that an investor, participant or potential participant in the National Electricity Market might require and does not amount to a recommendation of any investment. Anyone proposing to use the information in this information workbook (which contains data, information and forecasts from third parties) should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts. The Transmission Augmentation Information workbook does not constitute legal, business, technical or engineering advice and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this information workbook but cannot guarantee its accuracy or completeness. Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document: - make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this information workbook; and - are not liable (whether by reason of negligence or otherwise) for any statements or representations in this information workbook, or any omissions from it, or for any use or reliance on the information in it. Copyright © 2023 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.
References
Integrated System Plan (ISP)
NEM Electricity Statement of Opportunities (ESOO)
Contingent projects ¦ Australian Energy Regulator
Please refer to respective TNSP websites for most up to date Transmission Annual Planning Reports (TAPRs)
Please refer to the Australian Energy Regulator's (AER's) website for determination documents, final decision documents and other relevant information.

## Change log
Change Log
Release version | Date | Region | Type of Change | Project | Proponent(s) | Details
1 | 2022-12-16 |  | Initial Release |  |  | Initial release. Includes NEM transmission projects that have material effect in the ISP or ESOO and are committed, anticipated, actionable or considered a future project that requires preparatory activities.
2 | 2023-07-28 | QLD | Project removal - in service | Strathmore Second 275/132 kV Transformer Establishment | Powerlink | Strathmore Second 275/132 kV Transformer Establishment is in service and hence has been removed.
| 2023-07-28 | QLD | New project addition | CopperString 2023 | Powerlink | New transmission line from south of Townsville in the Burdekin region to Mount Isa to align with latest advice received from Powerlink.
| 2023-07-28 | QLD | Project update - preparatory activities received | Darling Downs REZ Expansion - Stage 1 | Powerlink | Updated and included network options to align with the preparatory activity reports and latest advice received from Powerlink.
| 2023-07-28 | QLD, NSW | Project update - preparatory activities received | QNI Connect - 330 kV options and 500 kV option | Powerlink, Transgrid | QNI Connect 330 kV and 500 kV options updated aligned with preparatory activity reports recieved from Transgrid and Powerlink.
| 2023-07-28 | QLD, NSW | Project update - timing | QNI Minor (Queensland - New South Wales Interconnector) | Transgrid | QNI Minor network upgrades are complete, internetwork testing is progressing.
| 2023-07-28 | NSW | Project update - timing | Wagga Wagga 330 kV 100 MVAr Capacitor Bank | Transgrid | In service and capacity release date updated to Jul-23 as advised by Transgrid.
| 2023-07-28 | NSW | Project update - timing | VNI Minor (also named VNI East Upgrade) | AEMO, Transgrid | The VNI minor NSW works in now in service. AEMO Victoria Planning has advised that the in service date for the Victoria works is July 2023.
| 2023-07-28 | NSW | Project update - description | HumeLink | Transgrid | Updated project description to include details of shunt reactors and updated the substation near Wagga Wagga to Gugaa substation as per advice from Transgrid.
| 2023-07-28 | NSW | Project update - status and increased network capacity | Waratah Super Battery Network Augmentations and SIPS Control | EnergyCo | Project status has been changed to committed, the in service and capacity release date updated to "Jul-25" for the Waratah Network Augmentations and SIPS control scheme as advised by Transgrid and EnergyCo. Increased network capacity updated to "increase of 910 MW between CNSW and SNW" based on latest advice from EnergyCo.
| 2023-07-28 | NSW | Project update - status | Waratah Super Battery Network Augmentation | EnergyCo | Project status has been changed to committed and the increased network capacity updated to "increase of 910 MW between CNSW and SNW" based on latest advice from EnergyCo.
| 2023-07-28 | NSW | Project update - description and timing | Sydney Ring (Reinforcing Sydney, Newcastle, and Wollongong Supply) - Option 1: Sydney Ring Northern 500 kV loop (Hunter Transmission Project 1.0) | EnergyCo | Project description updated to add "Bayswater and Eraring substation augmentation work to accomodate the additional transmission line". Project in service date updated to "Dec-27" based on latest advice received from EnergyCo.
| 2023-07-28 | NSW | Project update - description | Central-West Orana REZ Transmission Link | EnergyCo | Capacity of synchronous condensers at Elong Elong switching station and Merotherie substation updated to 3 x 250 MVAr and 4 x 250 MVAr respectively.
| 2023-07-28 | NSW | Project update - description and increased network capacity | New England REZ Transmission Link | EnergyCo | Project description has been updated based on latest advice from EnergyCo. The network capacity increase was updated to "2,400 MW".
| 2023-07-28 | VIC, NSW | Project update - project description, increased network capacity, funding approval status and early works timing | VNI West | AEMO, Transgrid | Project description and increased network capacity has been updated to align with the VNI West PACR Volume 1. Funding approval status updated to "PACR complete". Early works completion date updated to "Early 2026" based on latest advice from AEMO Victorian Planning.
| 2023-07-28 | VIC | Project update - description, increased network capacity and timing | Western Renewables Link | AEMO | Project description, increased network capacity and in service date have been updated to align with the VNI West PACR Volume 1, Victoria Government Gazette, No. S 267 and latest advice received from AEMO Victorian Planning.
| 2023-07-28 | VIC | New project addition | South West REZ minor Augmentations | AEMO on behalf of Victorian Government | New transmission project added to align with the AEMO Victorian Annual Planning Report 2022 and latest advice received from AEMO Victorian Planning.
| 2023-07-28 | VIC | New project addition | Koorangie Energy Storage System (KESS) | AEMO on behalf of Victorian Government | New battery energy storage system project added to align with the AEMO Victorian Annual Planning Report 2022, Victoria Government Gazette, No. S 267 and latest advice received from AEMO Victorian Planning.
| 2023-07-28 | VIC, TAS | Project update - description and increased network capacity | Marinus Link - Stage 1 and 2 | TasNetworks, Marinus Link Pty Ltd | Updated combined network capacity values for Basslink and Marinus Link and project description as advised by TasNetworks.
| 2023-07-28 | SA, NSW, VIC | Project update - status and description | Project EnergyConnect - Stage 1 and 2 | ElectraNet, Transgrid | Project status has been updated as advised by the relevant TNSPs. The project description has minor updates to the capacitor sizes at Buronga and Dinawan as advised by Transgrid. Buronga - Red Cliffs 220 kV line has moved from stage 1 to stage 2 of PEC as advised by the relevant TNSPs.
| 2023-07-28 | SA | Project removal - in service | Eyre Peninsula Link | ElectraNet | Eyre Peninsula Link is in service and hence has been removed.
| 2023-07-28 | SA | Project removal - in service | NCIPAP Smart Wires Power Guardian Technology Trial | ElectraNet | NCIPAP Smart Wires Power Guardian Technology Trial is in service and hence has been removed.
| 2023-07-28 | SA | Project removal - in service | Strengthen the Eastern Hills Transmission Corridor | ElectraNet | Strengthen the Eastern Hills Transmission Corridor is in service and hence has been removed.
| 2023-07-28 | SA | Project update - preparatory activities received | South East SA REZ Expansion - Stage 1 | ElectraNet | Project description has been updated to remove installation of "100 MVAr SVC at Tailem Bend" from scope and update the increased network capacity to 120 MW as per preparatory activity reports and latest advice received from ElectraNet.
| 2023-07-28 | SA | Project update - preparatory activities received | Mid North SA REZ Expansion | ElectraNet | Project description and increased network capacity has been updated to align with the preparatory activity reports and latest advice received from ElectraNet.
| 2023-07-28 | VIC | Project update - preparatory activities received | South West Victoria REZ Expansion | AEMO | Project description and increased network capacity has been updated to align with the preparatory activity reports and latest advice received from AEMO Victorian Planning.
2.1 | 2023-08-31 | VIC, NSW | Project update - project timing | VNI West | AEMO, Transgrid | Project in service date and capacity release date have been updated to align with the latest advice received from AEMO Victorian Planning and Transgrid. Note that the capacity release date was advised as "Q4 2029" and AEMO has interpreted this as "December 2029" for modelling purposes.

## Transmission augmentations
Transmission Augmentation Information
Region | Project type | Project name | Proponent(s) | Project status | Project description | Increased network capacity | Preparatory activities completion date | Funding approval | Construction stage | Early works completion date | In service date | Capacity release date | Source
NSW | New capacitor bank | Wagga Wagga 330 kV 100 MVAr Capacitor Bank | Transgrid | Committed | A new 330 kV 100 MVAr capacitor bank at Wagga Wagga. | 30 MW increase of flow in the southerly direction and 75 MW increase of flow in the northerly direction. | Not applicable | Other - funding approved | Construction started | Not applicable | 2023-07-01 | 2023-07-01 | Transgrid. Transmission Annual Planning Report - October 2022, at https://www.Transgrid.com.au/media/jn4klv4s/tgr12164-tapr-2022-v5-4-final.pdf
VIC,NSW | Upgraded Interconnector | VNI Minor (also named VNI East Upgrade) | AEMO, Transgrid | Committed | The VNI East Upgrade project consists of: VIC works: - Installation of a second 500/330 kV transformer at South Morang Terminal Station. - Re-tensioning of the 330 kV South Morang – Dederang transmission lines, as well as associated works (including replacement of series capacitors), to allow operation at thermal rating. NSW works: - Installation of modular power flow controllers on the 330 kV Upper Tumut – Canberra and Upper Tumut – Yass lines to balance power flows. This work is being undertaken by Transgrid in New South Wales. | Staged release of export capability from Victoria to New South Wales up to 170 MW, as per the PACR. | Not applicable | VIC works - Other - funding approved NSW works - CPA complete | Construction and first energization completed on time Nov 2022 for NSW works. Additional commissioning checks being done to verify the technology. Full autonomous operation expected in Q1 2023. Construction in progress for Victorian works. | Not applicable | In service for NSW works (manual operation) 30 July 2023 for Victoria works | In service for NSW works (Autonomous operation) | AEMO. Integrated System Plan Feedback Loop Notice – VNI Minor, at https://aemo.com.au/-/media/files/major-publications/isp/2020/isp-feedback-loop-notice-vni-minor.pdf?la=en AER. Final Decision - Transgrid - VNI Minor Upgrade, at https://www.aer.gov.au/system/files/AER%20-%20VNI%20Minor%20Contingent%20Project%20Determination%20-%2013%20April%202021_1.pdf As advised TNSP feedback.
QLD, NSW | Uprate interconnector | QNI Minor (Queensland - New South Wales Interconnector) | Transgrid | Committed | - Uprating the existing 330 kV Liddell – Tamworth lines. - Installing new dynamic reactive support at Tamworth and Dumaresq substations. - Installing new shunt connected capacitor banks at Tamworth, Armidale and Dumaresq substations. | 150 MW increase of flow in the northerly direction and 145-245 MW increase of flow in the southerly direction. | Not applicable | CPA complete | Commissioning started | Not applicable | 2022-06-01 | Some capacity for this project has already been released. Further capacity release expected over the coming months subject to market conditions for further inter-network testing. | AER. Final Decision - Transgrid - QNI Minor Contingent Project - April 2020, at https://www.aer.gov.au/system/files/AER%20-%20Final%20Decision%20-%20Transgrid%20-%20QNI%20minor%20upgrade%20contingent%20project%20-%20April%202020.pdf Transgrid. Transmission Annual Planning Report - October 2022, at https://www.Transgrid.com.au/media/jn4klv4s/tgr12164-tapr-2022-v5-4-final.pdf Transgrid. Queensland-NSW Interconnector, at https://www.Transgrid.com.au/projects-innovation/queensland-nsw-interconnector
QLD | Network upgrade | Northern QREZ | Powerlink | Committed | The Northern QREZ project consists of: - Establish a third 275 kV connection into Woree substation. - Conversion of one side of the coastal 132 kV double circuit transmission line to permanently operate at 275 kV as the third transmission line between Ross Woree. - Construction of a 275 kV bay at Ross Substation. - Installation of a 275/132 kV transformer at Tully Substation. - Installation of a 275 kV busbar at Woree Substation with associated bays and a line reactor. | Allow for up to 500 MW of new generation. Increased flow to the Far North Queensland REZ. | Not applicable | Other - funding pending | Construction started | Not applicable | 2023-11-01 | 2023-11-01 | Powerlink. 2022 Transmission Annual Planning Report (TAPR), at https://www.powerlink.com.au/sites/default/files/2022-10/Transmission%20Annual%20Planning%20Report%202022%20-%20Full%20report.pdf Powerlink. Developing the Northern Queensland Renewable Energy Zone FINAL REPORT AND DETERMINATION September 2021, at https://www.powerlink.com.au/sites/default/files/2021-09/Powerlink%20Queensland%20-%20Developing%20the%20Northern%20QREZ%20-%20Final%20Report.pdf
SA, NSW, VIC | New interconnector | Project EnergyConnect - Stage 1 | ElectraNet, Transgrid | Committed | AC interconnector between Wagga Wagga in New South Wales and Robertstown in South Australia via Buronga. Stage 1: - A new Robertstown to Bundey 275 kV double circuit line. - A new Bundey to Buronga 330 kV double circuit line with one circuit connected initially. - A new 330/275 kV substation and 3x400 MVA 275/330 kV transformers at Bundey. - A new 330/220 kV substation, 1x200 MVA 330/220 kV transformer and 1x200 MVA 330 kV phase shifting transformer at Buronga. - 1x60 MVAr 330 kV line reactor at Bundey - 1x60 MVAr 330 kV bus connected reactor at Bundey - 1x100 MVAr 275 kV bus connected capacitor at Bundey - 1x50 MVAr 330 kV line reactor at Buronga - 2x52 MVAr 330 kV capacitors at Buronga - 1x100 MVA 330 kV connected synchronous condenser at Buronga - An inter-trip protection scheme to trip the PEC interconnector if South Australia becomes separated from Victoria via the Heywood Interconnector. | 150 MW increase of flow between NSW and SA in both directions. Transgrid, ElectraNet and AEMO Victorian Planning to advise any updates ahead of publication of the final 2023 IASR. | Not applicable | CPA complete | Construction started | Not applicable | 2023-12-01 | 2024-07-01 | AER. Final Decision - ElectraNet - Project EnergyConnect Contingent Project - May 2021, at https://www.aer.gov.au/system/files/AER%20-%20Final%20Decision%20-%20ElectraNet%20-%20Project%20EnergyConnect%20Contingent%20Project%20-%20May%202021.pdf AER. Final Decision - Transgrid - Project EnergyConnect Contingent Project - May 2021, at https://www.aer.gov.au/system/files/AER%20-%20Final%20Decision%20-%20Transgrid%20-%20Project%20EnergyConnect%20Contingent%20Project%20-%20May%202021.pdf ElectraNet. Transmission Annual Planning Report - October 2022, at https://www.electranet.com.au/wp-content/uploads/221117_ENet-TAPR_A4_WEB.pdf Transgrid. Transmission Annual Planning Report - October 2022, at https://www.Transgrid.com.au/media/jn4klv4s/tgr12164-tapr-2022-v5-4-final.pdf
SA, NSW, VIC | New interconnector | Project EnergyConnect - Stage 2 | ElectraNet, Transgrid | Committed | Stage 2: - Second 330 kV circuit closed on the Bundey–Buronga 330 kV double circuit line (including 1 x 60 MVAr line reactor at Bundey and 1 x 50 MVar line reactor at Buronga of each circuit). - A new Buronga to Red Cliffs 220 kV double circuit line. - A new 330 kV double-circuit line from Dinawan to Buronga (including 50 MVar line reactors at both ends of each circuit). - A new 500 kV double-circuit line from Dinawan to Wagga Wagga operating at 330 kV (including 50 MVar line reactors at the Dinawan end on each circuit). - A new 330 kV switching station at Dinawan. - Additional 4x200 MVA 330 kV phase shifting transformers at Buronga. - Additional 2x200 MVA 330/220 kV transformers at Buronga. - An additional 1x100 MVA 330 kV connected synchronous condenser at Buronga - New 2x100 MVA 330 kV connected synchronous condenser at Dinawan - New 2x52 MVAr 330 kV capacitor banks at Dinawan. - Turning the existing 275 kV line between Para and Robertstown into Tungkillo. - A special protection scheme to detect and manage the loss of either of the AC interconnectors connecting to South Australia. | Inclusive of Stage 1, - 800 MW increase of flow between NSW and SA in both directions. - 100 MW increase of flow on VIC-SA Heywood interconnector in both directions. - NSW to SA and VIC to SA (Heywood interconnector) combined transfer 1,300 MW. - SA to NSW and SA to VIC (Heywood interconnector) combined transfer 1,450 MW. Increase REZ network capacity for V2, S2 and N5. | Not applicable | CPA complete | Construction has not started | Not applicable | 2024-12-01 | 2026-07-01 | AER. Final Decision - ElectraNet - Project EnergyConnect Contingent Project - May 2021, at https://www.aer.gov.au/system/files/AER%20-%20Final%20Decision%20-%20ElectraNet%20-%20Project%20EnergyConnect%20Contingent%20Project%20-%20May%202021.pdf AER. Final Decision - Transgrid - Project EnergyConnect Contingent Project - May 2021, at https://www.aer.gov.au/system/files/AER%20-%20Final%20Decision%20-%20Transgrid%20-%20Project%20EnergyConnect%20Contingent%20Project%20-%20May%202021.pdf ElectraNet. Transmission Annual Planning Report - October 2022, at https://www.electranet.com.au/wp-content/uploads/221117_ENet-TAPR_A4_WEB.pdf Transgrid. Transmission Annual Planning Report - October 2022, at https://www.Transgrid.com.au/media/jn4klv4s/tgr12164-tapr-2022-v5-4-final.pdf
NSW | Uprate Transmission | Waratah Super Battery Network Augmentations and SIPS Control | EnergyCo | Committed | Transmission augmentations to the network: - Uprate of Bannaby – Sydney West 330 kV transmission lines. - Substation works at Bannaby, Sydney West, Newcastle, Tomago, Liddell, Muswellbrook, Tamworth, Armidale, Dumaresq and Sapphire substations. - Link tendered paired generation to Waratah Super Battery with SIPS control scheme - SIPS control delivered by Transgrid | This will increase capacity between CNSW and SNW by 910 MW. (The limit increase is observed after the "Waratah Super Battery Network Augmentations and SIPS Control" and "Waratah Super Battery Network Augmentation" projects in service and has been formulated for the ISP DLT modelling and should not be used for other applications. The increase in capacity between CNSW and SNW is dependent on the output of the generation paired with the SIPS control scheme for a given period in time.) | Not applicable | Other - funding pending | Construction has not started | Not applicable | Jul-25 The contract of SIPS Service will be 5 years. | Jul-25 (Note: Capacity release from SIPS Control and link to tendered paired generation services is dependent on the output of the generation paired with the SIPS control scheme) | As advised by EnergyCo and Transgrid
NSW | Uprate Transmission | Waratah Super Battery Network Augmentation | EnergyCo | Committed | Transmission augmentations to the network: - Uprate of Yass – Collector, Collector – Marulan and Yass – Marulan 330 kV transmission lines. - Substation works at Upper Tumut, Lower Tumut, Yass, Collector, Marulan and Macarthur substations. | This will increase capacity between CNSW and SNW by 910 MW. (The limit increase is observed after the "Waratah Super Battery Network Augmentations and SIPS Control" and "Waratah Super Battery Network Augmentation" projects in service and has been formulated for the ISP DLT modelling and should not be used for other applications. The increase in capacity between CNSW and SNW is dependent on the output of the generation paired with the SIPS control scheme for a given period in time.) | Not applicable | Other - funding pending | Construction has not started | Not applicable | Aug-25 | Aug-25 | As advised by EnergyCo and Transgrid
VIC | REZ | South West REZ minor Augmentations | AEMO on behalf of Victorian Government | Committed | The four South West REZ minor augmentations include: - Establishing an automatic generator runback control scheme to manage thermal loading on the Ballarat – Berrybank – Terang – Moorabool 220 kV lines. - Establishing temperature-dependant 5-minute and 15-minute dynamic line ratings, utilising AusNet Services’ System Overload Control Scheme (SOCS), on the Moorabool to Heywood 500 kV line. - Undertaking terminal station interplant asset replacements to increase the end-to-end thermal capacity of the Sydenham to Keilor 500 kV line. - Undertaking terminal station interplant asset replacements to increase the end-to-end capacity thermal capacity of the Moorabool 500/220 kV transformers. | 81 MW. | Not applicable | Other - funding approved | Construction has not started | Not applicable | 2024-12-01 | 2024-12-01 | AEMO. Victorian Annual Planning Report 2022, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2022/2022-victorian-annual-planning-report.pdf?la=en Victorian State Government, Environment, Land, Water and Planning. Victorian Renewable Energy Zones Development Plan Directions Paper, at https://www.energy.vic.gov.au/__data/assets/pdf_file/0028/580618/Victorian-Renewable-energy-zones-development-plan-directions-paper.pdf As advised by AEMO Victorian Planning.
VIC | Network upgrade | Koorangie Energy Storage System (KESS) | AEMO on behalf of Victorian Government | Anticipated | The Koorangie Energy Storage System (KESS) consists of: - Establishing a new 220 kV terminal station, located approximately 15 km north-west of the existing Kerang Terminal Station, connecting into the existing Kerang – Wemen 220 kV line. | This project with Koorangie Energy Storage is expected to improve system strength in the Murray region and allow the stable connection of up to 300 MW of additional renewable energy generation. | Not applicable | Other - funding approved | Construction has not started | Not applicable | 2025-03-31 | 2025-03-31 | AEMO. Victorian Annual Planning Report 2022, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2022/2022-victorian-annual-planning-report.pdf?la=en Victorian State Government, Environment, Land, Water and Planning. Victorian Renewable Energy Zones Development Plan Directions Paper, at https://www.energy.vic.gov.au/__data/assets/pdf_file/0028/580618/Victorian-Renewable-energy-zones-development-plan-directions-paper.pdf
VIC | REZ | Ararat synchronous condenser | AEMO on behalf of Victorian Government | Anticipated | The Ararat synchronous condenser consists of: - Installing a new 250 MVA synchronous condenser to the existing Ararat Terminal Station. | This project will improve system strength in the network. | Not applicable | Other - funding approved | Construction has not started | Not applicable | 2025-09-01 | 2025-09-01 | AEMO. Victorian Annual Planning Report 2022, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2022/2022-victorian-annual-planning-report.pdf?la=en Victorian State Government, Environment, Land, Water and Planning. Victorian Renewable Energy Zones Development Plan Directions Paper, at https://www.energy.vic.gov.au/__data/assets/pdf_file/0028/580618/Victorian-Renewable-energy-zones-development-plan-directions-paper.pdf
VIC | New Line | Mortlake Turn-In | AEMO on behalf of Victorian Government | Anticipated | The Mortlake turn-in consists of: - Installing four new 500 kV circuit breakers and associated equipment to fully populate one the existing 500 kV bays and establish a new additional 500 kV bay at Mortlake Power Station. - Connecting the existing Haunted Gully to Tarrone 500 kV circuit, of the Moorabool – Heywood 500 kV double circuit line, into Mortlake Terminal Station to establish a Haunted Gully – Mortlake 500 kV circuit and a Mortlake to Tarrone 500 kV circuit. | The turn-in project is expected to allow up to 1,500 MW of additional generation output following its commissioning. | Not applicable | Other - funding approved | Construction has not started | Not applicable | 2025-10-01 | 2025-10-01 | AEMO. Victorian Annual Planning Report 2022, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2022/2022-victorian-annual-planning-report.pdf?la=en Victorian State Government, Environment, Land, Water and Planning. Victorian Renewable Energy Zones Development Plan Directions Paper, at https://www.energy.vic.gov.au/__data/assets/pdf_file/0028/580618/Victorian-Renewable-energy-zones-development-plan-directions-paper.pdf
VIC | REZ | Murray River REZ and Western Victoria REZ minor augmentations | AEMO on behalf of Victorian Government | Committed | The three Murray River and Western Victoria REZ minor augmentations include: - Establishing an automatic generator runback control scheme to manage thermal loading on the Red Cliffs – Kiamal – Murra Warra – Horsham – Bulgana 220 kV lines. - Modifying the existing Murraylink Very Fast Runback (VFRB) control scheme to also operate for Murraylink import from South Australia to Victoria to manage thermal loading on the Red Cliffs – Kiamal – Murra Warra – Horsham – Bulgana 220 kV lines. - Undertaking terminal station interplant asset replacements at Ballarat, Ararat, Waubra, Bulgana and Kiamal terminal stations to increase the end-to-end thermal capacity of the Ballarat – Waubra – Ararat – Crowlands – Bulgana – Horsham – Murra Warra – Kiamal 220 kV line. | 112 MW. | Not applicable | Other - funding approved | Construction has not started | Not applicable | 2025-10-01 | 2025-10-01 | AEMO. Victorian Annual Planning Report 2022, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2022/2022-victorian-annual-planning-report.pdf?la=en Victorian State Government, Environment, Land, Water and Planning. Victorian Renewable Energy Zones Development Plan Directions Paper, at https://www.energy.vic.gov.au/__data/assets/pdf_file/0028/580618/Victorian-Renewable-energy-zones-development-plan-directions-paper.pdf
VIC | REZ | Victoria Central North REZ minor augmentations | AEMO on behalf of Victorian Government | Committed | The two Central North REZ minor augmentations include: - Establishing an automatic generator runback control scheme to manage thermal loading on the Dederang – Glenrowan – Shepparton – Bendigo 220 kV lines. - Installing a control scheme that automates the enablement of the additional cooling on the Dederang No.3 330/220 kV transformer, thereby allowing the 340 MVA short term rating to be used at all times, effectively increasing the transformer rating from 240 MVA to 340 MVA. | 12 MW. | Not applicable | Other - funding approved | Construction has not started | Not applicable | 2025-10-01 | 2025-10-01 | AEMO. Victorian Annual Planning Report 2022, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2022/2022-victorian-annual-planning-report.pdf?la=en Victorian State Government, Environment, Land, Water and Planning. Victorian Renewable Energy Zones Development Plan Directions Paper, at https://www.energy.vic.gov.au/__data/assets/pdf_file/0028/580618/Victorian-Renewable-energy-zones-development-plan-directions-paper.pdf
NSW | New Transmission | HumeLink | Transgrid | Actionable ISP | - New Gugaa 500/330 kV Substation and 330 kV connection to the existing Wagga Wagga Substation - Three 500 kV transmission circuits and shunt reactors: - Between Maragle and Bannaby 500 kV Substation, 120 MVAr shunt reactor at both ends, - Between Maragle and Gugaa 500 kV Substation, 100 MVAr shunt reactor at Maragle end and - Between Gugaa and Bannaby 500 kV Substation, 120 MVAr shunt reactors at both ends. These circuits will be built on double circuit transmission structures. - Three new 500/330/33 kV 1,500 MVA transformers at Maragle Substation and two new 500/330/33 kV 1,500 MVA transformers at new Gugaa Substation - Augment the Maragle Substation to accommodate the additional transmission lines - Augment the existing Substations at Wagga Wagga and Bannaby to accommodate the additional transmission lines/transformers. | SNSW to CNSW: 2,200 MW in both directions. | Not applicable | CPA lodged | Construction has not started | 2024-07-01 | TBC | 2026-07-01 | AER. Determination - HumeLink - August 2022, at https://www.aer.gov.au/system/files/AER%20-%20Determination%20-%20HumeLink%20-%20August%202022.pdf Transgrid. Transgrid - HumeLink, at https://www.Transgrid.com.au/projects-innovation/humelink AEMO. 2022 Integrated Systems Plan (ISP) - Appendix 5. Network Investments, at https://aemo.com.au/-/media/files/major-publications/isp/2022/2022-documents/a5-network-investments.pdf?la=en Transgrid. Transmission Annual Planning Report - October 2022, at https://www.Transgrid.com.au/media/jn4klv4s/tgr12164-tapr-2022-v5-4-final.pdf As advised by Transgrid
VIC | Transmission | Western Renewables Link | AEMO Victorian Planning | Anticipated | The Western Renewables Link consists of: - A new 500 kV double circuit transmission line from Sydenham Terminal Station to Bulgana Terminal Station with switched shunt line reactors at the end of each circuit (approximately 70 MVAr). - Extension of the 500 kV Sydenham Terminal Station by two breaker and a half switched bays - Additional 100 MVAr at 500 kV switched bus reactor at Sydenham Terminal Station. - Rerouting of the existing No. 1 Sydenham to South Morang and Sydenham to Keilor 500 kV transmission lines to terminate into new bays. - Construction of new 220 kV circuit breakers and a second 220 kV bus at Bulgana Terminal Station. - A new 500 kV switchyard at Bulgana Terminal Station with two new 500/220 kV 1,000 MVA transformers, transmission line realignment, site provisioning and line cut in works for the existing Bulgana to Horsham 220 kV transmission line and Crowlands to Bulgana 220kV transmission line. - Cut-in, termination and switching of the existing Ballarat to Moorabool No.2 220 kV transmission line at Elaine Terminal Station, forming Ballarat to Elaine No.2 line and Elaine to Moorabool No.2 line. - Re-alignment and switching of the existing Ballarat to Elaine transmission line and Elaine to Moorabool transmission lines at Elaine Terminal Station and renaming them to Ballarat to Elaine No.3 line and Elaine to Moorabool No.3 line. - Implement new Special Control Schemes and/or amend some existing ones at multiple stations. - Validation of the capabilities of the existing earthing systems at multiple stations and the connected 220 kV transmission lines optic ground wire and/or earth wire. | REZ V3: +1,460 MW. | Not applicable | RIT-T complete | Construction has not started | Not applicable | 2027-07-01 | 2027-07-01 | AEMO, Western Renewables Link Project Analysis for the purposes of clause 5.16.4(z3) of the National Electricity Rules Nov 2022 , at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/victorian_transmission/2022/aemo--clause-5164z3-analysis--wrl-project--november-2022.pdf?la=en&hash=6C69FC7AAEB1C36FE0A3F65AC99BB614 AEMO, VNI West Project Assessment Conclusions Report Volume 1: Identifying the preferred option for VNI West, May 2023 https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/victorian_transmission/vni-west-rit-t/reports-and-updates/vni-west-pacr-volume-1.pdf?la=en AusNet, Project Overview August 2022, at https://www.westernrenewableslink.com.au/assets/resources/Project-overview-August-2022.pdf Victoria Government Gazette, No. S 267 Saturday 27 May 2023 at https://www.gazette.vic.gov.au/gazette/Gazettes2023/GG2023S267.pdf As advised by AEMO Victorian Planning
NSW | New transmission, synchronous condensers | Central-West Orana REZ Transmission Link | EnergyCo | Anticipated | - New Merotherie 500/330 kV substation with 4 x 500/330/33 kV 1,500 MVA transformers. - New 330 kV Uarbry East, Uarbry West and Elong Elong switching stations. - New 500 kV Wollar switching station. - 2 x 500 kV DCST line from Wollar to Merotherie with Quad Orange conductor. - 1 x 330 kV DCST from Merotherie to Uarbry East with Twin Olive conductor. - 1 x 330 kV DCST from Merotherie to Uarbry West with Twin Olive conductor - 2 x 500 kV DCST and initially operated at 330 kV from Merotherie to Elong Elong with Quad Orange conductor. - 3 x 250 MVAr synchronous condensers at Elong Elong switching station. - 4 x 250 MVAr synchronous condensers at Merotherie substation. - Provision of switch bays for future generator connections (cost estimation is not required) - An additional 330 kV SCST line from Bayswater to Liddell. - An additional 330 kV SCST line from Mt Piper to Wallerawang. *possible expansion to Uungula is subject to review and refinement as part of detailed design review, Network Operator tender and the authorisation process | At least 3,000 MW increase to network capacity in the Central-West Orana Renewable Energy Zone (REZ). | Not applicable | Other- funding process has not started | Construction has not started | Not applicable | Sep-27 | Sep-27 | As advised by EnergyCo. EnergyCo. Central-West Orana Renewable Energy Zone Transmission project - Scoping Report, at https://majorprojects.planningportal.nsw.gov.au/prweb/PRRestService/mp/01/getContent?AttachRef=PDA-48312206%2120220908T233216.666%20GMT EnergyCo. Central-West Orana Transmission Project, at https://www.energyco.nsw.gov.au/cwo EnergyCo. Network Infrastructure Strategy (NIS) - May 2023, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/network-infrastructure-strategy.pdf EnergyCo. Network Infrastructure Strategy (NIS) - Appendices, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-a-network-infrastructure-strategy_0.pdf https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-b-network-infrastructure-strategy.pdf
NSW | New transmission | Sydney Ring (Reinforcing Sydney, Newcastle, and Wollongong Supply) - Option 1: Sydney Ring Northern 500 kV loop (Hunter Transmission Project 1.0) | EnergyCo | Actionable NSW | Option 1: Sydney Ring Northern 500 kV loop (Hunter Transmission Project 1.0): - A new 500 kV double circuit line between Eraring and Bayswater substations - Two 500/330 kV 1,500 MVA transformers either at Eraring substation or new substation near Eraring. - Bayswater and Eraring substation augmentation work to accommodate the additional transmission line | CNSW to SNW: 5,000 MW increased in network capacity (this capacity increase for accommodation of additional new generation from North of Bayswater and 2/3 generation from Central West NSW). | 2021-06-01 | Other- funding process has not started | Construction has not started | Not applicable | Dec-27 | Dec-27 | AEMO. 2022 Integrated Systems Plan (ISP) - Appendix 5. Network Investments, at https://aemo.com.au/-/media/files/major-publications/isp/2022/2022-documents/a5-network-investments.pdf?la=en EnergyCo. Network Infrastructure Strategy May 2023, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/network-infrastructure-strategy.pdf EnergyCo. Network Infrastructure Strategy (NIS) - Appendices, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-a-network-infrastructure-strategy_0.pdf https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-b-network-infrastructure-strategy.pdf As advised by EnergyCo.
NSW | New transmission | Sydney Ring (Reinforcing Sydney, Newcastle, and Wollongong Supply) - Option 2: Sydney Ring Southern 500 kV loop | Transgrid | Alternate Option | Option 2: Sydney Ring Southern 500 kV loop: - A new 500 kV double-circuit line from the Bannaby substation to locality of South Creek (scope to be finalised by Transgrid) - Establish 500/330 kV substation in the locality of South Creek. - Cut-in both Eraring – Kemps Creek 500 kV circuits at the new substation in the locality of South Creek. - Two new 500/330 kV 1,500 MVA transformers at the new substation in the locality of South Creek. - Replace a section of existing Bannaby-Sydney West 330 kV to double-circuit line between the locality of South Creek and Sydney West. - Uprate the existing line between Bannaby and the locality of South Creek from 85°C to 100°C operating temperature. - Cut-in Bayswater – Sydney West 330 kV line at South Creek. - Cut-in Regentville – Sydney West 330 kV line at South Creek. Note: The option chosen should consider other minor network upgrades and the feasibility of a SIPS to provide a staged delivery of transfer capacity (e.g. using the Waratah Super Battery as a virtual transmission line). | CNSW to SNW: 4,500 MW increased in network capacity (This capacity increase for accommodation of additional new generation from South of Bannaby and 1/3 generation from Central West NSW). | Not applicable | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | AEMO. 2022 Integrated Systems Plan (ISP) - Appendix 5. Network Investments, at https://aemo.com.au/-/media/files/major-publications/isp/2022/2022-documents/a5-network-investments.pdf?la=en EnergyCo. Network Infrastructure Strategy May 2023, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/network-infrastructure-strategy.pdf EnergyCo. Network Infrastructure Strategy (NIS) - Appendices, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-a-network-infrastructure-strategy_0.pdf https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-b-network-infrastructure-strategy.pdf As advised by Transgrid and EnergyCo.
NSW | New Transmission | New England REZ Transmission Link | EnergyCo | Actionable NSW | - New Central South (Hub 1) 500/330 kV substation with 3 x 500/330/33 kV 1,500 MVA transformers - New 330 kV South (Hub3) and East (Hub 4) switching stations - New 330 kV Central (Hub5) switching station and cut into the existing lines between Tamworth and Armidale - New 500 kV built and initially 330 kV operated DCST line from Central (Hub5) to Central South (Hub1) with Quad Orange conductor - New 330 kV DCST line between Central South (Hub 1) and South (Hub 3) with Twin Olive conductor - New 500 kV DCST line between Central South (Hub 1) and Bayswater with Quad Orange conductor - New 330 kV DCST line between Central South (Hub 1) and East (Hub 4) with Twin Olive conductor - 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500kV DCST line between Hub 3 and Bayswater - New phase shifting transformers at Central switching station | 2,400 MW increase to network capacity in the New England Renewable Energy Zone (REZ). | 2021-06-01 | Other - funding pending | Construction has not started | Not applicable | Sep-28 | Sep-28 | AEMO. 2022 Integrated Systems Plan (ISP) - Appendix 5. Network Investments, at https://aemo.com.au/-/media/files/major-publications/isp/2022/2022-documents/a5-network-investments.pdf?la=en EnergyCo. Network Infrastructure Strategy (NIS) - May 2023, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/network-infrastructure-strategy.pdf EnergyCo. Network Infrastructure Strategy (NIS) - Appendices, at https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-a-network-infrastructure-strategy_0.pdf https://www.energyco.nsw.gov.au/sites/default/files/2023-05/appendix-b-network-infrastructure-strategy.pdf As advised by EnergyCo.
QLD | New transmission | CopperString 2032 | Powerlink | Anticipated | The CopperString 2032 project consists of: - Establish a new 500 kV substation south of Townsville (NQ 500 kV Substation) - Install 2x500/275 kV, 1500 MVA transformers at NQ 500kV substation - Establish a new NQ 275 kV Substation - Cut-in the Strathmore to Ross 275kV DCST and SCST lines to the NQ 275kV substation. - Establish a new 500 kV substation at Hughenden with associated switchgear and bays. - Establish a new 500kV substation (mid-point between NQ 500 kV and Hughenden substations) with associated switchgear and bays. - A new 500 kV transmission line from south of Townsville to Hughenden - A new 330 kV transmission line from Hughenden to Cloncurry - A new 220 kV transmission line from Cloncurry to Mount Isa - Up to six new substation sites (Only the 500 kV transmission line from south of Townsville to Hughenden to be modelled for the purpose of the 2023 reliability assessments and the 2024 Integrated System Plan). | 1,500 MW This network capacity increase is limited by the existing 275 kV network at the point of connection (i.e. the 500/275kV substation south of Townsville). | Not applicable | Other- partially funded | Construction has not started | 2024-12-01 | 30-Jun-29 | 30-Jun-29 | Powerlink. 2022 Transmission Annual Planning Report (TAPR), at https://www.powerlink.com.au/sites/default/files/2022-10/Transmission%20Annual%20Planning%20Report%202022%20-%20Full%20report.pdf Queensland Government, Queensland Energy and Jobs Plan - September 2022: https://www.epw.qld.gov.au/__data/assets/pdf_file/0029/32987/queensland-energy-and-jobs-plan.pdf Powerlink CopperString factsheet: https://www.powerlink.com.au/sites/default/files/2023-06/CopperString-Factsheet-20230621.pdf
VIC, TAS | New Interconnector | Marinus Link - Stage 1 | TasNetworks, Marinus Link Pty Ltd | Actionable ISP | Option 1 (Marinus Link – Stage 1) - A 750 MW symmetrical monopole HVDC link between Burnie area in Tasmania and Hazelwood area in Victoria. - A new 750 MW HVDC symmetrical monopole converter station in Burnie area. - A new 750 MW HVDC symmetrical monopole converter station in Hazelwood area. - A new 220 kV switching station at Heybridge adjacent to the converter station. - A new 220 kV switching station at Staverton. - A new double-circuit 220 kV alternative current (ac) transmission line from Staverton to Heybridge via Hampshire and Burnie. - A new double-circuit 220 kV ac transmission line from Palmerston to Sheffield with decommissioning of the existing single circuit line. - Cut-in both Sheffield-Mersey Forth double circuit 220 kV lines at Staverton. - Capacity increase of the four Sheffield–Staverton 220 kV transmission circuits. - A new 500 kV connection from converter station in Hazelwood area. - Decommissioning of the existing 220 kV single circuit 220 kV Burnie-Sheffield line. - Radialisation of the 110 kV Burnie-Emu Bay-Ulverstone-Sheffield network. | Marinus Link: 750 MW in both directions. Basslink and Marinus Link Stage 1 combined: VIC to TAS +962 MW, TAS to VIC +1,212 MW. (Combined transfer limit from VIC to TAS 462+500=962 MW. This is on an assumption that largest single contingency in Tasmania capped at 500 MW) | Not Applicable | PACR complete | Construction has not started | 2023-24 | 2028-12-01 | 2029-07-01 | TasNetworks, Annual Planning Report 2022, at https://www.tasnetworks.com.au/config/getattachment/a06436d3-a427-42f5-9bbc-230ee85ebd5c/annual-planning-report-2022.pdf As advised by TasNetworks and Marinus Link.
VIC, TAS | New Interconnector | Marinus Link - Stage 2 | TasNetworks, Marinus Link Pty Ltd | Actionable ISP | Option 2 (Marinus Link – Stage 2) - An additional 750 MW symmetrical monopole HVDC link between Burnie area in Tasmania and Hazelwood area in Victoria. - An additional new 750 MW HVDC symmetrical monopole converter station in Burnie area. - An additional new 750 MW HVDC symmetrical monopole converter station in Hazelwood area. - A new double-circuit 220 kV transmission line from Heybridge to Sheffield. - A new 500 kV connection from converter station in Hazelwood area. Pre-requisite: Option 1 (Marinus Link – Stage 1). | Marinus Link: 750 MW in both directions. Basslink and Marinus Link Stages 1 and 2 combined: VIC to TAS +1,712 MW, TAS to VIC +1,962 MW. (Combined transfer limit from VIC to TAS 462+625+625=1,712 MW. This is on an assumption that largest single contingency in Tasmania capped at 500 MW. Following an outage of Marinus Link cable, the remaining Marinus Link cable increases the transfer by 125 MW to its maximum transfer capacity of 750 MW. This will limit reduction in transfer from VIC to TAS to 500 MW). | Not applicable | PACR complete | Construction has not started | 2023-24 | 2030-12-01 | 2031-07-01 | TasNetworks, Annual Planning Report 2022, at https://www.tasnetworks.com.au/config/getattachment/a06436d3-a427-42f5-9bbc-230ee85ebd5c/annual-planning-report-2022.pdf As advised by TasNetworks and Marinus Link.
VIC,NSW | Transmission | VNI West | AEMO Victorian Planning, Transgrid | Actionable ISP | VNI West North of Kerang, the preferred option in the PACR, consists of: - A new 500 kV double-circuit overhead line from Bulgana to near Kerang to locality of Dinawan, including series compensation on the line near Kerang. - Construction of the Dinawan to near Wagga Wagga line as a double-circuit 500 kV line, rather than a double-circuit 330 kV line and later uprate from 330 kV to 500 kV operation (including new 500 kV bays and a transformer station near Wagga Wagga). - Establish Dinawan 500 kV switchyard with two 500/330 kV 1,500 MVA transformers. - Establish new terminal station near Kerang with two 500/220 kV 1,000 MVA transformers. - 220 kV connections from the new terminal station near Kerang to the existing 220 kV lines near Kerang. - Modular power flow controllers to prevent overloading on 330 kV lines between Upper/Lower Tumut and South Morang and 220 kV lines between Dederang and Thomastown following certain contingencies. - 500 kV line shunt reactors at both ends of the three following 500 kV circuits: (i) Bulgana – near Kerang, (ii) near Kerang – Dinawan and (iii) Dinawan – near Wagga Wagga. - Up to +/- 400 MVAr dynamic reactive compensation at the new 220 kV terminal station near Kerang. - Approximately 100 MVAr 500 kV switched bus connected reactor at Sydenham. - In addition, series compensation or additional power flow controllers would be installed along the Kerang to Bulgana section to reduce impedance on the new 500 kV network and thereby improve network load sharing with, and manage network loading on, the existing 330 kV Victoria – New South Wales Interconnector and the existing 220 kV western Victoria network between Bendigo and Kerang, in the absence of a new terminal station and connection near Bendigo. Work is ongoing to confirm the technical feasibility of this solution. | Indicative impact on transfer capability: VIC - NSW +1,935 MW. NSW - VIC +1,669 MW. Increase REZ network capacity for V2, V3 and N5. | Not applicable | PACR complete | Construction has not started | Early 2026 | 2028 | Dec-29 | AEMO Transgrid , Victoria to New South Wales Interconnector West Regulatory Investment Test for Transmission Project Assessment Draft Report , at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/victorian_transmission/vni-west-rit-t/vni-west-project-assessment-draft-report.pdf?la=en AEMO, VNI West Project Assessment Conclusions Report Volume 1: Identifying the preferred option for VNI West, May 2023 https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/victorian_transmission/vni-west-rit-t/reports-and-updates/vni-west-pacr-volume-1.pdf?la=en As advised by Transgrid and AEMO Victorian Planning.
QLD | New transmission and transformer | Gladstone Grid Reinforcement | Powerlink | Future ISP - preparatory activities requested | - New 275 kV double-circuit line between Calvale and Calliope River. - Rebuild Calliope River – Larcom Creek 275 kV as a double-circuit line. - Rebuild Larcom Creek – Bouldercombe 275 kV as a double-circuit line with one line tapped at Raglan. - A new (third) 275/132 kV transformer at Calliope River. (This option has been replaced with a "high-capacity" option in the 2023 Transmission Expansion Options Report. Please refer to the report for more details) | CNQ to GG: 550 MW, GG to CNQ: 500 MW. | 2021-06-30 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | Powerlink. Preparatory Activities - Gladstone Grid Reinforcement, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/isp/2021/preparatory-activities-gladstone-grid-reinforcement.pdf?la=en AEMO, 2023 Transmission Expansion Options Report, at https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation. The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
QLD | New transmission | Central to Southern Queensland | Powerlink | Future ISP - preparatory activities requested | - A new 275 kV double-circuit line between Calvale and Wandoan South. - 275 kV line shunt reactors at both ends of Calvale – Wandoan South 275 kV circuits. | 900 MW (in both directions of CQ to SQ) | 2021-06-01 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | Powerlink. Preparatory Activities - CQSQ Transmission Link, at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/isp/2021/preparatory-activities-cqsq-transmission-link.pdf?la=en
QLD | Transformer replacement, SIPS/runback scheme and SEQ 300 MW BESS | Darling Downs REZ Expansion - Stage 1 | Powerlink | Future ISP - preparatory activities requested | Option 1: - Replace existing 1,300 MVA 330/275 kV transformer at Middle Ridge with 1,500 MVA 330/275 kV transformer. Option 2: - Implement a limit extension special protection scheme – run-back of generation in SWQ with 300MW BESS response in SEQ (similar to a virtual transmission line). | Option 1: 500 MW Option 2: 330 MW | 2023-06-30 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | Powerlink. 2022 Transmission Annual Planning Report (TAPR), at https://www.powerlink.com.au/sites/default/files/2022-10/Transmission%20Annual%20Planning%20Report%202022%20-%20Full%20report.pdf The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
QLD, NSW | New Transmission | QNI Connect - 330 kV Options | Powerlink, Transgrid | Future ISP - preparatory activities requested | Option 1 - A new 330 kV single-circuit line from locality of New England Hub 5 to Dumaresq to Bulli Creek to Braemar. - A new 330/275 kV transformer at Braemar. - 330 kV Line shunt reactor at New England Hub 5, Dumaresq, Bulli Creek, and Braemar for the New England Hub 5 – Dumaresq - Bulli Creek - Braemar 330 kV circuits. (Pre-requisite: Cut-in both Tamworth-Armidale 330 kV lines to a new substation in locality of New England Hub 5). Option 2 - A new 330 kV double-circuit line from locality of New England Hub 5 to Dumaresq to Bulli Creek to Braemar. - A new 330/275 kV transformer at Braemar. - 330 kV Line shunt reactors at New England Hub 5, Dumaresq, Bulli Creek, and Braemar, for the 330 kV lines between New England Hub 5 and Braemar (via Dumaresq and Bulli Creek). (Pre-requisite: Cut-in both Tamworth-Armidale 330 kV lines to a new substation in locality of New England Hub 5). Option 3 - A Virtual Transmission Line option with a 200 MW energy storage system south of Armidale and north of Braemar. | Option 1: 730 MW (NNSW to SQ) 900 MW (SQ to NNSW) Option 2: 1,260 MW (NNSW to SQ) 1,700 MW (SQ to NNSW) Option 3: 200 MW (in both directions of NNSW to SQ) | Jun-21 completed by Powerlink Jun-23 updated by Powerlink Jun-23 completed by Transgrid | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | As advised by Transgrid and Powerlink. The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
QLD, NSW | New Transmission | QNI Connect - 500 kV option | Powerlink, Transgrid | Future ISP - preparatory activities requested | - Establish a new substation in NNSW and to New England REZ Hub 5. - A new 500/275 kV transformer at Halys substation - A new 500 kV double-circuit line between Halys and new Dumaresq 500 kV substation. - A new 500 kV double-circuit line between new Dumaresq and New England REZ Hub 5. - 2 x 500/330 kV transformers connecting to 330kV Dumaresq. Pre-requisite: CQ-SQ Option 5 (QEJP), CNSW-NNSW Option 1. | 3,000 MW (NNSW to SQ) 2,500 MW (SQ to NNSW) | 2023-06-01 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | As advised by Transgrid and Powerlink. AEMO, 2023 Transmission Expansion Options Report, at https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation. The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
VIC | REZ | South West Victoria REZ Expansion (SWV1) | AEMO | Future ISP - preparatory activities requested | Option 1: Moorabool-Geelong 220 kV line upratings via terminal station augmentations. Option 1A: New 500 kV single-circuit line from Mortlake-Moorabool, Sydenham line upratings. Option 1B: Moorabool-Sydenham 500 kV single-circuit. Option 1C: Heywood-Mortlake 500 kV single-circuit. Option 2A: New Mortlake-Bulgana 500 kV single-circuit. Option 2B: New Mortlake-Bulgana 500 kV double-circuit. Option 3A: New Heywood-Bulgana 500 kV single-circuit, New Alcoa Portland-Heywood 500 kV single circuit. Option 3B: New Heywood-Bulgana 500 kV double-circuit, New Alcoa Portland-Heywood 500 kV single-circuit. Pre-requisites for Option 1A to 3B: Option 1. | Option 1A: REZ V4: +1,500 MW Option 1B: REZ V4: +1,750 MW Option 1C: REZ V4: +1,750 MW Option 2A: REZ V4: +1,950 MW Option 2B: REZ V4: +2,900 MW Option 3A: Increased REZ network capacity for V4 and V8 by 1,800 MW Option 3B: Increased REZ network capacity for V4 and V8 2,800 MW | 2023-06-01 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | AEMO, 2022 Integrated System Plan appendix a5 network investments, at https://aemo.com.au/-/media/files/major-publications/isp/2022/2022-documents/a5-network-investments.pdf?la=en The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
SA | New line | Mid North SA REZ Expansion | ElectraNet | Future ISP - preparatory activities requested | - Build a 275 kV double-circuit line between Bundey and Para. - Build a 275 kV double-circuit line from Brinkworth to cut into Bungama-Blyth West 275 kV circuit. - Disconnect existing Waterloo-Templers 132 kV line at each end. - Build a 132 kV single-circuit line from Templers West to Templers. - 1 x 160 MVA, 275/132 kV transformer at Templers West. | 900 MW | 2023-06-30 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | ElectraNet. 2022 Transmission Annual Planning Report (TAPR), at https://www.electranet.com.au/wp-content/uploads/221117_ENet-TAPR_A4_WEB.pdf The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.
SA | New line | South East SA REZ Expansion - Stage 1 | ElectraNet | Future ISP - preparatory activities requested | - String vacant circuit on the 275 kV Tungkillo – Tailem Bend line. | 120 MW | 2023-06-30 | Other- funding process has not started | Construction has not started | Not applicable | Not applicable | Not applicable | ElectraNet. 2022 Transmission Annual Planning Report (TAPR), at https://www.electranet.com.au/wp-content/uploads/221117_ENet-TAPR_A4_WEB.pdf The preparatory activity reports provided to AEMO by the TNSP can be found on the 2023 Transmission Expansion Options Report Consultation page https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation.