## Introduction
Detailed NPV analysis
This spreadsheet presents the detailed NPV results for the post RIT-T analysis.
The "Tables" tag contains links to the origional data used to derive the NPV results given in the publication.
The table presents the:
~ Load at risk (MW) - which is the MW load shedding required to avoid the network limitation under the highest POE demand conditions and highest impacting scenario of the presented assessment
~Load at risk reduction (MW) - which is the MW load shedding reduction under the highest POE demand conditions and highest impacting scenario of the presented assessment as a result of implementing the respective credible option
~ Energy at risk (MWh) - which is the MWh unserved energy required to avoid the network limitation under the highest POE demand conditions and highest impacting scenario of the presented assessment
~ Energy at risk reduction (MWh) - which is the MWh unserved energy reduction under the highest POE demand conditions and highest impacting scenario of the presented assessment as a result of implementing the respective credible option
~ Expected unserved energy (MWh) - which is the portion of the energy at risk after taking into account the probability of the limitation occurring, including the probability of demand conditions occurring and weighted across the reasonable scenarios considered in the presented assessment
~ Expected unserved energy reduction (MWh) - which is the portion of the energy at risk reduction after taking into account the probability of the limitation occurring, including the probability of demand conditions occurring and weighted across the reasonable scenarios considered in the presented assessment as a result of implementing the respective credible option
~ Limitation cost ($ '000 or $M) - which is the cost of the sum of the expected unserved energy, obtained by multiplying the expected unserved energy by the VCR
~ Option cost ($ '000 or $M) - which is the cost of implementing, operating and maintaining an option
~ Remaining limitation cost ($ '000 or $M) - which is the cost of the remaining expected unserved energy after implementing an option, obtained by multiplying the expected unserved energy by the VCR
~ Gross Market Benefit($ '000 or $M) - which is the benefit from expected unserved energy reduction by an option, obtained by multiplying the expected unserved energy reduction by the VCR
~ Net Market Benefit($ '000 or $M) - which is the net market benefit from an option, obtained by subtracting the option cost from the gross market benefit the option can deliver
~ Project cost ($ '000 or $M) - which is the same as option cost in present value

## Tables
Table 3 | [6 empty] | Table 5
Year | Load at risk (MW) | Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ million) |  |  | Option | Project cost | Weighted gross market benefit | Net market benefit | Ranking under RIT-T
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 |  |  | Option 2 | 34.2644 | 130.6418 | 96.3773 | 1
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497 |  |  | Option 3a | 44.847 | 129.059 | 84.2121 | 4
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349 |  |  | Option 3b | 56.0587 | 140.9489 | 84.8901 | 3
2017-18 | 128.22 | 609.91 | 137.952 | 8.5972 |  |  | Option 3c | 61.0168 | 143.4196 | 82.4028 | 5
2018-19 | 137.21 | 712.39 | 174.9575 | 10.9034 |  |  | Option 3d | 50.1601 | 142.7154 | 92.5553 | 2
2019-20 | 159.07 | 879.61 | 157.2912 | 9.8024
2020-21 | 165.92 | 967.25 | 187.6502 | 11.6944
2021-22 | 185.58 | 1227.72 | 230.505 | 14.3651
2022-23 | 191.53 | 1410.23 | 257.5827 | 16.0526
2023-24 | 208.05 | 1617.19 | 291.0387 | 18.1375
2024-25 | 222.01 | 1625.84 | 311.018 | 19.3826
2025-26 | 236.78 | 1928.71 | 362.6683 | 22.6015
2026-27 | 251.62 | 2624.06 | 470.8553 | 29.3437
Table 6
| Do nothing | Non-network Option 3d (from 2016/17) |  |  |  | Network Option 2 (from 2018/19)
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M)
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0
2016-17 | 13.0349 | 8.8795 | 4.1553 | 2.289 | 1.8663 | 13.0349 | 0 | 0 | 0
2017-18 | 8.5972 | 3.1246 | 5.4725 | 2.289 | 3.1835 | 8.5972 | 0 | 0 | 0
2018-19 | 10.9034 | 2.1543 | 8.749 | 3.815 | 4.934 | 0.29572 | 10.6076 | 5.13 | 5.4776
2019-20 | 9.8024 | 2.7711 | 7.0313 | 3.815 | 3.2163 | 0.51708 | 9.2853 | 5.13 | 4.1553
2020-21 | 11.6944 | 3.715 | 7.9794 | 3.815 | 4.1644 | 0.80584 | 10.8885 | 5.13 | 5.7585
2021-22 | 14.3651 | 2.0428 | 12.3223 | 6.104 | 6.2183 | 1.0903 | 13.2748 | 5.13 | 8.1448
2022-23 | 16.0526 | 2.5638 | 13.4888 | 6.104 | 7.3848 | 1.5833 | 14.4693 | 5.13 | 9.3393
2023-24 | 18.1375 | 2.9249 | 15.2127 | 6.104 | 9.1087 | 2.2592 | 15.8784 | 5.13 | 10.7484
2024-25 | 19.3826 | 2.0971 | 17.2855 | 7.63 | 9.6555 | 3.1459 | 16.2367 | 5.13 | 11.1067
2025-26 | 22.6015 | 2.9111 | 19.6904 | 7.63 | 12.0604 | 4.0391 | 18.5624 | 5.13 | 13.4324
2026-27 | 29.3437 | 2.3105 | 27.0332 | 9.156 | 17.8772 | 5.0687 | 24.275 | 5.13 | 19.145
2027-28 | 34.3051 | 3.0372 | 31.2679 | 9.156 | 22.1119 | 6.5754 | 27.7297 | 5.13 | 22.5997
Residual |  |  | 320.0964 | 93.732 | 226.3644 | 0 | 287.5463 | 53.1961 | 234.3502
NPV |  |  | 142.7154 | 50.1601 | 92.5553 | 0 | 130.6418 | 34.2644 | 96.3773
Table 7
Sensitivity | Discount Rate |  | Cost |  |  |  | VCR
| 6% | 12% | 30% | -30% | 5%/-5%[1] | 15%/0%[2] | 20% | -20%
Network option 2 | 196.6 | 70.8 | 87.1 | 105.7 | 94.8 | 91.7 | 122.5 | 70.2
Non-network option 3a | 172.1201 | 61.7758 | 70.758 | 97.6661 | 86.4544 | 84.2121 | 110.0239 | 58.4002
Non-network option 3b | 176.579 | 61.641 | 68.0725 | 101.7078 | 87.6931 | 84.8901 | 113.0799 | 56.7004
Non-network option 3c | 175.2676 | 59.0697 | 64.0977 | 100.7078 | 85.4536 | 82.4028 | 111.0867 | 53.7189
Non-network option 3d | 186.5268 | 68.3904 | 77.5072 | 107.6033 | 95.0633 | 92.5553 | 121.1 | 64
Table 8
Description | Net Market Benefit ($Million) |  |  |  |  | Scenario Weighting
| Option 2 | Option 3a | Option 3b | Option 3c | Option 3d | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4
Under base scenario weightings | 96.4 | 84.2121 | 84.8901 | 82.4028 | 92.6 | 25% | 25% | 25% | 25%
Higher 220kV new generation | 71.6 | 60.3704 | 58.6705 | 55.1256 | 66.1 | 30% | 20% | 30% | 20%
Lower 220kV new generation | 121.2 | 108.0537 | 111.1098 | 109.6799 | 119 | 20% | 30% | 20% | 30%
Higher demand forecast | 109.3 | 96.9102 | 99.0421 | 96.9198 | 106.9 | 30% | 30% | 20% | 20%
Lower demand forecast | 83.4 | 71.5139 | 70.7382 | 67.8857 | 78.2 | 20% | 20% | 30% | 30%

## Assumptions
[12 empty] | Weightings |  |  |  | Capital Cost, million (annualised)
[10 empty] | VCR ($k) | Discount Rate | S1 | S2 | S3 | S4 | Network | 100MW | 80MW | 120MW | 30MW | 50MW
[9 empty] | Base | 62.32 | 10% | 25% | 25% | 25% | 25% | 5.13 | 7.63 | 6.104 | 9.156 | 2.289 | 3.815
Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations |  |  |  | D1 |  | 6%
Discount Rate | 10% | [7 empty] | D2 |  | 12%
Years | 40 |  |  | F | Full, consider all limitations. |  |  |  | C1 (30%) | [6 empty] | 6.669 | 9.919 | 7.9352 | 11.9028 | 2.9757 | 4.9595
10% POE | 0.3 | [7 empty] | C2(-30%) | [6 empty] | 3.591 | 5.341 | 4.2728 | 6.4092 | 1.6023 | 2.6705
50% POE | 0.7 | [7 empty] | V1(20%) | 74.784
S1, TSDF + 220kV new gen location | 0.25 | [7 empty] | V2(-20%) | 49.856
S2, TSDF + 500kV new genlocation | 0.25 | [7 empty] | C3(mixed 1) | [6 empty] | 5.3865 | 7.2485 | 5.7988 | 8.6982 | 2.1745 | 3.6242
S7, NEFR + 220kV new gen location | 0.25 | [7 empty] | C4(mixed 2) | [6 empty] | 5.8995 | 7.63 | 6.104 | 9.156 | 2.289 | 3.815
S8, NEFR + 500kV new gen location | 0.25
S9, TSDF no growth | 1
Network Option Cost | 5.13
Gen 80 | 6.104
Gen 100 | 7.63
Gen 120 | 9.156
Gen 30 | 2.289
Gen 50 | 3.815
Table 8: Net present value of net market benefits (PV, $M)
Sensitivity | Discount Rate |  | Cost |  |  |  | VCR
| 6% | 12% | 30% | -30% | 5%/-5% | 15%/0% | 20% | -20%
Network option 2 | 196.6 | 70.8 | 87.1 | 105.7 | 94.8 | 91.7 | 122.5 | 70.2 |  | 96.3773 |  | 90.9082
Non-network option 3a | 172.1201 | 61.7758 | 70.758 | 97.6661 | 86.4544 | 84.2121 | 110.0239 | 58.4002 |  | 84.2121 |  | 84.2121
Non-network option 3b | 176.579 | 61.641 | 68.0725 | 101.7078 | 87.6931 | 84.8901 | 113.0799 | 56.7004 |  | 84.8901 |  | 84.8901
Non-netowrk option 3c | 175.2676 | 59.0697 | 64.0977 | 100.7078 | 85.4536 | 82.4028 | 111.0867 | 53.7189 |  | 82.4028 |  | 82.4028
Non-network option3d | 186.5268 | 68.3904 | 77.5072 | 107.6033 | 95.0633 | 92.5553 | 121.1 | 64 |  | 92.5553 |  | 92.5553
diff | 10.0732 | 2.4096 | 9.5928 | -1.9033 | -0.26329 | 1.4 | 6.2
% | 5.124% | 3.403% | 11.01% | -1.801% | -0.2777% | 1.143% | 8.832%
Table 19: Net market benefits under different scenario weightings (PV, $M)
Description | Net market benefit ($, M) |  |  |  |  | Scenario weighting
| Option 2 | Option 3a | Option 3b | Option 3c | Option 3d | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 |  | Diff | %
Under current scenario weightings | 96.4 | 84.2121 | 84.8901 | 82.4028 | 92.6 | 25% | 25% | 25% | 25% |  | 3.8 | 3.942%
higher 220kV new generation | 71.6 | 60.3704 | 58.6705 | 55.1256 | 66.1 | 30% | 20% | 30% | 20% |  | 5.5 | 7.682%
Lower 220kV new generation | 121.2 | 108.0537 | 111.1098 | 109.6799 | 119 | 20% | 30% | 20% | 30% |  | 2.2 | 1.815%
Higher demand forecast | 109.3 | 96.9102 | 99.0421 | 96.9198 | 106.9 | 30% | 30% | 20% | 20% |  | 2.4 | 2.196%
Lower demand forecast | 83.4 | 71.5139 | 70.7382 | 67.8857 | 78.2 | 20% | 20% | 30% | 30% |  | 5.2 | 6.235%

## Other options
Do-Nothing means with stage 1 and stage 2, but without stage 3
Weighted cost-Benefit, with a tailored safety margin (SM) for each relevant constraint equation and 15 minute ratings
| Do nothing | Embedded gen 100 (from 2017/18) |  |  |  | Network Option (from 2018/19) |  |  |  |  | Do nothing |  |  | Embedded gen 100 (from 2017/18) |  |  | Network Option (from 2018/19)
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | BATS | BETS | Other | BATS | BETS | Other | BATS | BETS | Other
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0 | 2015-16 | 121.8 | 70.48 | 14.82 | 121.8 | 70.48 | 14.82 | 121.8 | 70.48 | 14.82
2016-17 | 13.0349 | 13.0349 | 0 | 0 | 0 | 13.0349 | 0 | 0 | 0 | 2016-17 | 137.21 | 82.53 | 18.08 | 137.21 | 82.53 | 18.08 | 137.21 | 82.53 | 18.08
2017-18 | 8.5972 | 0.16424 | 8.4329 | 7.63 | 0.80292 | 8.5972 | 0 | 0 | 0 | 2017-18 | 0 | 110.19 | 18.03 | 0 | 7.39 | 17.94 | 0 | 110.19 | 18.03
2018-19 | 10.9034 | 0.33812 | 10.5652 | 7.63 | 2.9352 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 0 | 113.53 | 23.68 | 0 | 16.96 | 23.62 | 0 | 8.24 | 19.11
2019-20 | 9.8024 | 0.53765 | 9.2647 | 7.63 | 1.6347 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-20 | 0 | 134 | 25.07 | 0 | 23.34 | 29.07 | 0 | 14.07 | 24.11
2020-21 | 11.6944 | 0.79575 | 10.8986 | 7.63 | 3.2686 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 0 | 128.15 | 37.77 | 0 | 28 | 38.16 | 0 | 21.73 | 24.96
2021-22 | 14.3651 | 1.0949 | 13.2702 | 7.63 | 5.6402 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 0 | 148.79 | 36.79 | 0 | 36.63 | 38.76 | 0 | 27.02 | 28.91
2022-23 | 16.0526 | 1.3388 | 14.7137 | 7.63 | 7.0837 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 0 | 143.82 | 47.71 | 0 | 48.99 | 48.04 | 0 | 41.09 | 37.65
2023-24 | 18.1375 | 1.7286 | 16.4089 | 7.63 | 8.7789 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 0 | 157.08 | 50.97 | 0 | 57.12 | 50.04 | 0 | 47.24 | 45.16
2024-25 | 19.3826 | 2.0971 | 17.2855 | 7.63 | 9.6555 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 0 | 166.73 | 55.28 | 0 | 61.66 | 55.2 | 0 | 55.59 | 50.29
2025-26 | 22.6015 | 2.9111 | 19.6904 | 7.63 | 12.0604 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 0 | 175.05 | 61.73 | 0 | 74.96 | 62.53 | 0 | 64.89 | 57.07
2026-27 | 29.3437 | 4.2375 | 25.1062 | 7.63 | 17.4762 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 0 | 185.32 | 66.3 | 0 | 84.83 | 66.95 | 0 | 72.16 | 60.03
2027-28 | 34.3051 | 5.2114 | 29.0937 | 7.63 | 21.4637 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 0 | 192.66 | 72.05 | 0 | 92.59 | 72.12 | 0 | 80.62 | 67.65
Residual | 353.568 | 53.7113 | 299.8567 | 78.6391 | 221.2176 | 67.7698 | 287.5463 | 53.1961 | 234.3502
NPV | 203.9768 | 63.028 | 140.9489 | 56.0587 | 84.8901 | 73.7535 | 130.6418 | 34.2644 | 96.3773
Check |  |  |  |  | 84.8901 |  |  |  | 96.3773
| Do nothing | Embedded gen 80 (from 2017/18) |  |  |  | Network Option (from 2018/19) |  |  |  |  | Do nothing |  |  | Embedded gen 80 (from 2017/18) |  |  | Network Option (from 2018/19)
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | BATS | BETS | Other | BATS | BETS | Other | BATS | BETS | Other
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0 | 2015-16 | 121.8 | 70.48 | 14.82 | 121.8 | 70.48 | 14.82 | 121.8 | 70.48 | 14.82
2016-17 | 13.0349 | 13.0349 | 0 | 0 | 0 | 13.0349 | 0 | 0 | 0 | 2016-17 | 137.21 | 82.53 | 18.08 | 137.21 | 82.53 | 18.08 | 137.21 | 82.53 | 18.08
2017-18 | 8.5972 | 0.50171 | 8.0955 | 6.104 | 1.9915 | 8.5972 | 0 | 0 | 0 | 2017-18 | 0 | 110.19 | 18.03 | 0 | 27.39 | 17.94 | 0 | 110.19 | 18.03
2018-19 | 10.9034 | 0.77013 | 10.1332 | 6.104 | 4.0292 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 0 | 113.53 | 23.68 | 0 | 32.92 | 24.39 | 0 | 8.24 | 19.11
2019-21 | 9.8024 | 1.0436 | 8.7588 | 6.104 | 2.6548 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-21 | 0 | 134 | 25.07 | 0 | 42.79 | 29.13 | 0 | 14.07 | 24.11
2020-21 | 11.6944 | 1.4825 | 10.2119 | 6.104 | 4.1079 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 0 | 128.15 | 37.77 | 0 | 56.05 | 37.85 | 0 | 21.73 | 24.96
2021-22 | 14.3651 | 2.0428 | 12.3223 | 6.104 | 6.2183 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 0 | 148.79 | 36.79 | 0 | 58.57 | 38.85 | 0 | 27.02 | 28.91
2022-23 | 16.0526 | 2.5638 | 13.4888 | 6.104 | 7.3848 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 0 | 143.82 | 47.71 | 0 | 68.44 | 47.57 | 0 | 41.09 | 37.65
2023-24 | 18.1375 | 2.9249 | 15.2127 | 6.104 | 9.1087 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 0 | 157.08 | 50.97 | 0 | 76.6 | 50.98 | 0 | 47.24 | 45.16
2024-25 | 19.3826 | 4.1566 | 15.226 | 6.104 | 9.122 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 0 | 166.73 | 55.28 | 0 | 86.28 | 55.29 | 0 | 55.59 | 50.29
2025-26 | 22.6015 | 5.1981 | 17.4034 | 6.104 | 11.2994 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 0 | 175.05 | 61.73 | 0 | 95.16 | 61.62 | 0 | 64.89 | 57.07
2026-27 | 29.3437 | 6.5462 | 22.7975 | 6.104 | 16.6935 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 0 | 185.32 | 66.3 | 0 | 104.78 | 67.11 | 0 | 72.16 | 60.03
2027-28 | 34.3051 | 7.8521 | 26.453 | 6.104 | 20.349 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 0 | 192.66 | 72.05 | 0 | 109.31 | 72.19 | 0 | 80.62 | 67.65
Residual | 353.568 | 80.9282 | 272.6398 | 62.9113 | 209.7285 | 68.1843 | 287.5463 | 53.1961 | 234.3502
NPV | 203.9768 | 74.9178 | 129.059 | 44.847 | 84.2121 | 73.8528 | 130.6418 | 34.2644 | 96.3773
Check |  |  |  |  | 84.2121 |  |  |  | 96.3773
| Do nothing | Embedded gen 120 (from 2018/19) |  |  |  | Network Option (from 2018/19) |  |  |  |  | Do nothing |  |  | Embedded gen 120 (from 2018/19) |  |  | Network Option (from 2018/19)
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | BATS | BETS | Other | BATS | BETS | Other | BATS | BETS | Other
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0 | 2015-16 | 121.8 | 70.48 | 14.82 | 121.8 | 70.48 | 14.82 | 121.8 | 70.48 | 14.82
2016-17 | 13.0349 | 13.0349 | 0 | 0 | 0 | 13.0349 | 0 | 0 | 0 | 2016-17 | 137.21 | 82.53 | 18.08 | 137.21 | 82.53 | 18.08 | 137.21 | 82.53 | 18.08
2017-18 | 8.5972 | 0.10516 | 0 | 0 | 0 | 8.5972 | 0 | 0 | 0 | 2017-18 | 0 | 110.19 | 18.03 | 0 | 110.19 | 18.03 | 0 | 110.19 | 18.03
2018-19 | 10.9034 | 0.15597 | 10.7474 | 9.156 | 1.5914 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 0 | 113.53 | 23.68 | 0 | 0 | 24.48 | 0 | 8.24 | 19.11
2019-20 | 9.8024 | 0.31035 | 9.492 | 9.156 | 0.33604 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-20 | 0 | 134 | 25.07 | 0 | 19.17 | 29.06 | 0 | 14.07 | 24.11
2020-21 | 11.6944 | 0.49199 | 11.2024 | 9.156 | 2.0464 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 0 | 128.15 | 37.77 | 0 | 23.58 | 34.56 | 0 | 21.73 | 24.96
2021-22 | 14.3651 | 0.60407 | 13.761 | 9.156 | 4.605 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 0 | 148.79 | 36.79 | 0 | 16.73 | 38.76 | 0 | 27.02 | 28.91
2022-23 | 16.0526 | 0.84319 | 15.2094 | 9.156 | 6.0534 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 0 | 143.82 | 47.71 | 0 | 23.96 | 47.58 | 0 | 41.09 | 37.65
2023-24 | 18.1375 | 1.0869 | 17.0506 | 9.156 | 7.8946 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 0 | 157.08 | 50.97 | 0 | 31.75 | 49.95 | 0 | 47.24 | 45.16
2024-25 | 19.3826 | 1.3616 | 18.0211 | 9.156 | 8.8651 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 0 | 166.73 | 55.28 | 0 | 43.58 | 55.33 | 0 | 55.59 | 50.29
2025-26 | 22.6015 | 1.6749 | 20.9266 | 9.156 | 11.7706 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 0 | 175.05 | 61.73 | 0 | 55.11 | 61.66 | 0 | 64.89 | 57.07
2026-27 | 29.3437 | 2.3105 | 27.0332 | 9.156 | 17.8772 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 0 | 185.32 | 66.3 | 0 | 59.76 | 66.3 | 0 | 72.16 | 60.03
2027-28 | 34.3051 | 3.0372 | 31.2679 | 9.156 | 22.1119 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 0 | 192.66 | 72.05 | 0 | 69.61 | 71.49 | 0 | 80.62 | 67.65
Residual | 353.568 | 31.3034 | 322.2646 | 94.3669 | 227.8977 | 68.1843 | 287.5463 | 53.1961 | 234.3502
NPV | 203.9768 | 54.7571 | 143.4196 | 61.0168 | 82.4028 | 73.8528 | 130.6418 | 34.2644 | 96.3773
| Do nothing | Embedded gen 30 (from 2015/16) |  |  |  | Network Option (from 2018/19) |  |  |  |  | Do nothing |  |  | Embedded gen 30 (from 2015/16) |  |  | Network Option (from 2018/19)
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | BATS | BETS | Other | BATS | BETS | Other | BATS | BETS | Other
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54
2015-16 | 20.497 | 13.9023 | 6.5947 | 2.289 | 4.3057 | 20.497 | 0 | 0 | 0 | 2015-16 | 121.8 | 70.48 | 14.82 | 121.84 | 40.46 | 14.82 | 121.8 | 70.48 | 14.82
2016-17 | 13.0349 | 8.8795 | 4.1553 | 2.289 | 1.8663 | 13.0349 | 0 | 0 | 0 | 2016-17 | 137.21 | 82.53 | 18.08 | 137.19 | 52.48 | 18.12 | 137.21 | 82.53 | 18.08
2017-18 | 8.5972 | 3.1246 | 5.4725 | 2.289 | 3.1835 | 8.5972 | 0 | 0 | 0 | 2017-18 | 0 | 110.19 | 18.03 | 0 | 77.39 | 17.94 | 0 | 110.19 | 18.03
2018-19 | 10.9034 | 4.0255 | 6.8778 | 2.289 | 4.5888 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 0 | 113.53 | 23.68 | 0 | 83.42 | 23.81 | 0 | 8.24 | 19.11
2019-20 | 9.8024 | 5.0902 | 4.7122 | 2.289 | 2.4232 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-20 | 0 | 134 | 25.07 | 0 | 93.35 | 29.07 | 0 | 14.07 | 24.11
2020-21 | 11.6944 | 6.1708 | 5.5236 | 2.289 | 3.2346 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 0 | 128.15 | 37.77 | 0 | 114.21 | 35.18 | 0 | 21.73 | 24.96
2021-22 | 14.3651 | 7.086 | 7.2791 | 2.289 | 4.9901 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 0 | 148.79 | 36.79 | 0 | 105.4 | 38.76 | 0 | 27.02 | 28.91
2022-23 | 16.0526 | 8.6707 | 7.3818 | 2.289 | 5.0928 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 0 | 143.82 | 47.71 | 0 | 116.01 | 47.57 | 0 | 41.09 | 37.65
2023-24 | 18.1375 | 10.0078 | 8.1297 | 2.289 | 5.8407 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 0 | 157.08 | 50.97 | 0 | 123.74 | 49.95 | 0 | 47.24 | 45.16
2024-25 | 19.3826 | 11.3926 | 7.99 | 2.289 | 5.701 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 0 | 166.73 | 55.28 | 0 | 136.72 | 56.08 | 0 | 55.59 | 50.29
2025-26 | 22.6015 | 13.6323 | 8.9692 | 2.289 | 6.6802 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 0 | 175.05 | 61.73 | 0 | 144.97 | 61.83 | 0 | 64.89 | 57.07
2026-27 | 29.3437 | 17.2994 | 12.0443 | 2.289 | 9.7553 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 0 | 185.32 | 66.3 | 0 | 151.28 | 66.3 | 0 | 72.16 | 60.03
2027-28 | 34.3051 | 20.241 | 14.0641 | 2.289 | 11.7751 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 0 | 192.66 | 72.05 | 0 | 162.77 | 72.31 | 0 | 80.62 | 67.65
Residual | 348.5724 | 205.6678 | 142.9047 | 23.2584 | 119.6463 | 68.1843 | 287.5463 | 53.1961 | 234.3502
NPV | 202.7809 | 123.9844 | 78.7965 | 20.3493 | 58.4472 | 73.8528 | 130.6418 | 34.2644 | 96.3773
Check |  |  |  |  | 58.4472 |  |  |  | 96.3773
| Do nothing | Embedded gen 50 (from 2015/16) |  |  |  | Network Option (from 2018/19) |  |  |  |  | Do nothing |  |  | Embedded gen 50 (from 2015/16) |  |  | Network Option (from 2019/20)
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | BATS | BETS | Other | BATS | BETS | Other | BATS | BETS | Other
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54 | 67.63 | 96.45 | 11.54
2015-16 | 20.497 | 10.6987 | 9.7984 | 3.815 | 5.9834 | 20.497 | 0 | 0 | 0 | 2015-16 | 121.8 | 70.48 | 14.82 | 121.88 | 20.49 | 14.82 | 121.8 | 70.48 | 14.82
2016-17 | 13.0349 | 7.0905 | 5.9443 | 3.815 | 2.1293 | 13.0349 | 0 | 0 | 0 | 2016-17 | 137.21 | 82.53 | 18.08 | 137.19 | 32.49 | 18.08 | 137.21 | 82.53 | 18.08
2017-18 | 8.5972 | 1.6236 | 6.9735 | 3.815 | 3.1585 | 8.5972 | 0 | 0 | 0 | 2017-18 | 0 | 110.19 | 18.03 | 0 | 57.39 | 17.94 | 0 | 110.19 | 18.03
2018-19 | 10.9034 | 2.1543 | 8.749 | 3.815 | 4.934 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 0 | 113.53 | 23.68 | 0 | 63.71 | 23.68 | 0 | 8.24 | 19.11
2019-20 | 9.8024 | 2.7711 | 7.0313 | 3.815 | 3.2163 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-20 | 0 | 134 | 25.07 | 0 | 73.36 | 29.06 | 0 | 14.07 | 24.11
2020-21 | 11.6944 | 3.715 | 7.9794 | 3.815 | 4.1644 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 0 | 128.15 | 37.77 | 0 | 78.16 | 38.16 | 0 | 21.73 | 24.96
2021-22 | 14.3651 | 4.6258 | 9.7393 | 3.815 | 5.9243 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 0 | 148.79 | 36.79 | 0 | 85.89 | 38.76 | 0 | 27.02 | 28.91
2022-23 | 16.0526 | 5.5946 | 10.4579 | 3.815 | 6.6429 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 0 | 143.82 | 47.71 | 0 | 99.33 | 47.68 | 0 | 41.09 | 37.65
2023-24 | 18.1375 | 6.3963 | 11.7413 | 3.815 | 7.9263 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 0 | 157.08 | 50.97 | 0 | 106.73 | 50.04 | 0 | 47.24 | 45.16
2024-25 | 19.3826 | 7.7673 | 11.6153 | 3.815 | 7.8003 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 0 | 166.73 | 55.28 | 0 | 113.67 | 56.13 | 0 | 55.59 | 50.29
2025-26 | 22.6015 | 9.3764 | 13.2251 | 3.815 | 9.4101 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 0 | 175.05 | 61.73 | 0 | 125.16 | 61.62 | 0 | 64.89 | 57.07
2026-27 | 29.3437 | 11.7167 | 17.627 | 3.815 | 13.812 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 0 | 185.32 | 66.3 | 0 | 129.6 | 66.3 | 0 | 72.16 | 60.03
2027-28 | 34.3051 | 14.0457 | 20.2594 | 3.815 | 16.4444 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 0 | 192.66 | 72.05 | 0 | 142.53 | 71.52 | 0 | 80.62 | 67.65
Residual | 353.568 | 144.7629 | 208.8051 | 39.3196 | 169.4855 | 68.1843 | 287.5463 | 53.1961 | 234.3502
NPV | 203.9768 | 90.9362 | 113.0406 | 34.0485 | 78.9921 | 73.8528 | 130.6418 | 34.2644 | 96.3773
Table 6
Option | Project cost | Weighted gross market benefit | Net market benefit | Ranking under RIT-T
Option 2 | 34.2644 | 130.6418 | 96.3773 | 1
Option 3a | 44.847 | 129.059 | 84.2121 | 4
Option 3b | 56.0587 | 140.9489 | 84.8901 | 3
Option 3c | 61.0168 | 143.4196 | 82.4028 | 5
Option 3d | 50.1601 | 142.7154 | 92.5553 | 2

## Option 3d
Weighted cost-Benefit, with a tailored safety margin (SM) for each relevant constraint equation and 15 minute ratings | [11 empty] | Base case (15 minute rating) | [9 empty] | Alternative case (15 minute rating) | [9 empty] | 5 minutes rating
0 | Do nothing | Embedded gen 30 (from 2015/16) | 0 | 0 | 0 | Network Option (from 2018/19) | 0 | 0 | 0 |  |  |  | Do nothing | Non-network option 3d (from 2016/17) | 0 | 0 | 0 | Network option 2 (from 2018/19) | 0 | 0 | 0 |  | Do nothing | Non-network option 3d (from 2015/16) | 0 | 0 | 0 | Network option 2 (from 2018/19) | 0 | 0 | 0 |  | Do nothing | Non-network option 3d (from 2017/18) | 0 | 0 | 0 | Network option 2 (from 2019/20) | 0 | 0 | 0
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) |  |  | Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M)
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 |  | Check | 2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 2014-15 | 1.0618 | 1.1 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0
2015-16 | 20.497 | 13.9023 | 6.5947 | 2.289 | 4.3057 | 20.497 | 0 | 0 | 0 |  |  | 2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0 | 2015-16 | 20.497 | 13.9023 | 6.5947 | 2.289 | 4.3057 | 20.497 | 0 | 0 | 0 | 2015-16 | 2.5543 | 0 | 2.6 | 2.289 | 0.311 | 20.497 | 0 | 0 | 0
2016-17 | 13.0349 | 8.8795 | 4.1553 | 2.289 | 1.8663 | 13.0349 | 0 | 0 | 0 |  |  | 2016-17 | 13.0349 | 8.8795 | 4.1553 | 2.289 | 1.8663 | 13.0349 | 0 | 0 | 0 | 2016-17 | 13.0349 | 8.8795 | 4.1553 | 2.289 | 1.8663 | 17.9848 | 0 | 0 | 0 | 2016-17 | 1.9337 | 0 | 1.9 | 2.289 | -0.389 | 17.9848 | 0 | 0 | 0
2017-18 | 8.5972 | 3.1246 | 5.4725 | 2.289 | 3.1835 | 0.16864 | 8.4285 | 5.13 | 3.2985 | 1 |  | 2017-18 | 8.5972 | 3.1246 | 5.4725 | 2.289 | 3.1835 | 8.5972 | 0 | 0 | 0 | 2017-18 | 8.5972 | 3.1246 | 5.4725 | 2.289 | 3.1835 | 8.5972 | 0 | 0 | 0 | 2017-18 | 8.5972 | 3.1246 | 5.4725 | 2.289 | 3.1835 | 0.16864 | 8.4285 | 5.13 | 3.2985
2018-19 | 10.9034 | 4.0255 | 6.8778 | 2.289 | 4.5888 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 1 |  | 2018-19 | 10.9034 | 2.1543 | 8.749 | 3.815 | 4.934 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 10.9034 | 2.1543 | 8.749 | 3.815 | 4.934 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 2018-19 | 10.9034 | 2.1543 | 8.749 | 3.815 | 4.934 | 0.29572 | 10.6076 | 5.13 | 5.4776
2019-20 | 9.8024 | 5.0902 | 4.7122 | 2.289 | 2.4232 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 1 |  | 2019-20 | 9.8024 | 2.7711 | 7.0313 | 3.815 | 3.2163 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-20 | 9.8024 | 2.7711 | 7.0313 | 3.815 | 3.2163 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 2019-20 | 9.8024 | 2.7711 | 7.0313 | 3.815 | 3.2163 | 0.51708 | 9.2853 | 5.13 | 4.1553
2020-21 | 11.6944 | 6.1708 | 5.5236 | 2.289 | 3.2346 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 1 |  | 2020-21 | 11.6944 | 3.715 | 7.9794 | 3.815 | 4.1644 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 11.6944 | 3.715 | 7.9794 | 3.815 | 4.1644 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 2020-21 | 11.6944 | 3.715 | 7.9794 | 3.815 | 4.1644 | 0.80584 | 10.8885 | 5.13 | 5.7585
2021-22 | 14.3651 | 7.086 | 7.2791 | 2.289 | 4.9901 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 1 |  | 2021-22 | 14.3651 | 2.0428 | 12.3223 | 6.104 | 6.2183 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 14.3651 | 2.0428 | 12.3223 | 6.104 | 6.2183 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 2021-22 | 14.3651 | 2.0428 | 12.3223 | 6.104 | 6.2183 | 1.0903 | 13.2748 | 5.13 | 8.1448
2022-23 | 16.0526 | 8.6707 | 7.3818 | 2.289 | 5.0928 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 1 |  | 2022-23 | 16.0526 | 2.5638 | 13.4888 | 6.104 | 7.3848 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 16.0526 | 2.5638 | 13.4888 | 6.104 | 7.3848 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 2022-23 | 16.0526 | 2.5638 | 13.4888 | 6.104 | 7.3848 | 1.5833 | 14.4693 | 5.13 | 9.3393
2023-24 | 18.1375 | 10.0078 | 8.1297 | 2.289 | 5.8407 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 1 |  | 2023-24 | 18.1375 | 2.9249 | 15.2127 | 6.104 | 9.1087 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 18.1375 | 2.9249 | 15.2127 | 6.104 | 9.1087 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 2023-24 | 18.1375 | 2.9249 | 15.2127 | 6.104 | 9.1087 | 2.2592 | 15.8784 | 5.13 | 10.7484
2024-25 | 19.3826 | 11.3926 | 7.99 | 2.289 | 5.701 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 1 |  | 2024-25 | 19.3826 | 2.0971 | 17.2855 | 7.63 | 9.6555 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 19.3826 | 2.0971 | 17.2855 | 7.63 | 9.6555 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 2024-25 | 19.3826 | 2.0971 | 17.2855 | 7.63 | 9.6555 | 3.1459 | 16.2367 | 5.13 | 11.1067
2025-26 | 22.6015 | 13.6323 | 8.9692 | 2.289 | 6.6802 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 1 |  | 2025-26 | 22.6015 | 2.9111 | 19.6904 | 7.63 | 12.0604 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 22.6015 | 2.9111 | 19.6904 | 7.63 | 12.0604 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 2025-26 | 22.6015 | 2.9111 | 19.6904 | 7.63 | 12.0604 | 4.0391 | 18.5624 | 5.13 | 13.4324
2026-27 | 29.3437 | 17.2994 | 12.0443 | 2.289 | 9.7553 | 5.0687 | 24.275 | 5.13 | 19.145 | 1 |  | 2026-27 | 29.3437 | 2.3105 | 27.0332 | 9.156 | 17.8772 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 29.3437 | 2.3105 | 27.0332 | 9.156 | 17.8772 | 5.0687 | 24.275 | 5.13 | 19.145 | 2026-27 | 29.3437 | 2.3105 | 27.0332 | 9.156 | 17.8772 | 5.0687 | 24.275 | 5.13 | 19.145
2027-28 | 34.3051 | 20.241 | 14.0641 | 2.289 | 11.7751 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 1 |  | 2027-28 | 34.3051 | 3.0372 | 31.2679 | 9.156 | 22.1119 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 34.3051 | 3.0372 | 31.2679 | 9.156 | 22.1119 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 2027-28 | 34.3051 | 3.0372 | 31.2679 | 9.156 | 22.1119 | 6.5754 | 27.7297 | 5.13 | 22.5997
[12 empty] | Residual |  |  | 320.0964 | 93.732 | 226.3644 |  | 287.5463 | 53.1961 | 234.3502 | Residual |  |  | 317.7113 | 93.0336 | 224.6777 |  | 287.5463 | 53.1961 | 234.3502 | Residual |  |  | 317.7113 | 93.0336 | 224.6777 |  | 285.7982 | 52.8727 | 232.9255
0 | Do nothing | Embedded gen 50 (from 2015/16) | 0 | 0 | 0 | Network Option (from 2018/19) | 0 | 0 | 0 |  |  | NPV |  |  | 142.7154 | 50.1601 | 92.5553 |  | 130.6418 | 34.2644 | 96.3773 | NPV |  |  | 147.5946 | 51.8847 | 95.71 |  | 130.6418 | 34.2644 | 96.3773 | NPV |  |  | 142.5987 | 51.8847 | 90.7141 |  | 135.9801 | 37.6909 | 98.2892
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Incremental Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) |  |  | Check |  |  |  |  | 92.5553 |  |  |  | 96.3773 | Check |  |  |  |  | 95.71 |  |  |  | 96.3773 | Check |  |  |  |  | 90.7141 |  |  |  | 98.2892
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 3.815 |  | Benefits Difference ($M) |  |  |  |  | 3.8221
2015-16 | 20.497 | 10.6987 | 9.7984 | 3.815 | 5.9834 | 20.497 | 0 | 0 | 0 |  |  | Error Margin (cost ±30%) |  |  |  |  | 28.1196 |  |  |  | 15.9588
2016-17 | 13.0349 | 7.0905 | 5.9443 | 3.815 | 2.1293 | 13.0349 | 0 | 0 | 0 |  |  | No clear outcome?
2017-18 | 8.5972 | 1.6236 | 6.9735 | 1.526 | 3.1585 | 8.5972 | 0 | 0 | 0 |  | 1.501
2018-19 | 10.9034 | 2.1543 | 8.749 | 1.526 | 4.934 | 0.29572 | 10.6076 | 5.13 | 5.4776 | 1 | 1.8712
2019-20 | 9.8024 | 2.7711 | 7.0313 | 1.526 | 3.2163 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 1 |  | Base case (15 minute rating)
2020-21 | 11.6944 | 3.715 | 7.9794 | 1.526 | 4.1644 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 1 |  |  | Do nothing | Non-network option 3d (from 2016/17) | 0 | 0 | 0 | Network option 2 (from 2018/19) | 0 | 0 | 0
2021-22 | 14.3651 | 4.6258 | 9.7393 | 1.526 | 5.9243 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 1 |  | Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M)
2022-23 | 16.0526 | 5.5946 | 10.4579 | 1.526 | 6.6429 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 1 |  | 2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0
2023-24 | 18.1375 | 6.3963 | 11.7413 | 1.526 | 7.9263 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 1 |  | 2015-16 | 20.497 | 20.497 | 0 | 0 | 0
2024-25 | 19.3826 | 7.7673 | 11.6153 | 1.526 | 7.8003 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 1 |  | 2016-17 | 13.0349 | 7.0905 | 5.9443 | 3.82 | 2.1243
2025-26 | 22.6015 | 9.3764 | 13.2251 | 1.526 | 9.4101 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 1 |  | 2017-18 | 8.5972 | 1.6236 | 6.9735 | 3.82 | 3.1535
2026-27 | 29.3437 | 11.7167 | 17.627 | 1.526 | 13.812 | 5.0687 | 24.275 | 5.13 | 19.145 | 1 |  | 2018-19 | 10.9034 | 2.1543 | 8.749 | 3.815 | 4.934
2027-28 | 34.3051 | 14.0457 | 20.2594 | 1.526 | 16.4444 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 1 |  | 2019-20 | 9.8024 | 2.7711 | 7.0313 | 3.815 | 3.2163
[12 empty] | 2020-21 | 11.6944 | 3.715 | 7.9794 | 3.815 | 4.1644
0 | Do nothing | Embedded gen 80 (from 2022/23) | 0 | 0 | 0 | Network Option (from 2018/19) | 0 | 0 | 0 |  |  | 2021-22 | 14.3651 | 2.0428 | 12.3223 | 6.104 | 6.2183
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Incremental Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) |  |  | 2022-23 | 16.0526 | 2.5638 | 13.4888 | 6.104 | 7.3848
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 6.104 |  | 2023-24 | 18.1375 | 2.9249 | 15.2127 | 6.104 | 9.1087
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0 |  |  | 2024-25 | 19.3826 | 2.0971 | 17.2855 | 7.63 | 9.6555
2016-17 | 13.0349 | 13.0349 | 0 | 0 | 0 | 13.0349 | 0 | 0 | 0 |  |  | 2025-26 | 22.6015 | 2.9111 | 19.6904 | 7.63 | 12.0604
2017-18 | 8.5972 | 0.50171 | 8.0955 | 2.289 | 1.9915 | 8.5972 | 0 | 0 | 0 |  |  | 2026-27 | 29.3437 | 2.3105 | 27.0332 | 9.156 | 17.8772
2018-19 | 10.9034 | 0.77013 | 10.1332 | 2.289 | 4.0292 | 0.29572 | 10.6076 | 5.13 | 5.4776 |  | 1.3842 | 2027-28 | 34.3051 | 3.0372 | 31.2679 | 9.156 | 22.1119
2019-21 | 9.8024 | 1.0436 | 8.7588 | 2.289 | 2.6548 | 0.51708 | 9.2853 | 5.13 | 4.1553 | 0 | 1.7274 | Residual |  |  | 320.0964 | 93.732 | 226.3644
2020-21 | 11.6944 | 1.4825 | 10.2119 | 2.289 | 4.1079 | 0.80584 | 10.8885 | 5.13 | 5.7585 | 0 | 2.2325 | NPV |  |  | 145.0847 | 52.3561 | 92.7286
2021-22 | 14.3651 | 2.0428 | 12.3223 | 2.289 | 6.2183 | 1.0903 | 13.2748 | 5.13 | 8.1448 | 0 | 2.583 | Check |  |  |  |  | 92.7286 |  |  |  | 0
2022-23 | 16.0526 | 2.5638 | 13.4888 | 2.289 | 7.3848 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 1
2023-24 | 18.1375 | 2.9249 | 15.2127 | 2.289 | 9.1087 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 1
2024-25 | 19.3826 | 4.1566 | 15.226 | 2.289 | 9.122 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 1
2025-26 | 22.6015 | 5.1981 | 17.4034 | 2.289 | 11.2994 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 1
2026-27 | 29.3437 | 6.5462 | 22.7975 | 2.289 | 16.6935 | 5.0687 | 24.275 | 5.13 | 19.145 | 1
2027-28 | 34.3051 | 7.8521 | 26.453 | 2.289 | 20.349 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 1
0 | Do nothing | Embedded gen 100 (from 2023/24) | 0 | 0 | 0 | Network Option (from 2018/19) | 0 | 0 | 0 |  | *no difference in benefits, USE suspected to be from RCTS-KGTS-WETS-BETS line
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M)
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 7.63
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0
2016-17 | 13.0349 | 13.0349 | 0 | 0 | 0 | 13.0349 | 0 | 0 | 0
2017-18 | 8.5972 | 0.16424 | 8.4329 | 1.526 | 0.80292 | 8.5972 | 0 | 0 | 0
2018-19 | 10.9034 | 0.33812 | 10.5652 | 1.526 | 2.9352 | 0.29572 | 10.6076 | 5.13 | 5.4776
2019-20 | 9.8024 | 0.53765 | 9.2647 | 1.526 | 1.6347 | 0.51708 | 9.2853 | 5.13 | 4.1553
2020-21 | 11.6944 | 0.79575 | 10.8986 | 1.526 | 3.2686 | 0.80584 | 10.8885 | 5.13 | 5.7585
2021-22 | 14.3651 | 1.0949 | 13.2702 | 1.526 | 5.6402 | 1.0903 | 13.2748 | 5.13 | 8.1448 |  | 0.94792
2022-23 | 16.0526 | 1.3388 | 14.7137 | 1.526 | 7.0837 | 1.5833 | 14.4693 | 5.13 | 9.3393 | 0 | 1.2249
2023-24 | 18.1375 | 1.7286 | 16.4089 | 1.526 | 8.7789 | 2.2592 | 15.8784 | 5.13 | 10.7484 | 1 | 1.1963
2024-25 | 19.3826 | 2.0971 | 17.2855 | 1.526 | 9.6555 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 1 | 2.0595
2025-26 | 22.6015 | 2.9111 | 19.6904 | 1.526 | 12.0604 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 1
2026-27 | 29.3437 | 4.2375 | 25.1062 | 1.526 | 17.4762 | 5.0687 | 24.275 | 5.13 | 19.145 | 1
2027-28 | 34.3051 | 5.2114 | 29.0937 | 1.526 | 21.4637 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 1
0 | Do nothing | Embedded gen 120 (from 2025/26) | 0 | 0 | 0 | Network Option (from 2018/19) | 0 | 0 | 0
Year | Limitation cost ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M) | Remaining Limitation cost ($M) | Gross Market Benefits ($M) | Option cost ($M) | Net Market Benefits ($M)
2014-15 | 18.0352 | 18.0352 | 0 | 0 | 0 | 18.0352 | 0 | 0 | 0 | 9.156
2015-16 | 20.497 | 20.497 | 0 | 0 | 0 | 20.497 | 0 | 0 | 0
2016-17 | 13.0349 | 13.0349 | 0 | 0 | 0 | 13.0349 | 0 | 0 | 0
2017-18 | 8.5972 | 0.10516 | 0 | 0 | 0 | 8.5972 | 0 | 0 | 0
2018-19 | 10.9034 | 0.15597 | 10.7474 | 1.526 | 1.5914 | 0.29572 | 10.6076 | 5.13 | 5.4776
2019-20 | 9.8024 | 0.31035 | 9.492 | 1.526 | 0.33604 | 0.51708 | 9.2853 | 5.13 | 4.1553
2020-21 | 11.6944 | 0.49199 | 11.2024 | 1.526 | 2.0464 | 0.80584 | 10.8885 | 5.13 | 5.7585
2021-22 | 14.3651 | 0.60407 | 13.761 | 1.526 | 4.605 | 1.0903 | 13.2748 | 5.13 | 8.1448
2022-23 | 16.0526 | 0.84319 | 15.2094 | 1.526 | 6.0534 | 1.5833 | 14.4693 | 5.13 | 9.3393
2023-24 | 18.1375 | 1.0869 | 17.0506 | 1.526 | 7.8946 | 2.2592 | 15.8784 | 5.13 | 10.7484
2024-25 | 19.3826 | 1.3616 | 18.0211 | 1.526 | 8.8651 | 3.1459 | 16.2367 | 5.13 | 11.1067 | 0 | 0.73553
2025-26 | 22.6015 | 1.6749 | 20.9266 | 1.526 | 11.7706 | 4.0391 | 18.5624 | 5.13 | 13.4324 | 1 | 1.2362
2026-27 | 29.3437 | 2.3105 | 27.0332 | 1.526 | 17.8772 | 5.0687 | 24.275 | 5.13 | 19.145 | 1 | 1.927
2027-28 | 34.3051 | 3.0372 | 31.2679 | 1.526 | 22.1119 | 6.5754 | 27.7297 | 5.13 | 22.5997 | 1 | 2.1741

## Base_SMFL
With up to stage 2 augmentation
15 minute rating
Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
S9, TSDF 2015-16 no growth | 1
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349
2017-18 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0
2025-26 | 0 | 0 | 0 | 0
2026-27 | 0 | 0 | 0 | 0
2027-28 | 0 | 0 | 0 | 0
[6 empty] | 10% POE 500kV new generation location S1 | [30 empty] | 10% POE 500kV new generation location S2
Scenario 1 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 40.55 | 90.89 | 27.267 | 1699.2794 |  | 2016-17 | 0 | 90.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 40.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 722.45 | 409.4 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.21 | 82.53 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 11 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
[6 empty] | 50% POE 500kV new generation location S1 | [30 empty] | 50% POE 500kV new generation location S2
Scenario 2 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 237.82 | 1149.93 | 620.317 | 38658.1554 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 324.42 | 68.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.44 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
[6 empty] | 10% POE 500kV new generation location S7 | [30 empty] | 10% POE 500kV new generation location S8
Scenario 7 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 320.18 | 212.78 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 96.3 | 52.26 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
[6 empty] | 50% POE 500kV new generation location S7 | [30 empty] | 50% POE 500kV new generation location S8
Scenario 8 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 152.1 | 536.5 | 188.607 | 11753.9882 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 39.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
10% POE S9
Scenario 9 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28
50% POE S9
[7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[6 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[6 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[6 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Base_SMFL_5min
With up to stage 2 augmentation
15 minute rating
Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
S9, TSDF 2015-16 no growth | 1
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2014-15 | 60.57 | 113.59 | 17.0385 | 1.0618
2015-16 | 93.31 | 270.13 | 40.9875 | 2.5543
2016-17 | 108.76 | 363.43 | 31.029 | 1.9337
2017-18 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0
2025-26 | 0 | 0 | 0 | 0
2026-27 | 0 | 0 | 0 | 0
2027-28 | 0 | 0 | 0 | 0
[6 empty] | 10% POE 500kV new generation location S1 | [30 empty] | 10% POE 500kV new generation location S2
Scenario 1 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 60.57 | 113.59 | 34.077 | 2123.6786 |  | 2014-15 | 78.2 | 19.35 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 28.52 | 16.01 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 78.2 | 19.35 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 28.52 | 16.01 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2015-16 | 93.31 | 270.13 | 81.039 | 5050.3505 |  | 2015-16 | 248.13 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 71.31 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2015-16 | 248.13 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 71.31 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1
2016-17 | 0.15 | 0.15 | 0.045 | 2.8044 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 351.94 | 0 | 0 | 0 | 0.27 | 3.6 | 0 | 0 | 0 | 7.62 | 97.27 | 0 | 0 | 0 | 0.27 | 3.6 | 0 | 0 | 0 | 7.62 | 5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
[6 empty] | 50% POE 500kV new generation location S1 | [30 empty] | 50% POE 500kV new generation location S2
Scenario 2 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 60.57 | 113.59 | 34.077 | 2123.6786 |  | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 93.31 | 270.13 | 81.039 | 5050.3505 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 108.76 | 363.43 | 109.029 | 6794.6873 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
[6 empty] | 10% POE 500kV new generation location S7 | [30 empty] | 10% POE 500kV new generation location S8
Scenario 7 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 3.12 | 3.12 | 0.936 | 58.3315 |  | 2015-16 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 0 | 0 | 0 | 0 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 50.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
[6 empty] | 50% POE 500kV new generation location S7 | [30 empty] | 50% POE 500kV new generation location S8
Scenario 8 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 3.12 | 3.12 | 0.936 | 58.3315 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 22.1 | 50.14 | 15.042 | 937.4174 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | [30 empty] | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | [30 empty] | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | [30 empty] | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | [30 empty] | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | [30 empty] | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | [30 empty] | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | [30 empty] | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | [30 empty] | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26 | [30 empty] | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27 | [30 empty] | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28 | [30 empty] | 2027-28
10% POE S9
Scenario 9 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15
2015-16 | 93.4 | 269.48 | 80.844 | 5038.1981 |  | 2015-16 | 246.99 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09 | 70.91 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09
2016-17 | 93.4 | 269.48 | 80.844 | 5038.1981 |  | 2016-17 | 246.99 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09 | 70.91 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28
50% POE S9
[7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[6 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
2015-16
2016-17
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Base_stage2_SMFL_5min
With up to stage 2 augmentation
15 minute rating
Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
S9, TSDF 2015-16 no growth | 1
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2014-15 | 60.57 | 113.59 | 17.0385 | 1.0618
2015-16 | 93.31 | 270.13 | 40.9875 | 2.5543
2016-17 | 108.76 | 363.43 | 31.029 | 1.9337
2017-18 | 31.09 | 39.23 | 3.1597 | 0.19692
2018-19 | 37.53 | 74.97 | 5.967 | 0.37186
2019-21 | 54.37 | 123.69 | 9.7508 | 0.60767
2020-21 | 80.14 | 199.83 | 17.4593 | 1.0881
2021-22 | 80.91 | 241.79 | 26.3633 | 1.643
2022-23 | 99.56 | 311.49 | 38.8428 | 2.4207
2023-24 | 107.98 | 369.75 | 54.9357 | 3.4236
2024-25 | 122.46 | 429.29 | 78.5673 | 4.8963
2025-26 | 140.43 | 508.47 | 106.5037 | 6.6373
2026-27 | 156.09 | 593.81 | 132.1725 | 8.237
2027-28 | 172.1 | 741.31 | 168.5122 | 10.5017
[6 empty] | 10% POE 500kV new generation location S1 | [30 empty] | 10% POE 500kV new generation location S2
Scenario 1 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 60.57 | 113.59 | 34.077 | 2123.6786 |  | 2014-15 | 78.2 | 19.35 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 28.52 | 16.01 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 78.2 | 19.35 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 28.52 | 16.01 | 0 | 0 | 16.04 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2015-16 | 93.31 | 270.13 | 81.039 | 5050.3505 |  | 2015-16 | 248.13 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 71.31 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2015-16 | 248.13 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 71.31 | 0 | 0 | 0 | 17.34 | 0.14 | 0 | 0 | 0 | 4.52 | 5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1
2016-17 | 0.15 | 0.15 | 0.045 | 2.8044 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 351.94 | 0 | 0 | 0 | 0.27 | 3.6 | 0 | 0 | 0 | 7.62 | 97.27 | 0 | 0 | 0 | 0.27 | 3.6 | 0 | 0 | 0 | 7.62 | 5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 28.12 | 0 | 0 | 0 | 4.44 | 0 | 0 | 0 | 6.67 | 0 | 21.58 | 0 | 0 | 0 | 4.44 | 0 | 0 | 0 | 5.07 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 64.92 | 0 | 0 | 0 | 10.05 | 0 | 0 | 0 | 0 | 0 | 27.48 | 0 | 0 | 0 | 10.05 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 96.58 | 0 | 0 | 0 | 15.57 | 0 | 0 | 0 | 11.54 | 0 | 33.1 | 0 | 0 | 0 | 15.57 | 0 | 0 | 0 | 5.7 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 157.78 | 0 | 0 | 0 | 23.24 | 0 | 0 | 0 | 18.81 | 0 | 47.1 | 0 | 0 | 0 | 23.24 | 0 | 0 | 0 | 9.8 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 200.98 | 0 | 0 | 0 | 25.23 | 0 | 0 | 0 | 15.58 | 0 | 45.88 | 0 | 0 | 0 | 25.23 | 0 | 0 | 0 | 9.8 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 268.74 | 0 | 0 | 0 | 30.08 | 0 | 0 | 0 | 12.67 | 0 | 64.02 | 0 | 0 | 0 | 30.08 | 0 | 0 | 0 | 5.46 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 306.88 | 0 | 0 | 0 | 36.4 | 0 | 0 | 0 | 26.47 | 0 | 61.78 | 0 | 0 | 0 | 36.4 | 0 | 0 | 0 | 9.8 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 366.99 | 0 | 0 | 0 | 40.96 | 0 | 0 | 0 | 21.34 | 0 | 71.7 | 0 | 0 | 0 | 40.96 | 0 | 0 | 0 | 9.8 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 426.07 | 0 | 0 | 0 | 50.18 | 0 | 0 | 0 | 32.22 | 0 | 82.64 | 0 | 0 | 0 | 47.99 | 0 | 0 | 0 | 9.8 | 0 | 7 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 493.84 | 0 | 0 | 0 | 59.36 | 0 | 0 | 0 | 40.61 | 0 | 93.27 | 0 | 0 | 0 | 52.98 | 0 | 0 | 0 | 9.84 | 0 | 9 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 613.61 | 0 | 0 | 0 | 69.47 | 0 | 0 | 0 | 58.23 | 0 | 104.15 | 0 | 0 | 0 | 58.11 | 0 | 0 | 0 | 9.84 | 0 | 11 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 7
[6 empty] | 50% POE 500kV new generation location S1 | [30 empty] | 50% POE 500kV new generation location S2
Scenario 2 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 60.57 | 113.59 | 34.077 | 2123.6786 |  | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 93.31 | 270.13 | 81.039 | 5050.3505 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 108.76 | 363.43 | 109.029 | 6794.6873 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 31.09 | 39.23 | 11.769 | 733.4441 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 37.53 | 74.97 | 22.491 | 1401.6391 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 54.37 | 123.69 | 37.107 | 2312.5082 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 80.14 | 199.83 | 59.949 | 3736.0217 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 80.91 | 241.79 | 72.537 | 4520.5058 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 99.56 | 311.49 | 98.305 | 6126.3676 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2023-24 | 107.98 | 369.75 | 127.235 | 7929.2852 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 6.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.82 | 0 | 3.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.41 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2024-25 | 122.46 | 429.29 | 173.356 | 10803.5459 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 29.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.11 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.12 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2025-26 | 140.43 | 508.47 | 226.923 | 14141.8414 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 66.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.1 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.93 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2026-27 | 156.09 | 593.81 | 280.434 | 17476.6469 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 112.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.41 | 0 | 30.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.93 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2027-28 | 172.1 | 741.31 | 363.996 | 22684.2307 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 161.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.23 | 0 | 39.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.93 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
[6 empty] | 10% POE 500kV new generation location S7 | [30 empty] | 10% POE 500kV new generation location S8
Scenario 7 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 3.12 | 3.12 | 0.936 | 58.3315 |  | 2015-16 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 0 | 0 | 0 | 0 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 50.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 13.79 | 0 | 0 | 0 | 1.26 | 0 | 0 | 0 | 9.93 | 0 | 8.91 | 0 | 0 | 0 | 1.26 | 0 | 0 | 0 | 8.72 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 13.83 | 0 | 0 | 0 | 6.77 | 0 | 0 | 0 | 24.05 | 0 | 10.09 | 0 | 0 | 0 | 6.77 | 0 | 0 | 0 | 9.79 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 24.31 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 41.02 | 0 | 7.88 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 9.93 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 60.19 | 0 | 0 | 0 | 11.9 | 0 | 0 | 0 | 41.67 | 0 | 16.62 | 0 | 0 | 0 | 11.9 | 0 | 0 | 0 | 9.93 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 96.37 | 0 | 0 | 0 | 17.91 | 0 | 0 | 0 | 47.09 | 0 | 24.77 | 0 | 0 | 0 | 17.91 | 0 | 0 | 0 | 9.93 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 134.88 | 0 | 0 | 0 | 21.91 | 0 | 0 | 0 | 44.66 | 0 | 30.8 | 0 | 0 | 0 | 21.91 | 0 | 0 | 0 | 9.79 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 190.95 | 0 | 0 | 0 | 26.11 | 0 | 0 | 0 | 34.98 | 0 | 41.9 | 0 | 0 | 0 | 26.11 | 0 | 0 | 0 | 9.83 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
[6 empty] | 50% POE 500kV new generation location S7 | [30 empty] | 50% POE 500kV new generation location S8
Scenario 8 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 3.12 | 3.12 | 0.936 | 58.3315 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 22.1 | 50.14 | 15.042 | 937.4174 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 3.87 | 6.23 | 1.869 | 116.4761 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 18.89 | 24.98 | 7.494 | 467.0261 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 26.65 | 44.65 | 13.395 | 834.7764 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 26.36 | 73.88 | 22.164 | 1381.2605 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 38.45 | 113.76 | 34.128 | 2126.857 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 52.61 | 161.37 | 48.411 | 3016.9735 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 62.5 | 201.45 | 60.435 | 3766.3092 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 77.84 | 252.04 | 75.612 | 4712.1398 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15
2015-16 | 93.4 | 269.48 | 80.844 | 5038.1981 |  | 2015-16 | 246.99 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09 | 70.91 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09
2016-17 | 93.4 | 269.48 | 80.844 | 5038.1981 |  | 2016-17 | 246.99 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09 | 70.91 |  |  |  | 16.97 | 0.43 |  |  |  | 5.09
2017-18 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2017-18 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2018-19 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2018-19 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2019-21 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2019-21 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2020-21 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2020-21 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2021-22 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2021-22 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2022-23 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2022-23 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2023-24 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2023-24 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2024-25 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2024-25 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2025-26 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2025-26 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2026-27 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2026-27 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
2027-28 | 3.96 | 3.96 | 1.188 | 74.0362 |  | 2027-28 |  | 1.06 | [7 empty] | 2.9 |  | 1.06 | [7 empty] | 2.9
50% POE S9
[7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[6 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
2015-16
2016-17
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 3_Gen_30_SMFL_5min
With up to stage 2 augmentation
15 minute rating
Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
S9, TSDF 2015-16 no growth | 1
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2014-15 | 0 | 0 | 0 | 0
2015-16 | 0 | 0 | 0 | 0
2016-17 | 1.79 | 1.79 | 0.22875 | 0.014256
2017-18 | 4.65 | 4.65 | 0.56625 | 0.035289
2018-19 | 10.06 | 10.06 | 1.0987 | 0.068474
2019-21 | 38.53 | 38.53 | 3.3638 | 0.20963
2020-21 | 33.32 | 40.23 | 3.6202 | 0.22561
2021-22 | 54.07 | 81.58 | 7.2795 | 0.45366
2022-23 | 62.2 | 119.76 | 11.8755 | 0.74008
2023-24 | 74.9 | 167.6 | 15.72 | 0.97967
2024-25 | 93.28 | 225.18 | 21.5978 | 1.346
2025-26 | 112.54 | 282.37 | 30.5167 | 1.9018
2026-27 | 128.86 | 358.14 | 48.0185 | 2.9925
2027-28 | 142.89 | 449.04 | 68.8137 | 4.2885
[6 empty] | 10% POE 500kV new generation location S1 | [30 empty] | 10% POE 500kV new generation location S2
Scenario 1 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | [30 empty] | 2014-15
2015-16 | 0 | 0 | 0 | 0 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.26 | 1.26 | 0.378 | 23.557 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 10.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 29.63 | 0 | 0 | 0 | 7.68 | 1.22 | 0 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 7.68 | 1.22 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 14.61 | 0 | 0 | 0 | 24.21 | 0 | 0 | 0 | 1.41 | 0 | 7.7 | 0 | 0 | 0 | 24.21 | 0 | 0 | 0 | 1.41 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 52.2 | 0 | 0 | 0 | 25.23 | 0 | 0 | 0 | 4.15 | 0 | 24.69 | 0 | 0 | 0 | 25.23 | 0 | 0 | 0 | 4.15 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 82.15 | 0 | 0 | 0 | 33.93 | 0 | 0 | 0 | 3.68 | 0 | 24.59 | 0 | 0 | 0 | 33.93 | 0 | 0 | 0 | 3.68 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 123.51 | 0 | 0 | 0 | 36.39 | 0 | 0 | 0 | 7.7 | 0 | 31.16 | 0 | 0 | 0 | 36.39 | 0 | 0 | 0 | 7.35 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 172.9 | 0 | 0 | 0 | 41.64 | 0 | 0 | 0 | 10.64 | 0 | 41.84 | 0 | 0 | 0 | 41.64 | 0 | 0 | 0 | 9.8 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 221.32 | 0 | 0 | 0 | 49.56 | 0 | 0 | 0 | 11.49 | 0 | 53.99 | 0 | 0 | 0 | 48.75 | 0 | 0 | 0 | 9.8 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 280.24 | 0 | 0 | 0 | 59.7 | 0 | 0 | 0 | 18.2 | 0 | 65.69 | 0 | 0 | 0 | 53.37 | 0 | 0 | 0 | 9.8 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 359.65 | 0 | 0 | 0 | 69.87 | 0 | 0 | 0 | 19.52 | 0 | 74.6 | 0 | 0 | 0 | 58.49 | 0 | 0 | 0 | 9.8 | 0 | 7 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
[6 empty] | 50% POE 500kV new generation location S1 | [30 empty] | 50% POE 500kV new generation location S2
Scenario 2 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | [30 empty] | 2014-15
2015-16 | 0 | 0 | 0 | 0 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.79 | 1.79 | 0.537 | 33.4658 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 4.65 | 4.65 | 1.395 | 86.9364 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 10.06 | 10.06 | 3.018 | 188.0818 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 38.53 | 38.53 | 11.559 | 720.3569 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 33.32 | 40.23 | 12.069 | 752.1401 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 54.07 | 81.58 | 24.474 | 1525.2197 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 62.2 | 119.76 | 35.928 | 2239.033 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 74.9 | 167.6 | 50.28 | 3133.4496 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 93.28 | 225.18 | 67.554 | 4209.9653 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 112.54 | 282.37 | 84.711 | 5279.1895 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 128.86 | 358.14 | 115.898 | 7222.7634 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 3.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.31 | 0 | 3.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2027-28 | 142.89 | 449.04 | 161.354 | 10055.5813 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 14.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.51 | 0 | 9.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.93 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
[6 empty] | 10% POE 500kV new generation location S7 | [30 empty] | 10% POE 500kV new generation location S8
Scenario 7 :Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | [30 empty] | 2014-15
2015-16 | 0 | 0 | 0 | 0 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 0 | 0 | 0 | 0 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 6.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 7.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 12.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 19.46 | 0 | 0 | 0 | 7.13 | 0 | 0 | 0 | 0 | 0 | 19.46 | 0 | 0 | 0 | 4.91 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 17.65 | 0 | 0 | 0 | 21.76 | 0 | 0 | 0 | 18.64 | 0 | 16.44 | 0 | 0 | 0 | 21.76 | 0 | 0 | 0 | 9.79 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 40.19 | 0 | 0 | 0 | 26.11 | 0 | 0 | 0 | 22.28 | 0 | 15.75 | 0 | 0 | 0 | 26.11 | 0 | 0 | 0 | 9.38 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
[6 empty] | 50% POE 500kV new generation location S7 | [30 empty] | 50% POE 500kV new generation location S8
Scenario 8 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15 | [30 empty] | 2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 0 | 0 | 0 | 0 |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 0 | 0 | 0 | 0 |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 1.42 | 1.42 | 0.426 | 26.5483 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 6.74 | 6.74 | 2.022 | 126.011 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 7.29 | 7.29 | 2.187 | 136.2938 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 12.03 | 12.03 | 3.609 | 224.9129 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 24.37 | 26.59 | 7.977 | 497.1266 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 47.99 | 58.05 | 17.415 | 1085.3028 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 51.24 | 88.58 | 26.574 | 1656.0917 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [6 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  | 2014-15
2015-16 | 64.05 | 145.58 | 43.674 | 2721.7637 |  | 2015-16 | 126.93 |  |  |  | 12.47 | 6.18 |  |  |  |  | 45.4 |  |  |  | 12.47 | 6.18 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 64.05 | 145.58 | 43.674 | 2721.7637 |  | 2016-17 | 126.93 |  |  |  | 12.47 | 6.18 |  |  |  |  | 45.4 |  |  |  | 12.47 | 6.18
2017-18 | 0 | 0 | 0 | 0 |  | 2017-18
2018-19 | 0 | 0 | 0 | 0 |  | 2018-19
2019-21 | 0 | 0 | 0 | 0 |  | 2019-21
2020-21 | 0 | 0 | 0 | 0 |  | 2020-21
2021-22 | 0 | 0 | 0 | 0 |  | 2021-22
2022-23 | 0 | 0 | 0 | 0 |  | 2022-23
2023-24 | 0 | 0 | 0 | 0 |  | 2023-24
2024-25 | 0 | 0 | 0 | 0 |  | 2024-25
2025-26 | 0 | 0 | 0 | 0 |  | 2025-26
2026-27 | 0 | 0 | 0 | 0 |  | 2026-27
2027-28 | 0 | 0 | 0 | 0 |  | 2027-28
50% POE S9
[7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[6 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
2015-16
2016-17
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 2_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Table 3
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497 | 0 | 0
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349 | 0 | 0
2017-18 | 128.22 | 609.91 | 137.952 | 8.5972 | 0 | 0
2018-19 | 137.21 | 712.39 | 174.9575 | 10.9034 | 0 | 0
2019-21 | 159.07 | 879.61 | 157.2912 | 9.8024 | 0 | 0
2020-21 | 165.92 | 967.25 | 187.6502 | 11.6944 | 0 | 0
2021-22 | 185.58 | 1227.72 | 230.505 | 14.3651 | 0 | 0
2022-23 | 191.53 | 1410.23 | 257.5827 | 16.0526 | 0 | 0
2023-24 | 208.05 | 1617.19 | 291.0387 | 18.1375 | 0 | 0
2024-25 | 222.01 | 1625.84 | 311.018 | 19.3826 | 0 | 0
2025-26 | 236.78 | 1928.71 | 362.6683 | 22.6015 | 0 | 0
2026-27 | 251.62 | 2624.06 | 470.8553 | 29.3437 | 0 | 0
2027-28 | 264.71 | 3071.35 | 550.4673 | 34.3051 | 0 | 0
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 40.55 | 90.89 | 27.267 | 1699.2794 |  |  | 2016-17 | 0 | 90.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 40.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 722.45 | 409.4 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.21 | 82.53 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 11 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 47.82 | 127.15 | 127.15 | 7923.988 |  |  | 2017-18 | 0 | 124.25 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 44.92 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 591.88 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 0 | 0 | 110.19 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 54.12 | 178.5 | 178.5 | 11124.12 |  |  | 2018-19 | 0 | 173.91 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 49.53 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 688.71 | 0 | 0 | 0 | 23.68 | 0 | 0 | 0 | 0 | 0 | 113.53 | 0 | 0 | 0 | 23.68 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 6.32 | 393.8624 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 854.54 | 0 | 0 | 0 | 25.07 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 25.07 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 8.04 | 501.0528 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 929.48 | 0 | 0 | 0 | 37.77 | 0 | 0 | 0 | 0 | 0 | 128.15 | 0 | 0 | 0 | 37.77 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 9.8 | 9.8 | 9.8 | 610.736 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 1190.93 | 0 | 0 | 0 | 36.79 | 0 | 0 | 0 | 0 | 0 | 148.79 | 0 | 0 | 0 | 36.79 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 11.62 | 11.62 | 11.62 | 724.1584 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 1362.52 | 0 | 0 | 0 | 47.71 | 0 | 0 | 0 | 0 | 0 | 143.82 | 0 | 0 | 0 | 47.71 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 12.84 | 12.84 | 12.84 | 800.1888 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 1562.51 | 0 | 0 | 0 | 54.68 | 0 | 0 | 0 | 0 | 0 | 157.08 | 0 | 0 | 0 | 50.97 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2024-25 | 14.67 | 14.67 | 14.67 | 914.2344 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 1560.67 | 0 | 0 | 0 | 65.17 | 0 | 0 | 0 | 0 | 0 | 166.73 | 0 | 0 | 0 | 55.28 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2025-26 | 16.53 | 16.53 | 16.53 | 1030.1496 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 1848.45 | 0 | 0 | 0 | 80.26 | 0 | 0 | 0 | 0 | 0 | 175.05 | 0 | 0 | 0 | 61.73 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2026-27 | 18.42 | 18.42 | 18.42 | 1147.9344 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 2527.48 | 0 | 0 | 0 | 96.58 | 0 | 0 | 0 | 0 | 0 | 185.32 | 0 | 0 | 0 | 66.3 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2027-28 | 29.9 | 29.9 | 29.9 | 1863.368 |  |  | 2027-28 | 0 | 9.56 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 9.56 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 2960.27 | 0 | 0 | 0 | 111.08 | 0 | 0 | 0 | 0 | 0 | 192.66 | 0 | 0 | 0 | 72.05 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 237.82 | 1149.93 | 620.317 | 38658.1554 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 324.42 | 68.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.44 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 128.22 | 609.91 | 308.567 | 19229.8954 |  |  | 2017-18 | 0 | 124.25 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 44.92 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 179.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 137.21 | 712.39 | 375.228 | 23384.209 |  |  | 2018-19 | 0 | 173.91 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 49.53 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 230.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 159.07 | 879.61 | 465.245 | 28994.0684 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 287.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 165.92 | 967.25 | 546.935 | 34084.9892 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 366.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 185.58 | 1227.72 | 680.558 | 42412.3746 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 446.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 191.53 | 1410.23 | 777.374 | 48445.9477 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 506.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 208.05 | 1617.19 | 884.178 | 55101.973 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 570.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 222.01 | 1625.84 | 922.648 | 57499.4234 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 621.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 236.78 | 1928.71 | 1067.206 | 66508.2779 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 697.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 251.62 | 2624.06 | 1410.386 | 87895.2555 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 890.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 264.71 | 3071.35 | 1649.993 | 102827.5638 |  |  | 2027-28 | 0 | 9.56 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 9.56 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 1040.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 320.18 | 212.78 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 96.3 | 52.26 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 5.43 | 6.07 | 6.07 | 378.2824 |  |  | 2017-18 | 0 | 6.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 349.21 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 77.03 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 12.73 | 21.97 | 21.97 | 1369.1704 |  |  | 2018-19 | 0 | 21.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 371.65 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 83.32 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 443.03 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 87.56 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 459.65 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 87.28 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 516.22 | 0 | 0 | 0 | 14.86 | 0 | 0 | 0 | 0 | 0 | 92.45 | 0 | 0 | 0 | 14.86 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 558.77 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 105.56 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 600.39 | 0 | 0 | 0 | 20.59 | 0 | 0 | 0 | 0 | 0 | 105.15 | 0 | 0 | 0 | 20.59 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 658.33 | 0 | 0 | 0 | 25.29 | 0 | 0 | 0 | 0 | 0 | 110.15 | 0 | 0 | 0 | 25.29 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 1.63 | 101.5816 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 729.13 | 0 | 0 | 0 | 30.76 | 0 | 0 | 0 | 0 | 0 | 125.81 | 0 | 0 | 0 | 30.76 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2026-27 | 3.3 | 3.3 | 3.3 | 205.656 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 813.04 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 130.93 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2027-28 | 5.01 | 5.01 | 5.01 | 312.2232 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 924.87 | 0 | 0 | 0 | 39.76 | 0 | 0 | 0 | 0 | 0 | 138.84 | 0 | 0 | 0 | 39.76 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 152.1 | 536.5 | 188.607 | 11753.9882 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 39.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 78.69 | 350.87 | 110.021 | 6856.5087 |  |  | 2017-18 | 0 | 6.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 87.62 | 375.95 | 124.132 | 7735.9062 |  |  | 2018-19 | 0 | 21.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 16.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 95.64 | 451.11 | 157.6 | 9821.632 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 31.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 99.91 | 472.28 | 195.626 | 12191.4123 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 77.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 107.31 | 531.08 | 231.662 | 14437.1758 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 103.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 125.52 | 578.73 | 241.337 | 15040.1218 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 96.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 125.74 | 620.98 | 267.137 | 16647.9778 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 115.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 135.44 | 683.62 | 306.754 | 19116.9093 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 145.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 156.57 | 759.89 | 365.307 | 22765.9322 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 196.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 165.86 | 847.97 | 451.315 | 28125.9508 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 281.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 178.6 | 964.63 | 516.966 | 32217.3211 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 325.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2017-18 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2018-19 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2018-19 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2019-21 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2019-21 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2020-21 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2020-21 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2021-22 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2021-22 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2022-23 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2022-23 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2023-24 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2023-24 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2024-25 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2024-25 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2025-26 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2025-26 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2026-27 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2026-27 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2027-28 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2027-28 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2017-18 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2018-19 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2019-21 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2020-21 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2021-22 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2022-23 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2023-24 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2024-25 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2025-26 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2026-27 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2027-28 |  | 164.98 | [9 empty] | 47.04

## Stage 3_Gen30_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 177.12 | 740.33 | 223.0788 | 13.9023 | 0 | 0
2016-17 | 207.79 | 886.4 | 142.4828 | 8.8795 | 0 | 0
2017-18 | 95.33 | 387.91 | 50.1388 | 3.1246 |  | 0
2018-19 | 107.23 | 452.84 | 64.5945 | 4.0255 |  | 0
2019-21 | 122.42 | 524.4 | 81.6787 | 5.0902 |  | 0
2020-21 | 149.39 | 636.87 | 99.0173 | 6.1708 |  | 0
2021-22 | 144.16 | 684.25 | 113.7032 | 7.086 |  | 0
2022-23 | 163.58 | 824.8 | 139.1322 | 8.6707 |  | 0
2023-24 | 173.69 | 928.74 | 160.588 | 10.0078 |  | 0
2024-25 | 192.8 | 1047.63 | 182.808 | 11.3926 |  | 0
2025-26 | 206.8 | 1201.44 | 218.7467 | 13.6323 |  | 0
2026-27 | 217.58 | 1562.39 | 277.5903 | 17.2994 |  | 0
2027-28 | 235.08 | 1828.02 | 324.7915 | 20.241 |  | 0
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 177.12 | 740.32 | 359.303 | 22391.763 |  |  | 2015-16 | 581.3 | 144.2 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.84 | 40.46 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 581.3 | 144.21 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.84 | 40.46 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 5.34 | 5.34 | 1.602 | 99.8366 |  |  | 2016-17 | 0 | 5.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 5.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 649.98 | 218.3 | 0 | 0 | 0 | 18.12 | 0 | 0 | 0 | 0 | 137.19 | 52.48 | 0 | 0 | 0 | 18.12 | 0 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 12.09 | 16.13 | 4.839 | 301.5665 |  |  | 2017-18 | 0 | 13.23 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 9.19 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 369.97 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 77.39 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 24.49 | 42.48 | 12.744 | 794.2061 |  |  | 2018-19 | 0 | 37.89 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 19.9 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 429.03 | 0 | 0 | 0 | 23.81 | 0 | 0 | 0 | 0 | 0 | 83.42 | 0 | 0 | 0 | 23.81 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2019-21 | 0 | 495.33 | 0 | 0 | 0 | 29.07 | 0 | 0 | 0 | 0 | 0 | 93.35 | 0 | 0 | 0 | 29.07 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 601.69 | 0 | 0 | 0 | 35.18 | 0 | 0 | 0 | 0 | 0 | 114.21 | 0 | 0 | 0 | 35.18 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 645.49 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 105.4 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 777.23 | 0 | 0 | 0 | 47.57 | 0 | 0 | 0 | 0 | 0 | 116.01 | 0 | 0 | 0 | 47.57 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 874.19 | 0 | 0 | 0 | 54.55 | 0 | 0 | 0 | 0 | 0 | 123.74 | 0 | 0 | 0 | 49.95 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 982.59 | 0 | 0 | 0 | 65.04 | 0 | 0 | 0 | 0 | 0 | 136.72 | 0 | 0 | 0 | 56.08 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 1120.95 | 0 | 0 | 0 | 80.49 | 0 | 0 | 0 | 0 | 0 | 144.97 | 0 | 0 | 0 | 61.83 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 1466.07 | 0 | 0 | 0 | 96.32 | 0 | 0 | 0 | 0 | 0 | 151.28 | 0 | 0 | 0 | 66.3 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 1716.69 | 0 | 0 | 0 | 111.33 | 0 | 0 | 0 | 0 | 0 | 162.77 | 0 | 0 | 0 | 72.31 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 177.12 | 740.33 | 359.306 | 22391.9499 |  |  | 2015-16 | 196.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 196.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 207.79 | 886.4 | 454.71 | 28337.5272 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 268.72 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.87 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 95.33 | 387.91 | 143.519 | 8944.1041 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 38.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 107.23 | 452.84 | 185.307 | 11548.3322 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 70.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 122.42 | 524.4 | 251.568 | 15677.7178 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 134.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 149.39 | 636.87 | 308.108 | 19201.2906 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 167.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 144.16 | 684.25 | 350.371 | 21835.1207 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 207.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 163.58 | 824.8 | 439.338 | 27379.5442 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 274.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 173.69 | 928.74 | 492.024 | 30662.9357 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 304.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 192.8 | 1047.63 | 578.105 | 36027.5036 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 376.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 206.8 | 1201.44 | 678.68 | 42295.3376 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 454.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 217.58 | 1562.39 | 851.743 | 53080.6238 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 547.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 235.08 | 1828.02 | 994.572 | 61981.727 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 637.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 86.02 | 289.51 | 86.853 | 5412.679 |  |  | 2015-16 | 266.78 | 22.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.63 | 16.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 266.78 | 22.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.63 | 16.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 0 | 0 | 0 | 0 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 317.63 | 57.55 | 0 | 0 | 0 | 3.55 | 0 | 0 | 0 | 0 | 96.29 | 22.22 | 0 | 0 | 0 | 3.55 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 172.33 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 196.79 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 53.32 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 236.1 | 0 | 0 | 0 | 8.07 | 0 | 0 | 0 | 0 | 0 | 57.56 | 0 | 0 | 0 | 8.07 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 253.98 | 0 | 0 | 0 | 13.03 | 0 | 0 | 0 | 0 | 0 | 56.12 | 0 | 0 | 0 | 13.03 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 323.57 | 0 | 0 | 0 | 14.77 | 0 | 0 | 0 | 0 | 0 | 70.59 | 0 | 0 | 0 | 14.77 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 340.32 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 67.47 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 378.62 | 0 | 0 | 0 | 20.57 | 0 | 0 | 0 | 0 | 0 | 74.45 | 0 | 0 | 0 | 20.57 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 422.3 | 0 | 0 | 0 | 25.97 | 0 | 0 | 0 | 0 | 0 | 83.5 | 0 | 0 | 0 | 25.97 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 469.82 | 0 | 0 | 0 | 30.67 | 0 | 0 | 0 | 0 | 0 | 88.56 | 0 | 0 | 0 | 30.67 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 552.85 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 99.69 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 630.88 | 0 | 0 | 0 | 40.21 | 0 | 0 | 0 | 0 | 0 | 108.56 | 0 | 0 | 0 | 40.21 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 86.02 | 289.51 | 86.853 | 5412.679 |  |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 122.06 | 378.73 | 113.619 | 7080.7361 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 51.75 | 173.99 | 52.197 | 3252.917 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 57.62 | 201.09 | 60.327 | 3759.5786 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 65.63 | 244.17 | 73.251 | 4565.0023 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 69.15 | 267.01 | 85.549 | 5331.4137 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 7.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 85.36 | 338.34 | 101.502 | 6325.6046 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 87.43 | 360.28 | 113.705 | 7086.0956 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 8.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 95.02 | 399.19 | 146.476 | 9128.3843 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 38.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 109.47 | 448.27 | 148.726 | 9268.6043 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 20.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 119.23 | 500.49 | 190.859 | 11894.3329 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 58.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 134.62 | 587.78 | 252.102 | 15710.9966 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 108.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 148.77 | 671.09 | 296.989 | 18508.3545 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 136.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2017-18 | [5 empty] | 10.94 | [9 empty] | 10.94
2018-19 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2018-19 | [5 empty] | 10.94 | [9 empty] | 10.94
2019-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2019-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2020-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2020-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2021-22 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2021-22 | [5 empty] | 10.94 | [9 empty] | 10.94
2022-23 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2022-23 | [5 empty] | 10.94 | [9 empty] | 10.94
2023-24 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2023-24 | [5 empty] | 10.94 | [9 empty] | 10.94
2024-25 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2024-25 | [5 empty] | 10.94 | [9 empty] | 10.94
2025-26 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2025-26 | [5 empty] | 10.94 | [9 empty] | 10.94
2026-27 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2026-27 | [5 empty] | 10.94 | [9 empty] | 10.94
2027-28 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2027-28 | [5 empty] | 10.94 | [9 empty] | 10.94
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 3_Gen50_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 157.19 | 603.97 | 171.673 | 10.6987 | 0 | 0
2016-17 | 187.76 | 750.32 | 113.7763 | 7.0905 | 0 | 0
2017-18 | 75.33 | 267.91 | 26.0532 | 1.6236 |  | 0
2018-19 | 87.39 | 325.82 | 34.5688 | 2.1543 |  | 0
2019-21 | 102.42 | 383.44 | 44.465 | 2.7711 |  | 0
2020-21 | 116.32 | 453.31 | 59.611 | 3.715 |  | 0
2021-22 | 124.65 | 532.6 | 74.2267 | 4.6258 |  | 0
2022-23 | 147.01 | 609.48 | 89.7725 | 5.5946 |  | 0
2023-24 | 156.77 | 679.18 | 102.636 | 6.3963 |  | 0
2024-25 | 169.8 | 768.08 | 124.636 | 7.7673 |  | 0
2025-26 | 186.78 | 881.74 | 150.4553 | 9.3764 |  | 0
2026-27 | 195.9 | 1104.42 | 188.009 | 11.7167 |  | 0
2027-28 | 214.05 | 1304.16 | 225.3802 | 14.0457 |  | 0
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 157.19 | 603.97 | 278.96 | 17384.7872 |  |  | 2015-16 | 536.42 | 52.73 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.88 | 20.49 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 536.42 | 52.73 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.88 | 20.49 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 0.15 | 0.15 | 0.045 | 2.8044 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 623.64 | 108.6 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.19 | 32.49 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 7 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 249.97 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 57.39 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 302.14 | 0 | 0 | 0 | 23.68 | 0 | 0 | 0 | 0 | 0 | 63.71 | 0 | 0 | 0 | 23.68 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 354.38 | 0 | 0 | 0 | 29.06 | 0 | 0 | 0 | 0 | 0 | 73.36 | 0 | 0 | 0 | 29.06 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 415.15 | 0 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0 | 78.16 | 0 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 493.84 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 85.89 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 561.8 | 0 | 0 | 0 | 47.68 | 0 | 0 | 0 | 0 | 0 | 99.33 | 0 | 0 | 0 | 47.68 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 624.64 | 0 | 0 | 0 | 54.54 | 0 | 0 | 0 | 0 | 0 | 106.73 | 0 | 0 | 0 | 50.04 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 702.9 | 0 | 0 | 0 | 65.18 | 0 | 0 | 0 | 0 | 0 | 113.67 | 0 | 0 | 0 | 56.13 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 801.6 | 0 | 0 | 0 | 80.14 | 0 | 0 | 0 | 0 | 0 | 125.16 | 0 | 0 | 0 | 61.62 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 1007.99 | 0 | 0 | 0 | 96.43 | 0 | 0 | 0 | 0 | 0 | 129.6 | 0 | 0 | 0 | 66.3 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 1193.45 | 0 | 0 | 0 | 110.71 | 0 | 0 | 0 | 0 | 0 | 142.53 | 0 | 0 | 0 | 71.52 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 157.19 | 603.97 | 278.96 | 17384.7872 |  |  | 2015-16 | 139.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 139.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 187.76 | 750.32 | 366.671 | 22850.9367 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 202.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 75.33 | 267.91 | 80.891 | 5041.1271 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 87.39 | 325.82 | 106.58 | 6642.0656 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 12.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 102.42 | 383.44 | 136.382 | 8499.3262 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 116.32 | 453.31 | 189.004 | 11778.7293 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 75.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 124.65 | 532.6 | 226.014 | 14085.1925 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 94.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 147.01 | 609.48 | 283.826 | 17688.0363 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 144.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 156.77 | 679.18 | 329.88 | 20558.1216 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 180.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 169.8 | 768.08 | 398.998 | 24865.5554 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 240.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 186.78 | 881.74 | 476.657 | 29705.2642 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 303.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 195.9 | 1104.42 | 592.055 | 36896.8676 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 372.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 214.05 | 1304.16 | 701.18 | 43697.5376 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 442.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 58.3 | 214.62 | 64.386 | 4012.5355 |  |  | 2015-16 | 214.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 214.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 287.36 | 2.22 | 0 | 0 | 0 | 3.55 | 0 | 0 | 0 | 0 | 93.32 | 2.22 | 0 | 0 | 0 | 3.55 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 73.18 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 30.09 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 96.25 | 0 | 0 | 0 | 4.81 | 0 | 0 | 0 | 0 | 0 | 28.47 | 0 | 0 | 0 | 4.81 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 123.86 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 37.55 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 144.13 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 37.27 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 211.34 | 0 | 0 | 0 | 15.17 | 0 | 0 | 0 | 0 | 0 | 54.14 | 0 | 0 | 0 | 15.17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 218.38 | 0 | 0 | 0 | 20.88 | 0 | 0 | 0 | 0 | 0 | 49.31 | 0 | 0 | 0 | 20.88 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 235.34 | 0 | 0 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 51.42 | 0 | 0 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 292.11 | 0 | 0 | 0 | 25.04 | 0 | 0 | 0 | 0 | 0 | 63.52 | 0 | 0 | 0 | 25.04 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 348.64 | 0 | 0 | 0 | 31.56 | 0 | 0 | 0 | 0 | 0 | 79.87 | 0 | 0 | 0 | 31.56 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 403.88 | 0 | 0 | 0 | 34.94 | 0 | 0 | 0 | 0 | 0 | 78.94 | 0 | 0 | 0 | 34.94 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 474.23 | 0 | 0 | 0 | 39.4 | 0 | 0 | 0 | 0 | 0 | 89.75 | 0 | 0 | 0 | 39.4 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 58.3 | 214.62 | 64.386 | 4012.5355 |  |  | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 99.09 | 293.13 | 87.939 | 5480.3585 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 31.75 | 74.84 | 22.452 | 1399.2086 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 33.28 | 101.06 | 30.318 | 1889.4178 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 45.63 | 131.94 | 39.582 | 2466.7502 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 49.9 | 156.76 | 47.028 | 2930.785 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 69.31 | 226.51 | 67.953 | 4234.831 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 70.19 | 239.26 | 71.778 | 4473.205 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 72.12 | 256.04 | 76.812 | 4786.9238 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 88.56 | 317.15 | 95.145 | 5929.4364 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 111.43 | 380.2 | 119.716 | 7460.7011 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 113.88 | 438.82 | 153.465 | 9563.9388 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 31.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 129.15 | 513.63 | 192.736 | 12011.3075 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 55.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2017-18 | [5 empty] | 10.94 | [9 empty] | 10.94
2018-19 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2018-19 | [5 empty] | 10.94 | [9 empty] | 10.94
2019-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2019-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2020-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2020-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2021-22 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2021-22 | [5 empty] | 10.94 | [9 empty] | 10.94
2022-23 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2022-23 | [5 empty] | 10.94 | [9 empty] | 10.94
2023-24 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2023-24 | [5 empty] | 10.94 | [9 empty] | 10.94
2024-25 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2024-25 | [5 empty] | 10.94 | [9 empty] | 10.94
2025-26 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2025-26 | [5 empty] | 10.94 | [9 empty] | 10.94
2026-27 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2026-27 | [5 empty] | 10.94 | [9 empty] | 10.94
2027-28 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2027-28 | [5 empty] | 10.94 | [9 empty] | 10.94
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 3_Gen80_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497 | 0 | 0
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349 | 0 | 0
2017-18 | 45.33 | 102.69 | 8.0505 | 0.50171 |  | 0
2018-19 | 57.31 | 152.56 | 12.3577 | 0.77013 |  | 0
2019-21 | 71.92 | 204.45 | 16.746 | 1.0436 |  | 0
2020-21 | 93.9 | 282.5 | 23.7877 | 1.4825 |  | 0
2021-22 | 97.42 | 315.47 | 32.7792 | 2.0428 |  | 0
2022-23 | 116.01 | 402.04 | 41.1385 | 2.5638 |  | 0
2023-24 | 127.58 | 429.41 | 46.9333 | 2.9249 |  | 0
2024-25 | 141.57 | 513.72 | 66.6977 | 4.1566 |  | 0
2025-26 | 156.78 | 582.51 | 83.4095 | 5.1981 |  | 0
2026-27 | 171.89 | 698.19 | 105.0415 | 6.5462 |  | 0
2027-28 | 181.5 | 790.49 | 125.9965 | 7.8521 |  | 0
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 40.55 | 90.89 | 27.267 | 1699.2794 |  |  | 2016-17 | 0 | 90.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 40.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 722.45 | 409.4 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.21 | 82.53 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 11 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 84.75 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 27.39 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 128.17 | 0 | 0 | 0 | 24.39 | 0 | 0 | 0 | 0 | 0 | 32.92 | 0 | 0 | 0 | 24.39 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 175.32 | 0 | 0 | 0 | 29.13 | 0 | 0 | 0 | 0 | 0 | 42.79 | 0 | 0 | 0 | 29.13 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 244.65 | 0 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0 | 56.05 | 0 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 276.62 | 0 | 0 | 0 | 38.85 | 0 | 0 | 0 | 0 | 0 | 58.57 | 0 | 0 | 0 | 38.85 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 354.47 | 0 | 0 | 0 | 47.57 | 0 | 0 | 0 | 0 | 0 | 68.44 | 0 | 0 | 0 | 47.57 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 374.72 | 0 | 0 | 0 | 54.69 | 0 | 0 | 0 | 0 | 0 | 76.6 | 0 | 0 | 0 | 50.98 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 449.47 | 0 | 0 | 0 | 64.25 | 0 | 0 | 0 | 0 | 0 | 86.28 | 0 | 0 | 0 | 55.29 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 501.44 | 0 | 0 | 0 | 81.07 | 0 | 0 | 0 | 0 | 0 | 95.16 | 0 | 0 | 0 | 61.62 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 602.45 | 0 | 0 | 0 | 95.74 | 0 | 0 | 0 | 0 | 0 | 104.78 | 0 | 0 | 0 | 67.11 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 678.16 | 0 | 0 | 0 | 112.33 | 0 | 0 | 0 | 0 | 0 | 109.31 | 0 | 0 | 0 | 72.19 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 237.82 | 1149.93 | 620.317 | 38658.1554 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 324.42 | 68.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.44 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 45.33 | 102.69 | 30.807 | 1919.8922 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 57.31 | 152.56 | 45.768 | 2852.2618 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 71.92 | 204.45 | 61.335 | 3822.3972 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 93.9 | 282.5 | 84.75 | 5281.62 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 97.42 | 315.47 | 110.426 | 6881.7483 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 22.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 116.01 | 402.04 | 133.135 | 8296.9732 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 17.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 127.58 | 429.41 | 154.016 | 9598.2771 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 35.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 141.57 | 513.72 | 219.748 | 13694.6954 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 93.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 156.78 | 582.51 | 269.309 | 16783.3369 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 135.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 171.89 | 698.19 | 340.084 | 21194.0349 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 186.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 181.5 | 790.49 | 404.545 | 25211.2444 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 239.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 320.18 | 212.78 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 96.3 | 52.26 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0.09 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 3.32 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 3.32 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 4.37 | 0 | 0 | 0 | 8.14 | 0 | 0 | 0 | 0 | 0 | 4.37 | 0 | 0 | 0 | 8.14 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 14 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 7.28 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 44.4 | 0 | 0 | 0 | 14.77 | 0 | 0 | 0 | 0 | 0 | 15.82 | 0 | 0 | 0 | 14.77 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 73.16 | 0 | 0 | 0 | 19.95 | 0 | 0 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 19.95 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 78.93 | 0 | 0 | 0 | 20.62 | 0 | 0 | 0 | 0 | 0 | 24.66 | 0 | 0 | 0 | 20.62 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 116.18 | 0 | 0 | 0 | 25.96 | 0 | 0 | 0 | 0 | 0 | 33.52 | 0 | 0 | 0 | 25.96 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 165.47 | 0 | 0 | 0 | 30.8 | 0 | 0 | 0 | 0 | 0 | 42.06 | 0 | 0 | 0 | 30.8 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 210.29 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 52.01 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 266.71 | 0 | 0 | 0 | 39.41 | 0 | 0 | 0 | 0 | 0 | 59.46 | 0 | 0 | 0 | 39.41 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 152.1 | 536.5 | 188.607 | 11753.9882 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 39.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 1.75 | 1.75 | 0.525 | 32.718 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 7.62 | 7.62 | 2.286 | 142.4635 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 12.51 | 12.51 | 3.753 | 233.887 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 19.91 | 26.63 | 7.989 | 497.8745 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 30.59 | 59.17 | 17.751 | 1106.2423 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 42.35 | 93.11 | 27.933 | 1740.7846 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 45.28 | 99.55 | 29.865 | 1861.1868 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 59.48 | 142.14 | 42.642 | 2657.4494 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 72.86 | 196.27 | 58.881 | 3669.4639 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 86.94 | 245.22 | 73.566 | 4584.6331 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 98.87 | 306.12 | 91.836 | 5723.2195 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2017-18 | [5 empty] | 10.94 | [9 empty] | 10.94
2018-19 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2018-19 | [5 empty] | 10.94 | [9 empty] | 10.94
2019-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2019-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2020-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2020-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2021-22 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2021-22 | [5 empty] | 10.94 | [9 empty] | 10.94
2022-23 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2022-23 | [5 empty] | 10.94 | [9 empty] | 10.94
2023-24 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2023-24 | [5 empty] | 10.94 | [9 empty] | 10.94
2024-25 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2024-25 | [5 empty] | 10.94 | [9 empty] | 10.94
2025-26 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2025-26 | [5 empty] | 10.94 | [9 empty] | 10.94
2026-27 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2026-27 | [5 empty] | 10.94 | [9 empty] | 10.94
2027-28 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2027-28 | [5 empty] | 10.94 | [9 empty] | 10.94
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 3_Gen100_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497 | 0 | 0
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349 | 0 | 0
2017-18 | 25.33 | 30.58 | 2.6355 | 0.16424 | 200.614 | 17.2127
2018-19 | 40.58 | 63.45 | 5.4255 | 0.33812 | 224.5412 | 19.2656
2019-21 | 52.41 | 100.63 | 8.6273 | 0.53765 | 239.8765 | 20.5814
2020-21 | 66.16 | 149.58 | 12.7688 | 0.79575 | 268.984 | 23.0788
2021-22 | 75.39 | 209.15 | 17.5688 | 1.0949 | 314.5082 | 26.9848
2022-23 | 97.03 | 254.86 | 21.483 | 1.3388 | 364.8098 | 31.3007
2023-24 | 107.16 | 319.2 | 27.7372 | 1.7286 | 411.1435 | 35.2761
2024-25 | 116.86 | 364.36 | 33.6508 | 2.0971 | 403.529 | 34.6228
2025-26 | 137.49 | 427.41 | 46.7118 | 2.9111 | 471.0122 | 40.4129
2026-27 | 151.78 | 524.78 | 67.9965 | 4.2375 | 641.5037 | 55.041
2027-28 | 164.71 | 615.98 | 83.6227 | 5.2114 | 741.7862 | 63.6453
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 40.55 | 90.89 | 27.267 | 1699.2794 |  |  | 2016-17 | 0 | 90.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 40.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 722.45 | 409.4 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.21 | 82.53 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 11 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 | 251.44 | 1.48 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 12.64 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 7.39 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 | 310.78 | 11.24 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 39.83 | 0 | 0 | 0 | 23.62 | 0 | 0 | 0 | 0 | 0 | 16.96 | 0 | 0 | 0 | 23.62 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 | 22.33 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 71.56 | 0 | 0 | 0 | 29.07 | 0 | 0 | 0 | 0 | 0 | 23.34 | 0 | 0 | 0 | 29.07 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 | 0 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 111.42 | 0 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 | 0 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 170.39 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 36.63 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 | 0 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 206.82 | 0 | 0 | 0 | 48.04 | 0 | 0 | 0 | 0 | 0 | 48.99 | 0 | 0 | 0 | 48.04 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 | 0 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 265.31 | 0 | 0 | 0 | 53.89 | 0 | 0 | 0 | 0 | 0 | 57.12 | 0 | 0 | 0 | 50.04 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 | 4.26 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 299.19 | 0 | 0 | 0 | 65.17 | 0 | 0 | 0 | 0 | 0 | 61.66 | 0 | 0 | 0 | 55.2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 | 12.51 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 346.34 | 0 | 0 | 0 | 81.07 | 0 | 0 | 0 | 0 | 0 | 74.96 | 0 | 0 | 0 | 62.53 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 | 36.86 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 429.47 | 0 | 0 | 0 | 95.31 | 0 | 0 | 0 | 0 | 0 | 84.83 | 0 | 0 | 0 | 66.95 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 | 69.26 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 504.8 | 0 | 0 | 0 | 111.18 | 0 | 0 | 0 | 0 | 0 | 92.59 | 0 | 0 | 0 | 72.12 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 237.82 | 1149.93 | 620.317 | 38658.1554 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 324.42 | 68.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.44 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 25.33 | 30.58 | 9.174 | 571.7237 | 827.95 | 332.51 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 40.58 | 63.45 | 19.035 | 1186.2612 | 856.51 | 378.23 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 52.41 | 100.63 | 30.189 | 1881.3785 | 979.9 | 495.28 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 66.16 | 149.58 | 44.874 | 2796.5477 | 1251.59 | 541.47 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 75.39 | 209.15 | 62.745 | 3910.2684 | 1562.92 | 637.41 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 97.03 | 254.86 | 76.458 | 4764.8626 | 1799.32 | 749.12 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 107.16 | 319.2 | 100.275 | 6249.138 | 2093.35 | 841.05 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 6.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 116.86 | 364.36 | 115.538 | 7200.3282 | 2023.1 | 784.65 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 137.49 | 427.41 | 155.278 | 9676.925 | 2500 | 906.65 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 38.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 151.78 | 524.78 | 219.804 | 13698.1853 | 3502.55 | 1302.22 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 89.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 164.71 | 615.98 | 268.773 | 16749.9334 | 4151.26 | 1498.81 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 119.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 320.18 | 212.78 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 96.3 | 52.26 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 | 70.32 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 | 97.45 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 1.37 | 0 | 0 | 0 | 21.37 | 0 | 0 | 0 | 0 | 0 | 1.37 | 0 | 0 | 0 | 21.37 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 23.84 | 0 | 0 | 0 | 25.04 | 0 | 0 | 0 | 0 | 0 | 11.58 | 0 | 0 | 0 | 25.04 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 56.31 | 0 | 0 | 0 | 30.76 | 0 | 0 | 0 | 0 | 0 | 15.54 | 0 | 0 | 0 | 30.76 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 117.29 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 33.11 | 0 | 0 | 0 | 34.93 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 154.3 | 0 | 0 | 0 | 39.41 | 0 | 0 | 0 | 0 | 0 | 36.93 | 0 | 0 | 0 | 39.41 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 152.1 | 536.5 | 188.607 | 11753.9882 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 39.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 1.66 | 1.66 | 0.498 | 31.0354 | 511.66 | 100.36 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 4.3 | 4.3 | 1.29 | 80.3928 | 550.32 | 115.74 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 8.08 | 8.08 | 2.424 | 151.0637 | 587.57 | 194.1 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 12.63 | 12.63 | 3.789 | 236.1305 | 623.62 | 191.92 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 15.3 | 15.3 | 4.59 | 286.0488 | 671.13 | 202.33 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 19.96 | 19.96 | 5.988 | 373.1722 | 686.07 | 270.34 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 22.74 | 22.74 | 6.822 | 425.147 | 698.58 | 311.8 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 36.62 | 48.88 | 14.664 | 913.8605 | 764.73 | 324.62 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 46.3 | 87.07 | 26.121 | 1627.8607 | 775.34 | 375.77 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 68.04 | 152.22 | 45.666 | 2845.9051 | 918.95 | 452.79 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 76.34 | 193.71 | 58.113 | 3621.6022 | 1031.11 | 489.27 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2017-18 | [5 empty] | 10.94 | [9 empty] | 10.94
2018-19 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2018-19 | [5 empty] | 10.94 | [9 empty] | 10.94
2019-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2019-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2020-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2020-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2021-22 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2021-22 | [5 empty] | 10.94 | [9 empty] | 10.94
2022-23 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2022-23 | [5 empty] | 10.94 | [9 empty] | 10.94
2023-24 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2023-24 | [5 empty] | 10.94 | [9 empty] | 10.94
2024-25 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2024-25 | [5 empty] | 10.94 | [9 empty] | 10.94
2025-26 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2025-26 | [5 empty] | 10.94 | [9 empty] | 10.94
2026-27 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2026-27 | [5 empty] | 10.94 | [9 empty] | 10.94
2027-28 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2027-28 | [5 empty] | 10.94 | [9 empty] | 10.94
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 3_Gen120_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497 | 0 | 0
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349 | 0 | 0
2017-18 | 17.94 | 17.94 | 1.6875 | 0.10516 |  | 0
2018-19 | 24.48 | 24.48 | 2.5027 | 0.15597 |  | 0
2019-21 | 48.23 | 52 | 4.98 | 0.31035 |  | 0
2020-21 | 58.14 | 84.59 | 7.8945 | 0.49199 |  | 0
2021-22 | 55.49 | 104.14 | 9.693 | 0.60407 |  | 0
2022-23 | 71.54 | 148.82 | 13.53 | 0.84319 |  | 0
2023-24 | 81.7 | 198.33 | 17.4405 | 1.0869 |  | 0
2024-25 | 98.91 | 251.6 | 21.8483 | 1.3616 |  | 0
2025-26 | 116.77 | 306.59 | 26.876 | 1.6749 |  | 0
2026-27 | 126.06 | 398.5 | 37.0755 | 2.3105 |  | 0
2027-28 | 141.1 | 460.2 | 48.736 | 3.0372 |  | 0
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 40.55 | 90.89 | 27.267 | 1699.2794 |  |  | 2016-17 | 0 | 90.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 40.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 722.45 | 409.4 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.21 | 82.53 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 11 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 24.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 22.94 | 0 | 0 | 0 | 29.06 | 0 | 0 | 0 | 0 | 0 | 19.17 | 0 | 0 | 0 | 29.06 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 50.03 | 0 | 0 | 0 | 34.56 | 0 | 0 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 34.56 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 65.38 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 16.73 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 101.24 | 0 | 0 | 0 | 47.58 | 0 | 0 | 0 | 0 | 0 | 23.96 | 0 | 0 | 0 | 47.58 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 144.58 | 0 | 0 | 0 | 53.75 | 0 | 0 | 0 | 0 | 0 | 31.75 | 0 | 0 | 0 | 49.95 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 186.42 | 0 | 0 | 0 | 65.18 | 0 | 0 | 0 | 0 | 0 | 43.58 | 0 | 0 | 0 | 55.33 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 226.4 | 0 | 0 | 0 | 80.19 | 0 | 0 | 0 | 0 | 0 | 55.11 | 0 | 0 | 0 | 61.66 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 302.84 | 0 | 0 | 0 | 95.66 | 0 | 0 | 0 | 0 | 0 | 59.76 | 0 | 0 | 0 | 66.3 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
2027-28 | 20.34 | 20.34 | 6.102 | 380.2766 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 348.69 | 0 | 0 | 0 | 111.51 | 0 | 0 | 0 | 0 | 0 | 69.61 | 0 | 0 | 0 | 71.49 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 237.82 | 1149.93 | 620.317 | 38658.1554 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 324.42 | 68.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.44 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 17.94 | 17.94 | 5.382 | 335.4062 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 24.48 | 24.48 | 7.344 | 457.6781 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 48.23 | 52 | 15.6 | 972.192 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 58.14 | 84.59 | 25.377 | 1581.4946 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 55.49 | 104.14 | 31.242 | 1947.0014 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 71.54 | 148.82 | 44.646 | 2782.3387 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 81.7 | 198.33 | 59.499 | 3707.9777 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 98.91 | 251.6 | 75.48 | 4703.9136 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 116.77 | 306.59 | 92.831 | 5785.2279 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 126.06 | 398.5 | 125.934 | 7848.2069 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 9.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 141.1 | 460.2 | 159.613 | 9947.0822 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 30.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 320.18 | 212.78 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 96.3 | 52.26 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 21.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 25.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 30.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 17.9 | 0 | 0 | 0 | 34.94 | 0 | 0 | 0 | 0 | 0 | 8.85 | 0 | 0 | 0 | 34.94 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 53 | 0 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0 | 16.71 | 0 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 152.1 | 536.5 | 188.607 | 11753.9882 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 39.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 1.66 | 1.66 | 0.498 | 31.0354 |  |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 4.3 | 4.3 | 1.29 | 80.3928 |  |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 8.08 | 8.08 | 2.424 | 151.0637 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 12.63 | 12.63 | 3.789 | 236.1305 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 15.3 | 15.3 | 4.59 | 286.0488 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 19.96 | 19.96 | 5.988 | 373.1722 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 21.37 | 21.37 | 6.411 | 399.5335 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 25.04 | 25.04 | 7.512 | 468.1478 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 30.75 | 30.75 | 9.225 | 574.902 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 43.79 | 52.84 | 15.852 | 987.8966 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 56.13 | 92.42 | 27.726 | 1727.8843 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2017-18 | [5 empty] | 10.94 | [9 empty] | 10.94
2018-19 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2018-19 | [5 empty] | 10.94 | [9 empty] | 10.94
2019-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2019-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2020-21 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2020-21 | [5 empty] | 10.94 | [9 empty] | 10.94
2021-22 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2021-22 | [5 empty] | 10.94 | [9 empty] | 10.94
2022-23 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2022-23 | [5 empty] | 10.94 | [9 empty] | 10.94
2023-24 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2023-24 | [5 empty] | 10.94 | [9 empty] | 10.94
2024-25 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2024-25 | [5 empty] | 10.94 | [9 empty] | 10.94
2025-26 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2025-26 | [5 empty] | 10.94 | [9 empty] | 10.94
2026-27 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2026-27 | [5 empty] | 10.94 | [9 empty] | 10.94
2027-28 | 10.94 | 10.94 | 3.282 | 204.5342 |  |  | 2027-28 | [5 empty] | 10.94 | [9 empty] | 10.94
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
2017-18
2018-19
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28

## Stage 3_ACCR_SMFL
stage 3 100MW embedded generation at Bendigo
15 minute rating
SRMC($) | 85.8 |  | Case type
VCR ($k) | 62.32 |  | F | P | Partial , only consider BATS - MLTS and BATS - BETS limitations
Discount Rate | 0.1
Years | 40 |  |  | F | Full, consider all limitations.
10% POE | 0.3
50% POE | 0.7
S1, TSDF + 220kV new gen location | 0.25
S2, TSDF + 500kV new genlocation | 0.25
S7, NEFR + 220kV new gen location | 0.25
S8, NEFR + 500kV new gen location | 0.25
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M) | Expected Generation (MWh) | Generation Cost ($K) |  | Generation cost is minimal and has not been included in the cost of the embedded generation option in the Cost-Benefit summary sheet
2014-15 | 175.62 | 902.92 | 289.396 | 18.0352 | 0 | 0
2015-16 | 207.1 | 985.37 | 328.8995 | 20.497 | 0 | 0
2016-17 | 237.82 | 1149.93 | 209.1602 | 13.0349 | 0 | 0
2017-18 | 17.57 | 33.18 | 2.706 | 0.16864 | 200.614 | 17.2127
2018-19 | 27.35 | 58.68 | 4.7453 | 0.29572 | 224.5412 | 19.2656
2019-21 | 38.18 | 104.31 | 8.2973 | 0.51708 | 239.8765 | 20.5814
2020-21 | 46.69 | 161.66 | 12.9307 | 0.80584 | 268.984 | 23.0788
2021-22 | 55.93 | 198.95 | 17.4945 | 1.0903 | 314.5082 | 26.9848
2022-23 | 78.74 | 265.89 | 25.4055 | 1.5833 | 364.8098 | 31.3007
2023-24 | 92.4 | 334.4 | 36.251 | 2.2592 | 411.1435 | 35.2761
2024-25 | 105.88 | 411.4 | 50.48 | 3.1459 | 403.529 | 34.6228
2025-26 | 121.96 | 481.43 | 64.8127 | 4.0391 | 471.0122 | 40.4129
2026-27 | 132.19 | 549.92 | 81.3328 | 5.0687 | 641.5037 | 55.041
2027-28 | 148.27 | 665.1 | 105.5102 | 6.5754 | 741.7862 | 63.6453
[7 empty] | 10% POE S1 | [30 empty] | 10% POE S2
Scenario 1 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2014-15 | 342.09 | 549.29 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 67.63 | 96.45 | 0 | 0 | 0 | 11.54 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2015-16 | 640.47 | 330.08 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 121.8 | 70.48 | 0 | 0 | 0 | 14.82 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2016-17 | 40.55 | 90.89 | 27.267 | 1699.2794 |  |  | 2016-17 | 0 | 90.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 40.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2016-17 | 722.45 | 409.4 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 137.21 | 82.53 | 0 | 0 | 0 | 18.08 | 0 | 0 | 0 | 0 | 11 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 2.9 | 2.9 | 0.87 | 54.2184 | 251.44 | 1.48 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2017-18 | 0 | 3.36 | 0 | 0 | 0 | 3.56 | 0.53 | 0 | 0 | 25.73 | 0 | 3.36 | 0 | 0 | 0 | 3.56 | 0.53 | 0 | 0 | 10.12 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 4
2018-19 | 4.59 | 4.59 | 1.377 | 85.8146 | 310.78 | 11.24 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2018-19 | 0 | 13.16 | 0 | 0 | 0 | 8.99 | 0 | 0 | 0 | 36.53 | 0 | 8.24 | 0 | 0 | 0 | 8.99 | 0 | 0 | 0 | 10.12 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2019-21 | 6.32 | 6.32 | 1.896 | 118.1587 | 22.33 |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2019-21 | 0 | 39.37 | 0 | 0 | 0 | 13.99 | 0 | 0 | 0 | 50.95 | 0 | 14.07 | 0 | 0 | 0 | 13.99 | 0 | 0 | 0 | 10.12 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2020-21 | 8.04 | 8.04 | 2.412 | 150.3158 | 0 |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2020-21 | 0 | 88.07 | 0 | 0 | 0 | 14.84 | 0 | 0 | 0 | 58.75 | 0 | 21.73 | 0 | 0 | 0 | 14.84 | 0 | 0 | 0 | 10.12 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2021-22 | 9.8 | 9.8 | 2.94 | 183.2208 | 0 |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2021-22 | 0 | 121.41 | 0 | 0 | 0 | 18.79 | 0 | 0 | 0 | 58.75 | 0 | 27.02 | 0 | 0 | 0 | 18.79 | 0 | 0 | 0 | 10.12 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2022-23 | 11.62 | 11.62 | 3.486 | 217.2475 | 0 |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2022-23 | 0 | 175.2 | 0 | 0 | 0 | 27.53 | 0 | 0 | 0 | 63.16 | 0 | 41.09 | 0 | 0 | 0 | 27.53 | 0 | 0 | 0 | 10.12 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7
2023-24 | 12.84 | 12.84 | 3.852 | 240.0566 | 0 |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2023-24 | 0 | 230.89 | 0 | 0 | 0 | 35.04 | 0 | 0 | 0 | 68.47 | 0 | 47.24 | 0 | 0 | 0 | 35.04 | 0 | 0 | 0 | 10.12 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7
2024-25 | 14.67 | 14.67 | 4.401 | 274.2703 | 4.26 |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2024-25 | 0 | 302.76 | 0 | 0 | 0 | 40.17 | 0 | 0 | 0 | 68.47 | 0 | 55.59 | 0 | 0 | 0 | 40.17 | 0 | 0 | 0 | 10.12 | 0 | 9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7
2025-26 | 16.53 | 16.53 | 4.959 | 309.0449 | 12.51 |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 13.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2025-26 | 0 | 349.91 | 0 | 0 | 0 | 49.61 | 0 | 0 | 0 | 81.91 | 0 | 64.89 | 0 | 0 | 0 | 46.95 | 0 | 0 | 0 | 10.12 | 0 | 7 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 9
2026-27 | 18.42 | 18.42 | 5.526 | 344.3803 | 36.86 |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0 | 13.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2026-27 | 0 | 403.65 | 0 | 0 | 0 | 55.78 | 0 | 0 | 0 | 90.49 | 0 | 72.16 | 0 | 0 | 0 | 49.91 | 0 | 0 | 0 | 10.12 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 10
2027-28 | 20.34 | 20.34 | 10.54 | 656.8528 | 69.26 |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2027-28 | 0 | 492.69 | 0 | 0 | 0 | 67.48 | 0 | 0 | 0 | 104.93 | 0 | 80.62 | 0 | 0 | 0 | 57.53 | 0 | 0 | 0 | 10.12 | 0 | 11 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12
[7 empty] | 50% POE S1 | [30 empty] | 50% POE S2
Scenario 2 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 175.62 | 902.92 | 442.838 | 27597.6642 |  |  | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 59.51 | 186.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.55 | 49.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 207.1 | 985.37 | 519.527 | 32376.9226 |  |  | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 287.73 | 32.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.98 | 21.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 237.82 | 1149.93 | 620.317 | 38658.1554 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 324.42 | 68.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.44 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 17.57 | 33.18 | 9.954 | 620.3333 | 827.95 | 332.51 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 27.35 | 58.68 | 17.604 | 1097.0813 | 856.51 | 378.23 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 38.18 | 104.31 | 31.293 | 1950.1798 | 979.9 | 495.28 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 46.69 | 161.66 | 48.498 | 3022.3954 | 1251.59 | 541.47 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 55.93 | 198.95 | 59.685 | 3719.5692 | 1562.92 | 637.41 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 78.74 | 265.89 | 86.718 | 5404.2658 | 1799.32 | 749.12 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2023-24 | 92.4 | 334.4 | 119.99 | 7477.7768 | 2093.35 | 841.05 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 2.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.41 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.12 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2024-25 | 105.88 | 411.4 | 163.628 | 10197.297 | 2023.1 | 784.65 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 22.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.07 | 0 | 10.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.12 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2025-26 | 121.96 | 481.43 | 206.295 | 12856.3044 | 2500 | 906.65 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 45.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.15 | 0 | 20.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.12 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2026-27 | 132.19 | 549.92 | 258.944 | 16137.3901 | 3502.55 | 1302.22 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 77.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.49 | 0 | 26.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.12 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2027-28 | 148.27 | 665.1 | 335.253 | 20892.967 | 4151.26 | 1498.81 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 135.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.75 | 0 | 35.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
[7 empty] | 10% POE S7 | [30 empty] | 10% POE S8
Scenario 7 :Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 42.19 | 317.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.24 | 74.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 275.91 | 158.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.53 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 1.5 | 1.5 | 0.45 | 28.044 |  |  | 2016-17 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 320.18 | 212.78 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 96.3 | 52.26 | 0 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 | 70.32 |  | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 | 97.45 |  | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 |  |  | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 0 | 0 | 0 | 0 |  |  | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2021-22 | 0 | 0 | 0 | 0 |  |  | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 1.97 | 0 | 0 | 0 | 22.54 | 0 | 0 | 0 | 0 | 0 | 1.97 | 0 | 0 | 0 | 9.95 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2022-23 | 0 | 0 | 0 | 0 |  |  | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 3.22 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 34.64 | 0 | 1.75 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 10.12 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2023-24 | 0 | 0 | 0 | 0 |  |  | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 17.69 | 0 | 0 | 0 | 8.2 | 0 | 0 | 0 | 44.65 | 0 | 6.81 | 0 | 0 | 0 | 8.2 | 0 | 0 | 0 | 10.12 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2024-25 | 0 | 0 | 0 | 0 |  |  | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 52.28 | 0 | 0 | 0 | 11.74 | 0 | 0 | 0 | 48.95 | 0 | 15.67 | 0 | 0 | 0 | 11.74 | 0 | 0 | 0 | 10.12 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2025-26 | 1.63 | 1.63 | 0.489 | 30.4745 |  |  | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2025-26 | 0 | 87.95 | 0 | 0 | 0 | 17.56 | 0 | 0 | 0 | 52.85 | 0 | 25.08 | 0 | 0 | 0 | 17.56 | 0 | 0 | 0 | 10.12 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2026-27 | 3.3 | 3.3 | 0.99 | 61.6968 |  |  | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2026-27 | 0 | 120.19 | 0 | 0 | 0 | 21.53 | 0 | 0 | 0 | 57.85 | 0 | 30.79 | 0 | 0 | 0 | 21.53 | 0 | 0 | 0 | 10.12 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2027-28 | 5.01 | 5.01 | 1.503 | 93.667 |  |  | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2027-28 | 0 | 164.76 | 0 | 0 | 0 | 25.64 | 0 | 0 | 0 | 58.75 | 0 | 39.73 | 0 | 0 | 0 | 25.64 | 0 | 0 | 0 | 10.12 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
[7 empty] | 50% POE S7 | [30 empty] | 50% POE S8
Scenario 8 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count |  | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 101.17 | 360.01 | 135.954 | 8472.6533 |  |  | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014-15 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015-16 | 115.89 | 434.75 | 138.272 | 8617.111 |  |  | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-16 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-17 | 152.1 | 536.5 | 188.607 | 11753.9882 |  |  | 2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-17 | 39.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017-18 | 0 | 0 | 0 | 0 | 511.66 | 100.36 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018-19 | 0 | 0 | 0 | 0 | 550.32 | 115.74 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019-21 | 0 | 0 | 0 | 0 | 587.57 | 194.1 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-21 | 2.42 | 2.71 | 0.813 | 50.6662 | 623.62 | 191.92 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-22 | 11.92 | 24.51 | 7.353 | 458.239 | 671.13 | 202.33 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-23 | 12.07 | 38.06 | 11.418 | 711.5698 | 686.07 | 270.34 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-24 | 25.13 | 70.54 | 21.162 | 1318.8158 | 698.58 | 311.8 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-25 | 37.53 | 112.97 | 33.891 | 2112.0871 | 764.73 | 324.62 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-26 | 52.76 | 158.36 | 47.508 | 2960.6986 | 775.34 | 375.77 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-27 | 62.44 | 199.57 | 59.871 | 3731.1607 | 918.95 | 452.79 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-28 | 75.49 | 249.15 | 74.745 | 4658.1084 | 1031.11 | 489.27 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% POE S9
Scenario 9 - Limitation | [7 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000) |  |  | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15 | 0 | 0 | 0 | 0 |  |  | 2014-15
2015-16 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2015-16 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82 |  |  |  |  | 4 |  |  |  | 1 | 1
2016-17 | 207.11 | 990.79 | 521.293 | 32486.9798 |  |  | 2016-17 | 647.95 | 328.02 |  |  |  | 14.82 |  |  |  |  | 121.8 | 70.49 |  |  |  | 14.82
2017-18 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2017-18 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2018-19 | 100.86 | 456.16 | 252.334 | 15725.4549 |  |  | 2018-19 |  | 445.22 |  |  |  | 10.94 | [5 empty] | 89.92 |  |  |  | 10.94
2019-21 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2019-21 | [9 empty] | 3.91 | [9 empty] | 3.91
2020-21 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2020-21 | [9 empty] | 3.91 | [9 empty] | 3.91
2021-22 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2021-22 | [9 empty] | 3.91 | [9 empty] | 3.91
2022-23 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2022-23 | [9 empty] | 3.91 | [9 empty] | 3.91
2023-24 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2023-24 | [9 empty] | 3.91 | [9 empty] | 3.91
2024-25 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2024-25 | [9 empty] | 3.91 | [9 empty] | 3.91
2025-26 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2025-26 | [9 empty] | 3.91 | [9 empty] | 3.91
2026-27 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2026-27 | [9 empty] | 3.91 | [9 empty] | 3.91
2027-28 | 3.91 | 3.91 | 1.173 | 73.1014 |  |  | 2027-28 | [9 empty] | 3.91 | [9 empty] | 3.91
50% POE S9
[8 empty] | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Sum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Maximum | Count | Count | Count | Count | Count | Count | Count | Count | Count | Count
[7 empty] | Year | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT | VBAT | VBE6 | VBE2 | VHOT | VSHT | VWE6 | VKG6 | VRC6 | VKG2 | VFVT
2014-15
[7 empty] | 2015-16 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2016-17 | 288.39 | 31.69 | [8 empty] | 78.19 | 21.07
[7 empty] | 2017-18 |  | 164.98 | [9 empty] | 47.04
[7 empty] | 2018-19 |  | 164.98 | [9 empty] | 47.04
2019-21
2020-21
2021-22
2022-23
2023-24
2024-25
2025-26
2026-27
2027-28