## Introduction
Appendix D - Detailed NPV analysis
This Appendix presents the detailed NPV results for the RIT-T analysis.
Do Nothing option and eleven credible options assessed in this RIT-T are presented in this spreadsheet.
Sensitivity analysis results to discount rate, capital cost, and the value of customer reliability (VCR) are presented on a scenario weighted basis.
Unweighted scenario results are also presented, for each of the five reasonable scenarios assessed under the RIT-T, applying the base set of assumptions for discount rate, capital cost, and VCR.
Sensitivity analysis to different scenario weights are also presented, applying the base set of assumptions for discount rate, capital cost, and VCR.
The table presents the:
~ Maximum load at risk (MW) - which is the MW load shedding required to avoid the network limitation under the highest POE demand conditions and highest impacting scenario of the presented assessment
~ Maximum load at risk reduction (MW) - which is the MW load shedding reduction under the highest POE demand conditions and highest impacting scenario of the presented assessment as a result of implementing the respective credible option
~ Maximum energy at risk (MWh) - which is the MWh unserved energy required to avoid the network limitation under the highest POE demand conditions and highest impacting scenario of the presented assessment
~ Maximum energy at risk reduction (MWh) - which is the MWh unserved energy reduction under the highest POE demand conditions and highest impacting scenario of the presented assessment as a result of implementing the respective credible option
~ Expected unserved energy (MWh) - which is the portion of the energy at risk after taking into account the probability of the limitation occurring, including the probability of demand conditions occurring and weighted across the reasonable scenarios considered in the presented assessment
~ Expected unserved energy reduction (MWh) - which is the portion of the energy at risk reduction after taking into account the probability of the limitation occurring, including the probability of demand conditions occurring and weighted across the reasonable scenarios considered in the presented assessment as a result of implementing the respective credible option
~ Annualised gross market benefits ($ '000 or $M) - which is the annual benefit cost of the expected unserved energy, obtained by multiplying the benefit of the expected unserved energy by the VCR, and the change in dispatch cost from the "base case" as compared with the option of scenarios considered in the presented assessment
~ Annualised gross market benefits based on year in service ($ '000 or $M) - which is the annual benefit cost of the expected unserved energy, obtained by multiplying the benefit of the expected unserved energy by the VCR, and the change in dispatch cost from the "base case" as compared with the option of scenarios considered in the presented assessment in the corresponding year
~ Annualised net market benefits ($ '000 or $M) - which is the annual benefit cost of the expected unserved energy, obtained by multiplying the benefit of the expected unserved energy by the VCR and minus the annualised project cost, and the change in dispatch cost from the "base case" as compared with the option of scenarios considered in the presented assessment
~ Annualised project cost ($M) - which is the cost of the project calculated annually based on the assumed life of the asset and discount rate, this cost is used to identify the optimal time for augmentation associated with the options considered in the assessment presented
~ Year in Service - which is the year when practical completion of the respective stages in a credible option. Completion of all stages ="Y", completion of stage 1 = "Y1" and completion of stages 1 & 2 = "Y2"
~ Dispatch cost ($ '000) - which is the generation rescheduling, demand management dispatch and local generation dispatch cost change compared to the base case - do nothing - option for the scenario presented in assessment
~ Limitation cost ($ '000 or $M) - which is the cost of the sum of the expected unserved energy, obtained by multiplying the expected unserved energy by the VCR, and the change in dispatch cost from the "base case" - option of the scenarios considered in the presented assessment

## NPV_Summary
Table 16: Gross market benefits for each credible option (NPV, $M)
Options | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Weighted Gross Market Benefits
Scenario weights | 20% | 20% | 20% | 20% | 20%
Option 1a | 291.4742 | 794.8078 | 235.1296 | 540.6635 | 150.5314 | 402.5213
Option 1b | 314.5681 | 809.5856 | 255.9541 | 556.7246 | 188.2542 | 425.0173
Option 2 | 293.2074 | 796.6544 | 235.4665 | 540.6875 | 150.0545 | 403.2141
Option 3a | 289.0961 | 795.6809 | 293.2495 | 550.8749 | 167.1798 | 419.2163
Option 3b | 312.1024 | 814.2995 | 314.5291 | 570.9799 | 206.2095 | 443.6241
Option 4a | 289.0961 | 795.1712 | 293.1917 | 551.015 | 167.6133 | 419.2175
Option 4b | 312.0639 | 814.2995 | 314.5291 | 570.9799 | 206.2095 | 443.6164
Option 5 | 271.1284 | 754.9198 | 236.0798 | 526.0494 | 129.9186 | 383.6192
Option 6 | 210.1635 | 630.4921 | 218.2871 | 459.2331 | 141.814 | 331.998
Option 7 | 228.0696 | 721.9789 | 260.7821 | 489.99 | 164.4329 | 373.0507
Option 8 | 64.9435 | 202.6981 | 59.903 | 126.2926 | 44.4911 | 99.6657
Table 17: Net market benefits for each credible option (PV, $M)
Options | Project Cost | Weighted Gross Market Benefit | Net Market Benefit | Ranking under RIT-T
Option 1a | 150.165 | 402.5213 | 252.3563 | 6
Option 1b | 150.8823 | 425.0173 | 274.135 | 5
Option 2 | 152.5561 | 403.2141 | 250.6579 | 7
Option 3a | 125.536 | 419.2163 | 293.6803 | 3
Option 3b | 126.2534 | 443.6241 | 317.3707 | 1
Option 4a | 131.6335 | 419.2175 | 287.584 | 4
Option 4b | 132.3508 | 443.6164 | 311.2656 | 2
Option 5 | 205.5204 | 383.6192 | 178.0988 | 8
Option 6 | 263.2669 | 331.998 | 68.731 | 11
Option 7 | 238.638 | 373.0507 | 134.4127 | 9
Option 8 | 18.1906 | 99.6657 | 81.475 | 10
Table 18: Net present value of net market benefits (PV, $M)
Sensitivity | Discount Rate |  | Capital Cost |  | VCR
| 6% | 12% | 30% | -30% | 20% | -20%
Option 1a | 635.2078 | 152.1164 | 207.3068 | 297.4058 | 332.8606 | 171.8521
Option 1b | 643.6006 | 174.1565 | 228.8703 | 319.3997 | 359.1384 | 189.1315
Option 2 | 634.3053 | 150.2186 | 204.8911 | 296.4248 | 331.3008 | 170.0151
Option 3a | 659.4402 | 195.4601 | 256.0195 | 331.3411 | 377.5235 | 209.837
Option 3b | 678.7827 | 218.2859 | 279.4947 | 355.2467 | 406.0955 | 228.6459
Option 4a | 653.3538 | 189.362 | 248.0939 | 327.074 | 371.4275 | 203.7405
Option 4b | 672.6682 | 212.183 | 271.5603 | 350.9708 | 399.9888 | 222.5423
Option 5 | 540.2267 | 83.0918 | 116.4427 | 239.7549 | 254.8227 | 101.375
Option 6 | 394.2099 | -15.9149 | -10.2491 | 147.7111 | 135.1306 | 2.3314
Option 7 | 463.4867 | 46.3159 | 62.8213 | 206.0041 | 209.0229 | 59.8026
Option 8 | 153.8681 | 61.3044 | 76.0179 | 86.9322 | 101.702 | 61.2481
Table 19: Net market benefits under different scenario weightings (PV, $M)
Description | Net market benefit ($, M) |  |  | Scenario weighting
| Option 3a | Option 3b | Option 4b | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5
Under current scenario weightings | 293.6803 | 317.3707 | 311.2656 | 20% | 20% | 20% | 20% | 20%
Weightings of medium demand scenarios reduced | 294.2779 | 317.1881 | 311.0846 | 15.8% | 15.8% | 26.3% | 26.3% | 15.8%
Weightings of medium demand scenarios increased | 293.1395 | 317.5359 | 311.4293 | 23.8% | 23.8% | 14.3% | 14.3% | 23.8%
Weighting of 500 kV generation placement scenarios reduced | 245.4085 | 270.0578 | 263.9511 | 23.8% | 14.3% | 23.8% | 14.3% | 23.8%
Weighting of 500 kV generation placement scenarios increased | 347.0332 | 369.664 | 363.5605 | 15.8% | 26.3% | 15.8% | 26.3% | 15.8%
Weightings of high wind generator contribution to peak demand scenario reduced | 314.769 | 337.1386 | 331.0327 | 21.7% | 21.7% | 21.7% | 21.7% | 13%
Weightings of high wind generator contribution to peak demand scenario increased | 263.1015 | 288.4686 | 282.3643 | 17.6% | 17.6% | 17.6% | 17.6% | 29.4%
Table 21: Annualised cost-benefit assessment of preferred option
Year | Market impact of “do nothing” |  | Market impact of the preferred option from implementation in accordance with respective stages
| Expected unserved energy (MWh) | Limitation cost ($ million) | Expected unserved energy reduction (MWh) | Gross market benefit ($ million) | Annualised cost ($ million) | Annualised net market benefit ($ million)
2013–14 | 569.6677 | 35.2909 | 0 | 0 | 0 | 0
2014–15 | 585.8501 | 36.2934 | 0 | 0 | 0 | 0
2015–16 | 616.3063 | 38.1802 | 107.9529 | 6.6877 | 0.073356 | 6.6143
2016–17 | 751.4799 | 46.5542 | 156.9977 | 9.726 | 0.073356 | 9.6526
2017–18 | 814.4794 | 50.457 | 631.3759 | 39.1137 | 3.4722 | 35.6416
2018–19 | 824.5247 | 51.0793 | 691.3685 | 42.8303 | 3.4722 | 39.3581
2019–20 | 954.0132 | 59.1011 | 954.9436 | 59.1588 | 12.9106 | 46.2482
2020–21 | 1061.7679 | 65.7765 | 1059.4221 | 65.6312 | 12.9106 | 52.7206
2021–22 | 994.5728 | 61.6138 | 984.8583 | 61.012 | 12.9106 | 48.1014
2022–23 | 1239.6154 | 76.7942 | 1179.8886 | 73.0941 | 12.9106 | 60.1835

## Do Nothing
Do Nothing: Constraints on Ballarat-Bendigo 220 kV line and Moorabool-Ballarat No.1 220 kV line only
VCR ($k) | 61.95
Discount Rate | 10%
Years | 40
Scenario 1 | 20%
Scenario 2 | 20%
Scenario 3 | 20%
Scenario 4 | 20%
Scenario 5 | 20%
Table 4: Forecast market impact under the "Do Nothing" Option
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2013-14 | 251.05 | 1479.8 | 569.6677 | 35.2909
2014-15 | 252.88 | 1386.98 | 585.8501 | 36.2934
2015-16 | 277.81 | 1538.02 | 616.3063 | 38.1802
2016-17 | 304.78 | 2036.71 | 751.4799 | 46.5542
2017-18 | 331.37 | 2126.43 | 814.4794 | 50.457
2018-19 | 279.96 | 2378.59 | 824.5247 | 51.0793
2019-20 | 284.59 | 2365.79 | 954.0132 | 59.1011
2020-21 | 298.14 | 2976.12 | 1061.7679 | 65.7765
2021-22 | 285 | 3451.06 | 994.5728 | 61.6138
2022-23 | 330.27 | 4821.69 | 1239.6154 | 76.7942
Scenario 1 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 246.86 | 1475.43 | 632.0554 | 39155.8345
2014-15 | 249.41 | 1222.11 | 657.1946 | 40713.2079
2015-16 | 277.81 | 1140.87 | 670.0608 | 41510.2666
2016-17 | 295.34 | 1232.23 | 746.6378 | 46254.2092
2017-18 | 331.37 | 1226.09 | 755.3991 | 46796.9755
2018-19 | 245.74 | 1066.92 | 744.0456 | 46093.6249
2019-20 | 169.53 | 1252.71 | 860.8202 | 53327.8139
2020-21 | 181.21 | 1405.96 | 962.3574 | 59618.0434
2021-22 | 285 | 1246.75 | 783.047 | 48509.7592
2022-23 | 204.83 | 1324.64 | 853.7125 | 52887.4881
Scenario 2 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 251.05 | 1479.8 | 715.0869 | 44299.6322
2014-15 | 249.15 | 1386.98 | 721.075 | 44670.5987
2015-16 | 271.44 | 1538.02 | 830.2854 | 51436.183
2016-17 | 304.78 | 2036.71 | 1137.0117 | 70437.8736
2017-18 | 94.6 | 2126.43 | 1235.5013 | 76539.3043
2018-19 | 279.96 | 2378.59 | 1383.658 | 85717.6131
2019-20 | 78.18 | 2365.79 | 1514.1992 | 93804.6404
2020-21 | 158.58 | 2976.12 | 1770.9682 | 109711.4775
2021-22 | 119.77 | 3451.06 | 1883.835 | 116703.5807
2022-23 | 213.62 | 4821.69 | 2541.5105 | 157446.5742
Scenario 3 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 242.97 | 1318.8 | 552.0484 | 34199.3984
2014-15 | 252.88 | 1057.92 | 568.451 | 35215.5419
2015-16 | 258.48 | 980.47 | 555.8126 | 34432.5881
2016-17 | 276.68 | 1034.24 | 610.6057 | 37827.0219
2017-18 | 304.55 | 1090.32 | 647.142 | 40090.4469
2018-19 | 265.23 | 998.77 | 642.1257 | 39779.6859
2019-20 | 284.59 | 1133.11 | 708.7031 | 43904.1583
2020-21 | 270.69 | 1157.32 | 725.1597 | 44923.6422
2021-22 | 284.9 | 939.1 | 591.3297 | 36632.8737
2022-23 | 299.37 | 1116.65 | 689.4939 | 42714.1483
Scenario 4 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 242.97 | 1318.8 | 609.0484 | 37730.5484
2014-15 | 248.07 | 1190.43 | 622.5636 | 38567.815
2015-16 | 259.63 | 1272.7 | 685.4918 | 42466.2145
2016-17 | 293.28 | 1665.3 | 927.4634 | 57456.3601
2017-18 | 70.87 | 1618.21 | 986.2142 | 61095.9672
2018-19 | 118.43 | 1491.01 | 996.7038 | 61745.8029
2019-20 | 143.26 | 1838.94 | 1154.1038 | 71496.7329
2020-21 | 298.14 | 2051.83 | 1258.4248 | 77959.4164
2021-22 | 229.51 | 2190.03 | 1346.1022 | 83391.0288
2022-23 | 330.27 | 2787.24 | 1694.6731 | 104984.9998
Scenario 5 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 245.24 | 1344.03 | 340.0994 | 21069.1554
2014-15 | 185.7 | 836.58 | 359.9662 | 22299.9036
2015-16 | 114.11 | 557.36 | 339.8809 | 21055.6205
2016-17 | 107.52 | 504.83 | 335.6811 | 20795.4454
2017-18 | 115.2 | 550.71 | 448.1405 | 27762.3027
2018-19 | 118.76 | 517.43 | 356.0902 | 22059.7904
2019-20 | 139.94 | 714.71 | 532.2397 | 32972.2482
2020-21 | 147.17 | 811.03 | 591.9292 | 36670.0139
2021-22 | 96.35 | 516.29 | 368.5501 | 22831.6775
2022-23 | 107.05 | 639.11 | 418.6868 | 25937.6473

## Option1a
Option 1a:
Stage 1: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 82 degC in 2019-20
Stage 2: Up-rate the existing Moorabool-Ballarat 220 kV line to maximum operating temperature of 82 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 77.2 | 48.4 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 15.0989 | 9.4661 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 92.2989 | 57.8661 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 9.4384 | 5.9174 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 150.165 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 15.3558
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2019-20 | 284.59 | 2336.36 | 953.8788 | 59.0928 | 15.3558 | 43.737 | Y | 59.0928
2020-21 | 297.96 | 2975.15 | 1061.3048 | 65.7478 | 15.3558 | 50.392 | Y | 65.7478
2021-22 | 284.9 | 3436.28 | 994.3222 | 61.5983 | 15.3558 | 46.2425 | Y | 61.5983
2022-23 | 330.27 | 4821.17 | 1236.8599 | 76.6235 | 15.3558 | 61.2677 | Y | 76.6235
[7 empty] | 4 | 741.4476 | Residual
[8 empty] | 402.5213 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 291.4742 | 794.8078 | 235.1296 | 540.6635 | 150.5314 | 402.5213 | 150.165 | 252.3563
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 601.39 | 8933.25 | 7328.5942 | 454006.4082
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 662.25 | 9318.88 | 7558.4942 | 468248.7132
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 697.21 | 9475.84 | 7580.813 | 469631.3629
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 798.57 | 9833.03 | 7702.0102 | 477139.5344
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 923.07 | 10647.55 | 8135.9714 | 504023.4258
2019-20 | 169.53 | 1254.51 | 861.3396 | Y | 53359.9882 |  | 2019-20 | 1046.82 | 11854.72 | 8609.1119 | 533334.4834
2020-21 | 181.33 | 1402.16 | 961.2022 | Y | 59546.4788 |  | 2020-21 | 1090.88 | 13070.25 | 9043.6186 | 560252.1698
2021-22 | 279.01 | 1230.41 | 778.1005 | Y | 48203.3247 |  | 2021-22 | 1029.92 | 14370.86 | 9487.2786 | 587736.9068
2022-23 | 193.06 | 1304.56 | 846.5433 | Y | 52443.3562 |  | 2022-23 | 1240.22 | 16758.96 | 10450.3673 | 647400.253
|  |  |  | 4 | 507468.564 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 607.22 | 8942.04 | 7327.1738 | 453918.4194
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 675.47 | 9339.9 | 7561.4878 | 468434.1667
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 773.64 | 9690.59 | 7758.2434 | 480623.1811
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 1102.89 | 10425.98 | 8093.9276 | 501418.8148
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 1118.79 | 10939.75 | 8424.1694 | 521877.2919
2019-20 | 66.33 | 2336.36 | 1505.0089 | Y | 93235.3001 |  | 2019-20 | 1337.43 | 12341.61 | 8889.5683 | 550708.7574
2020-21 | 158.6 | 2975.15 | 1767.6596 | Y | 109506.5122 |  | 2020-21 | 1282.91 | 13542.23 | 9348.3985 | 579133.2858
2021-22 | 108.25 | 3436.28 | 1882.2999 | Y | 116608.48 |  | 2021-22 | 1557.65 | 15728.95 | 10431.9028 | 646256.3785
2022-23 | 215.3 | 4821.17 | 2534.977 | Y | 157041.8276 |  | 2022-23 | 1734.53 | 18335.87 | 11457.3507 | 709782.8771
|  |  |  | 4 | 1519616.526 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8619.28 | 7213.3043 | 446864.2026
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8755.49 | 7261.9854 | 449879.9931
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 563.01 | 8863.23 | 7331.3549 | 454177.4348
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 576.21 | 8922.18 | 7333.5182 | 454311.455
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 661.15 | 9157.33 | 7439.8178 | 460896.7102
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 741.15 | 9524.17 | 7653.0018 | 474103.464
2019-20 | 284.59 | 1140.71 | 715.4888 | Y | 44324.5312 |  | 2019-20 | 782.97 | 9904.03 | 7815.4454 | 484166.8401
2020-21 | 270.55 | 1157.25 | 725.1384 | Y | 44922.3239 |  | 2020-21 | 828.57 | 10377.36 | 8039.0088 | 498016.5952
2021-22 | 284.9 | 946.71 | 594.2347 | Y | 36812.8409 |  | 2021-22 | 758.18 | 10544.13 | 7972.7162 | 493909.7711
2022-23 | 299.37 | 1116.65 | 689.4661 | Y | 42712.4237 |  | 2022-23 | 784.75 | 11385.88 | 8248.7226 | 511008.3675
|  |  |  | 4 | 413307.1159 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8619.28 | 7213.3043 | 446864.2026
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8755.12 | 7264.3158 | 450024.3663
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.59 | 8861.67 | 7328.3542 | 453991.5402
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 619.2 | 9069.53 | 7469.8436 | 462756.811
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 927.68 | 9615.95 | 7713.3574 | 477842.4934
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 981.26 | 10006.35 | 7969.5895 | 493716.0708
2019-20 | 142.41 | 1842.34 | 1155.1374 | Y | 71560.7644 |  | 2019-20 | 982.24 | 10256.2 | 8065.5887 | 499663.2212
2020-21 | 297.96 | 2051.5 | 1258.3314 | Y | 77953.6327 |  | 2020-21 | 1005.02 | 10670.57 | 8233.9923 | 510095.8242
2021-22 | 229.51 | 2190.03 | 1348.5869 | Y | 83544.9572 |  | 2021-22 | 980.96 | 11127.6 | 8447.3875 | 523315.6569
2022-23 | 330.27 | 2787.23 | 1694.6701 | Y | 104984.8115 |  | 2022-23 | 1073.45 | 12153.08 | 8808.0414 | 545658.1623
|  |  |  | 4 | 1015886.3844 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7322.7668 | 453645.4033
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.74 | 8884.88 | 7313.8897 | 453095.4657
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 645.53 | 9262.5 | 7541.3546 | 467186.9199
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 693.25 | 9457.87 | 7582.9713 | 469765.0708
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 775.63 | 9760.92 | 7655.6801 | 474269.381
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 874.64 | 10430.06 | 7974.8922 | 494044.5693
2019-20 | 142.12 | 715.3 | 532.419 | Y | 32983.3595 |  | 2019-20 | 930.76 | 11565.88 | 8470.246 | 524731.7397
2020-21 | 147.17 | 811.01 | 594.1921 | Y | 36810.1994 |  | 2020-21 | 971.26 | 12839.27 | 8923.2608 | 552796.0066
2021-22 | 96.35 | 515.76 | 368.389 | Y | 22821.6961 |  | 2021-22 | 975.34 | 14322.46 | 9393.2279 | 581910.4696
2022-23 | 105.14 | 634.57 | 418.643 | Y | 25934.9314 |  | 2022-23 | 1077.58 | 16575.32 | 10279.3945 | 636808.488
|  |  |  | 4 | 250959.575 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | N | 0 | 0
2018-19 | N | 0 | 0
2019-20 | Y | 70.9113 | 47.2742
2020-21 | Y | 78.8974 | 52.5983
2021-22 | Y | 73.9179 | 49.2786
2022-23 | Y | 91.9482 | 61.2988
| 4 | 889.7372 | 593.1581 | Residual
|  | 483.0255 | 322.017 | NPV

## Option1b
Option 1b:
Stage 1: Install wind monitoring facility onh the Ballarat-Bendigo 220 kV line in 2015-16
Stage 2: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 82 degC in 2019-20
Stage 3: Up-rate the existing Moorabool-Ballarat 220 kV line to maximum operating temperature of 82 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 0.6 | 77.2 | 48.4 |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% | 2% |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 0.11735 | 15.0989 | 9.4661 |  | Scenario 1 | 20%
Project Cost ($M) | 0.71735 | 92.2989 | 57.8661 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 0.073356 | 9.4384 | 5.9174 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 150.8823 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 15.4291
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 43.5 | 235.41 | 107.9529 | 6.6877 | 0.073356 | 6.6143 | Y1 | 6.6877
2016-17 | 40.4 | 276.59 | 156.9977 | 9.726 | 0.073356 | 9.6526 | Y1 | 9.726
2017-18 | 47.24 | 268.99 | 182.7203 | 11.3195 | 0.073356 | 11.2462 | Y1 | 11.3195
2018-19 | 40.64 | 289.89 | 236.6927 | 14.6631 | 0.073356 | 14.5898 | Y1 | 14.6631
2019-20 | 284.59 | 2335.76 | 951.6553 | 58.955 | 15.4291 | 43.5259 | Y | 58.955
2020-21 | 297.95 | 2982.33 | 1061.8469 | 65.7814 | 15.4291 | 50.3523 | Y | 65.7814
2021-22 | 284.93 | 3436.2 | 993.6199 | 61.5548 | 15.4291 | 46.1256 | Y | 61.5548
2022-23 | 330.27 | 4820.79 | 1236.9856 | 76.6313 | 15.4291 | 61.2021 | Y | 76.6313
[7 empty] | 8 | 730.0182 | Residual
[8 empty] | 425.0173 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 314.5681 | 809.5856 | 255.9541 | 556.7246 | 188.2542 | 425.0173 | 150.8823 | 274.135
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 596.9 | 8928.76 | 7327.2292 | 453921.8489
2015-16 | 41.49 | 156.85 | 121.9874 | Y1 | 7557.117 |  | 2015-16 | 662.25 | 9318.88 | 7557.8121 | 468206.4584
2016-17 | 30.36 | 140.79 | 147.1375 | Y1 | 9115.1694 |  | 2016-17 | 700.99 | 9468.14 | 7578.4652 | 469485.9191
2017-18 | 30.53 | 154.73 | 160.9174 | Y1 | 9968.8354 |  | 2017-18 | 798.57 | 9831.61 | 7703.6109 | 477238.694
2018-19 | 15.64 | 210.29 | 215.8928 | Y1 | 13374.559 |  | 2018-19 | 923.07 | 10646.73 | 8135.7221 | 504007.9829
2019-20 | 169.53 | 1256.12 | 859.4835 | Y | 53245.0041 |  | 2019-20 | 1046.82 | 11853.11 | 8610.968 | 533449.4676
2020-21 | 181.33 | 1402.94 | 961.4254 | Y | 59560.306 |  | 2020-21 | 1090.88 | 13069.47 | 9043.3954 | 560238.3426
2021-22 | 279.01 | 1230.38 | 778.0983 | Y | 48203.1909 |  | 2021-22 | 1029.92 | 14370.89 | 9487.2807 | 587737.0406
2022-23 | 194.12 | 1305.5 | 848.6874 | Y | 52576.182 |  | 2022-23 | 1239.16 | 16758.02 | 10448.2232 | 647267.4272
|  |  |  | 8 | 500860.4565 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 607.22 | 8942.04 | 7330.807 | 454143.4912
2015-16 | 13.66 | 78.68 | 57.6051 | Y1 | 3568.6372 |  | 2015-16 | 677.85 | 9342.28 | 7562.1834 | 468477.2641
2016-17 | 40.24 | 227.07 | 143.7031 | Y1 | 8902.4083 |  | 2016-17 | 776.49 | 9687.23 | 7757.222 | 480559.9029
2017-18 | -33.46 | 247.68 | 142.7371 | Y1 | 8842.5646 |  | 2017-18 | 1101.73 | 10427.11 | 8092.2597 | 501315.4872
2018-19 | 21.54 | 272.99 | 271.2013 | Y1 | 16800.9193 |  | 2018-19 | 1118.44 | 10939.3 | 8426.9558 | 522049.9093
2019-20 | 65.91 | 2335.76 | 1506.4899 | Y | 93327.0505 |  | 2019-20 | 1337.85 | 12342.21 | 8888.0873 | 550617.007
2020-21 | 158.41 | 2982.33 | 1771.805 | Y | 109763.3222 |  | 2020-21 | 1283.1 | 13535.05 | 9344.253 | 578876.4758
2021-22 | 108.26 | 3436.2 | 1882.0738 | Y | 116594.4694 |  | 2021-22 | 1557.64 | 15729.03 | 10432.129 | 646270.3891
2022-23 | 215.3 | 4820.79 | 2534.8615 | Y | 157034.6712 |  | 2022-23 | 1734.53 | 18336.25 | 11457.4662 | 709790.0336
|  |  |  | 8 | 1495971.2586 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8619.28 | 7213.3043 | 446864.2026
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8755.49 | 7264.9016 | 450060.6541
2015-16 | 43.5 | 143.6 | 96.5295 | Y1 | 5980.0038 |  | 2015-16 | 563.01 | 8863.23 | 7330.2204 | 454107.1538
2016-17 | 40.4 | 144.59 | 134.5954 | Y1 | 8338.1875 |  | 2016-17 | 576.21 | 8922.18 | 7336.1074 | 454471.851
2017-18 | 23.54 | 195.66 | 166.0452 | Y1 | 10286.5001 |  | 2017-18 | 661.15 | 9153.34 | 7438.0202 | 460785.3489
2018-19 | 9.74 | 236.36 | 205.6873 | Y1 | 12742.327 |  | 2018-19 | 741.15 | 9524.05 | 7653.5013 | 474134.4043
2019-20 | 284.59 | 1133.12 | 708.7062 | Y | 43904.3466 |  | 2019-20 | 782.97 | 9911.62 | 7822.228 | 484587.0246
2020-21 | 270.54 | 1153.05 | 720.9593 | Y | 44663.4274 |  | 2020-21 | 828.58 | 10381.56 | 8043.1879 | 498275.4916
2021-22 | 284.93 | 938.99 | 588.9368 | Y | 36484.6348 |  | 2021-22 | 758.15 | 10551.85 | 7978.0142 | 494237.9772
2022-23 | 299.37 | 1116.71 | 689.4843 | Y | 42713.5536 |  | 2022-23 | 784.75 | 11385.82 | 8248.7044 | 511007.2376
|  |  |  | 8 | 406905.3547 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8619.28 | 7213.3043 | 446864.2026
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8755.12 | 7264.3158 | 450024.3663
2015-16 | 16.96 | 71.28 | 42.0689 | Y1 | 2606.1671 |  | 2015-16 | 566.59 | 8865.86 | 7329.6279 | 454070.4496
2016-17 | 39.96 | 200.28 | 129.8518 | Y1 | 8044.3165 |  | 2016-17 | 619.2 | 9069.49 | 7469.8314 | 462756.0577
2017-18 | -2.29 | 242.73 | 162.3142 | Y1 | 10055.3622 |  | 2017-18 | 927.68 | 9615.95 | 7713.3296 | 477840.7687
2018-19 | -25.43 | 245.03 | 241.1394 | Y1 | 14938.5834 |  | 2018-19 | 981.3 | 10010.86 | 7970.9884 | 493802.7314
2019-20 | 142.41 | 1842.34 | 1155.1374 | Y | 71560.7644 |  | 2019-20 | 982.24 | 10256.2 | 8065.5887 | 499663.2212
2020-21 | 297.95 | 2051.49 | 1261.2446 | Y | 78134.1054 |  | 2020-21 | 1005.03 | 10670.58 | 8231.0791 | 509915.3515
2021-22 | 229.54 | 2189.83 | 1348.9367 | Y | 83566.6298 |  | 2021-22 | 980.93 | 11127.8 | 8447.0377 | 523293.9843
2022-23 | 330.27 | 2787.23 | 1694.336 | Y | 104964.1152 |  | 2022-23 | 1073.45 | 12153.08 | 8808.3754 | 545678.8585
|  |  |  | 8 | 999927.5851 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 581.27 | 8883.41 | 7313.4428 | 453067.7815
2015-16 | 4.14 | 235.41 | 221.5735 | Y1 | 13726.4796 |  | 2015-16 | 641.08 | 9262.04 | 7540.5327 | 467136.002
2016-17 | 32.92 | 276.59 | 229.7005 | Y1 | 14229.9447 |  | 2016-17 | 689.35 | 9453.12 | 7582.787 | 469753.6571
2017-18 | 47.24 | 268.99 | 281.5876 | Y1 | 17444.3518 |  | 2017-18 | 775.72 | 9762.83 | 7655.9127 | 474283.793
2018-19 | 40.64 | 289.89 | 249.5429 | Y1 | 15459.1814 |  | 2018-19 | 874.64 | 10426.39 | 7973.4981 | 493958.2061
2019-20 | 139.94 | 709.51 | 528.4595 | Y | 32738.0673 |  | 2019-20 | 932.94 | 11571.67 | 8474.2055 | 524977.032
2020-21 | 143.18 | 809.79 | 593.8003 | Y | 36785.9298 |  | 2020-21 | 975.25 | 12840.49 | 8923.6526 | 552820.2761
2021-22 | 99.23 | 518.97 | 370.0538 | Y | 22924.8354 |  | 2021-22 | 972.46 | 14319.25 | 9391.563 | 581807.3303
2022-23 | 106.2 | 635.4 | 417.559 | Y | 25867.7776 |  | 2022-23 | 1076.52 | 16574.49 | 10280.4785 | 636875.6418
|  |  |  | 8 | 246426.1649 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | Y1 | 8.0252 | 5.3501
2016-17 | Y1 | 11.6712 | 7.7808
2017-18 | Y1 | 13.5834 | 9.0556
2018-19 | Y1 | 17.5957 | 11.7305
2019-20 | Y | 70.7461 | 47.164
2020-21 | Y | 78.9377 | 52.6251
2021-22 | Y | 73.8657 | 49.2438
2022-23 | Y | 91.9575 | 61.305
| 8 | 876.0218 | 584.0145 | Residual
|  | 510.0208 | 340.0138 | NPV

## Option2
Option 2:
Stage 1: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 82 degC in 2019-20
Stage 2: Up-rate the existing Moorabool-Ballarat 220 kV line to maximum operating temperature of 90 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 77.2 | 50.4 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 15.0989 | 9.8573 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 92.2989 | 60.2573 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 9.4384 | 6.1619 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 152.5561 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 15.6003
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2019-20 | 284.59 | 2365.72 | 951.4678 | 58.9434 | 15.6003 | 43.3431 | Y | 58.9434
2020-21 | 298.16 | 2975.69 | 1061.5756 | 65.7646 | 15.6003 | 50.1643 | Y | 65.7646
2021-22 | 285.04 | 3452.33 | 996.242 | 61.7172 | 15.6003 | 46.1169 | Y | 61.7172
2022-23 | 330.27 | 4820.56 | 1239.6487 | 76.7962 | 15.6003 | 61.1959 | Y | 76.7962
[7 empty] | 4 | 743.1194 | Residual
[8 empty] | 403.2141 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 293.2074 | 796.6544 | 235.4665 | 540.6875 | 150.0545 | 403.2141 | 152.5561 | 250.6579
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 547.82 | 8766.4 | 7323.4667 | 453688.7633
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 596.24 | 8925.93 | 7326.3689 | 453868.5521
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 662.25 | 9319.53 | 7558.6918 | 468260.9545
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 700.95 | 9479.06 | 7584.7359 | 469874.3902
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 798.57 | 9834.82 | 7703.668 | 477242.2326
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 923.01 | 10646.94 | 8136.2731 | 504042.1198
2019-20 | 169.53 | 1247.47 | 858.0162 | Y | 53154.1061 |  | 2019-20 | 1046.82 | 11861.76 | 8612.4353 | 533540.3656
2020-21 | 181.21 | 1403.4 | 961.5862 | Y | 59570.2626 |  | 2020-21 | 1091 | 13069.01 | 9043.2346 | 560228.3859
2021-22 | 285.04 | 1246.86 | 783.6233 | Y | 48545.4622 |  | 2021-22 | 1023.89 | 14354.41 | 9481.7558 | 587394.7693
2022-23 | 204.83 | 1324 | 853.1421 | Y | 52852.1519 |  | 2022-23 | 1228.45 | 16739.52 | 10443.7685 | 646991.4573
|  |  |  | 4 | 511424.2785 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 601.99 | 8933.68 | 7328.2655 | 453986.049
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 666.47 | 9322.52 | 7559.1274 | 468287.9449
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 748.62 | 9655.11 | 7744.3882 | 479764.8465
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 1061 | 10365.45 | 8074.573 | 500219.7949
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 1103.45 | 10925.45 | 8423.0864 | 521810.2025
2019-20 | 78.16 | 2365.72 | 1504.5801 | Y | 93208.736 |  | 2019-20 | 1325.6 | 12312.25 | 8889.9971 | 550735.3216
2020-21 | 158.6 | 2975.69 | 1771.9998 | Y | 109775.3851 |  | 2020-21 | 1282.91 | 13541.69 | 9344.0583 | 578864.4129
2021-22 | 120.01 | 3452.33 | 1888.3206 | Y | 116981.4587 |  | 2021-22 | 1545.89 | 15712.9 | 10425.8822 | 645883.3998
2022-23 | 215.3 | 4820.56 | 2541.16 | Y | 157424.862 |  | 2022-23 | 1734.53 | 18336.48 | 11451.1678 | 709399.8427
|  |  |  | 4 | 1523322.9612 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8619.28 | 7213.3043 | 446864.2026
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8755.49 | 7261.9854 | 449879.9931
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 563.01 | 8863.23 | 7330.2204 | 454107.1538
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 576.21 | 8913.79 | 7333.5498 | 454313.4126
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 661.15 | 9153.12 | 7437.9533 | 460781.2057
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 741.15 | 9524.01 | 7652.9532 | 474100.4507
2019-20 | 284.59 | 1133.12 | 708.7062 | Y | 43904.3466 |  | 2019-20 | 782.97 | 9911.62 | 7822.228 | 484587.0246
2020-21 | 270.66 | 1153.08 | 723.8846 | Y | 44844.6534 |  | 2020-21 | 828.46 | 10381.53 | 8040.2626 | 498094.2656
2021-22 | 284.9 | 946.71 | 591.2698 | Y | 36629.1616 |  | 2021-22 | 758.18 | 10544.13 | 7975.6812 | 494093.4503
2022-23 | 299.37 | 1123.67 | 692.0804 | Y | 42874.3808 |  | 2022-23 | 784.75 | 11378.86 | 8246.1083 | 510846.4104
|  |  |  | 4 | 414874.2953 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8619.28 | 7213.3043 | 446864.2026
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 543.05 | 8751.28 | 7263.1485 | 449952.0483
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 562.4 | 8861.67 | 7329.9202 | 454088.5539
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 618.07 | 9072.32 | 7472.4457 | 462918.0099
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 922.7 | 9610.97 | 7713.507 | 477851.7562
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 981.3 | 10010.86 | 7970.9606 | 493801.0067
2019-20 | 143.26 | 1843.13 | 1155.3776 | Y | 71575.6423 |  | 2019-20 | 981.39 | 10255.41 | 8065.3486 | 499648.3433
2020-21 | 298.16 | 2051.85 | 1258.4378 | Y | 77960.2242 |  | 2020-21 | 1004.82 | 10670.22 | 8233.8859 | 510089.2327
2021-22 | 229.52 | 2190.15 | 1349.034 | Y | 83572.6563 |  | 2021-22 | 980.95 | 11127.48 | 8446.9404 | 523287.9578
2022-23 | 330.27 | 2787.25 | 1694.6762 | Y | 104985.1881 |  | 2022-23 | 1073.45 | 12153.06 | 8808.0353 | 545657.7856
|  |  |  | 4 | 1015890.0291 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.93 | 8766.41 | 7323.4698 | 453688.9516
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.74 | 8884.88 | 7311.1822 | 452927.7398
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 642.93 | 9264.24 | 7541.8836 | 467219.689
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 693.13 | 9445.49 | 7579.2008 | 469531.4896
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 775.63 | 9762.39 | 7655.765 | 474274.6442
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 874.64 | 10424.09 | 7972.7989 | 493914.8906
2019-20 | 139.94 | 709.51 | 530.6589 | Y | 32874.3176 |  | 2019-20 | 932.94 | 11571.67 | 8472.0062 | 524840.7816
2020-21 | 147.17 | 810.98 | 591.9697 | Y | 36672.5217 |  | 2020-21 | 971.26 | 12839.3 | 8925.4832 | 552933.6842
2021-22 | 96.35 | 515.38 | 368.9625 | Y | 22857.2256 |  | 2021-22 | 975.34 | 14322.84 | 9392.6544 | 581874.9401
2022-23 | 105.14 | 634.17 | 417.185 | Y | 25844.6132 |  | 2022-23 | 1077.58 | 16575.72 | 10280.8524 | 636898.8062
|  |  |  | 4 | 250085.6107 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | N | 0 | 0
2018-19 | N | 0 | 0
2019-20 | Y | 70.7321 | 47.1547
2020-21 | Y | 78.9175 | 52.6117
2021-22 | Y | 74.0606 | 49.3738
2022-23 | Y | 92.1555 | 61.437
| 4 | 891.7433 | 594.4955 | Residual
|  | 483.8569 | 322.5713 | NPV

## Option3a
Option 3a:
Stage 1: Install a third Moorabool-Ballarat 220 kV line in 2017-18
Stage 2: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 82 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 27.8 | 77.2 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 5.4372 | 15.0989 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 33.2372 | 92.2989 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 3.3988 | 9.4384 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 125.536 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 12.8372
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 294.98 | 1065.14 | 448.6556 | 27.7942 | 3.3988 | 24.3954 | Y1 | 27.7942
2018-19 | 296.5 | 1239.25 | 454.6758 | 28.1672 | 3.3988 | 24.7684 | Y1 | 28.1672
2019-20 | 302.52 | 2402.13 | 955.9456 | 59.2208 | 12.8372 | 46.3836 | Y | 59.2208
2020-21 | 341.36 | 2927.77 | 1061.0754 | 65.7336 | 12.8372 | 52.8964 | Y | 65.7336
2021-22 | 308.53 | 3237.19 | 984.9248 | 61.0161 | 12.8372 | 48.1789 | Y | 61.0161
2022-23 | 321.02 | 4414.69 | 1180.5491 | 73.135 | 12.8372 | 60.2978 | Y | 73.135
[7 empty] | 6 | 702.7233 | Residual
[8 empty] | 419.2163 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 289.0961 | 795.6809 | 293.2495 | 550.8749 | 167.1798 | 419.2163 | 125.536 | 293.6803
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 597.82 | 8920.64 | 7324.19 | 453733.5705
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 664.38 | 9325.03 | 7568.1868 | 468849.1723
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 700.25 | 9467.1 | 7595.9458 | 470568.8398
2017-18 | 232.94 | 457.29 | 210.6301 | Y1 | 13048.5335 |  | 2017-18 | 800.55 | 9808.02 | 7708.8979 | 477566.2261
2018-19 | 193.81 | 212.32 | 121.9321 | Y1 | 7553.6924 |  | 2018-19 | 919.63 | 10611.72 | 8133.9113 | 503895.8038
2019-20 | 205.02 | 1310.47 | 868.1063 | Y | 53779.1865 |  | 2019-20 | 1011.33 | 11798.76 | 8602.3452 | 532915.2851
2020-21 | -33.57 | 1446.89 | 967.7984 | Y | 59955.1109 |  | 2020-21 | 1305.78 | 13025.52 | 9037.0224 | 559843.5377
2021-22 | 308.53 | 1274.02 | 788.3999 | Y | 48841.375 |  | 2021-22 | 1000.4 | 14327.25 | 9476.9791 | 587098.8565
2022-23 | 143.9 | 1126.48 | 791.1054 | Y | 49008.982 |  | 2022-23 | 1289.38 | 16937.04 | 10505.8051 | 650834.6272
|  |  |  | 6 | 470906.4729 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 599.05 | 8923.51 | 7325.0625 | 453787.6206
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 667.14 | 9327.79 | 7564.4392 | 468617.0084
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 742.38 | 9645.24 | 7762.5252 | 480888.4361
2017-18 | 54.61 | 1065.14 | 522.5732 | Y1 | 32373.4097 |  | 2017-18 | 1050.32 | 10328.43 | 8078.0532 | 500435.3957
2018-19 | 233.08 | 1239.25 | 526.887 | Y1 | 32640.6521 |  | 2018-19 | 1082.5 | 10863.79 | 8414.6495 | 521287.5378
2019-20 | 112.01 | 2402.13 | 1518.3074 | Y | 94059.1459 |  | 2019-20 | 1291.75 | 12275.84 | 8876.2698 | 549884.9116
2020-21 | -0.77 | 2927.77 | 1750.2842 | Y | 108430.1037 |  | 2020-21 | 1442.28 | 13589.61 | 9365.7739 | 580209.6943
2021-22 | -95.98 | 3237.19 | 1837.2347 | Y | 113816.6909 |  | 2021-22 | 1761.88 | 15928.04 | 10476.968 | 649048.1676
2022-23 | 52.26 | 4414.69 | 2407.593 | Y | 149150.3888 |  | 2022-23 | 1897.57 | 18742.35 | 11584.7347 | 717674.3159
|  |  |  | 6 | 1433122.6779 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8755.13 | 7262.8155 | 449931.4215
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.91 | 8864.56 | 7329.6573 | 454072.2685
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 573.49 | 8918.24 | 7344.9668 | 455020.6933
2017-18 | 294.98 | 970.65 | 701.2423 | Y1 | 43441.9617 |  | 2017-18 | 650 | 9142.68 | 7449.8131 | 461515.9228
2018-19 | 296.5 | 1025.25 | 782.861 | Y1 | 48498.2414 |  | 2018-19 | 728 | 9502.66 | 7665.9647 | 474906.5144
2019-20 | 302.52 | 1165.43 | 705.193 | Y | 43686.7088 |  | 2019-20 | 765.04 | 9879.31 | 7825.7411 | 484804.6624
2020-21 | 253.82 | 1175.97 | 720.1666 | Y | 44614.3184 |  | 2020-21 | 845.3 | 10358.64 | 8043.9806 | 498324.6006
2021-22 | 306.15 | 981.06 | 600.355 | Y | 37191.9898 |  | 2021-22 | 736.93 | 10509.78 | 7966.596 | 493530.6222
2022-23 | 321.02 | 1182.54 | 709.9838 | Y | 43983.4989 |  | 2022-23 | 763.1 | 11319.99 | 8228.2049 | 509737.2923
|  |  |  | 6 | 422618.7421 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8754.81 | 7262.3076 | 449899.9558
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.91 | 8864.08 | 7329.5114 | 454063.2288
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 609.04 | 9050.4 | 7473.09 | 462957.9255
2017-18 | 52.06 | 802.76 | 433.5111 | Y1 | 26856.0139 |  | 2017-18 | 911.06 | 9576.46 | 7711.5698 | 477731.7466
2018-19 | 164.8 | 776.59 | 361.4817 | Y1 | 22393.7901 |  | 2018-19 | 995.01 | 10000.05 | 7982.5896 | 494521.4257
2019-20 | 164.12 | 1889.4 | 1159.0524 | Y | 71803.2962 |  | 2019-20 | 960.53 | 10209.14 | 8061.6738 | 499420.6894
2020-21 | 341.36 | 2100.31 | 1263.3213 | Y | 78262.7533 |  | 2020-21 | 961.62 | 10621.76 | 8229.0025 | 509786.7036
2021-22 | 131.94 | 2103.07 | 1314.1401 | Y | 81410.978 |  | 2021-22 | 1078.53 | 11214.56 | 8481.8343 | 525449.6361
2022-23 | 145.9 | 2593.19 | 1632.6334 | Y | 101141.6416 |  | 2022-23 | 1257.82 | 12347.12 | 8870.078 | 549501.3321
|  |  |  | 6 | 971827.0359 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.72 | 8882.12 | 7312.4799 | 453008.131
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 641.23 | 9260.91 | 7545.7433 | 467458.7962
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 688.37 | 9457.14 | 7596.8712 | 470626.1708
2017-18 | 77.94 | 345.63 | 375.3214 | Y1 | 23251.1583 |  | 2017-18 | 768.38 | 9727.56 | 7663.3145 | 474742.332
2018-19 | 128.41 | 490.65 | 480.217 | Y1 | 29749.4407 |  | 2018-19 | 864.18 | 10402.29 | 7976.4864 | 494143.3325
2019-20 | 175.66 | 785.51 | 529.0688 | Y | 32775.8122 |  | 2019-20 | 897.22 | 11495.67 | 8473.5962 | 524939.2871
2020-21 | 181.25 | 891.54 | 603.8066 | Y | 37405.8213 |  | 2020-21 | 937.18 | 12758.74 | 8913.6462 | 552200.3846
2021-22 | 105.87 | 581.17 | 384.4943 | Y | 23819.4231 |  | 2021-22 | 965.82 | 14257.05 | 9377.1226 | 580912.7426
2022-23 | 110.45 | 480.23 | 361.4298 | Y | 22390.5736 |  | 2022-23 | 1072.27 | 16729.66 | 10336.6077 | 640352.8458
|  |  |  | 6 | 215141.5031 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | Y1 | 33.3531 | 22.2354
2018-19 | Y1 | 33.8006 | 22.5337
2019-20 | Y | 71.065 | 47.3767
2020-21 | Y | 78.8803 | 52.5869
2021-22 | Y | 73.2193 | 48.8129
2022-23 | Y | 87.762 | 58.508
| 6 | 843.2679 | 562.1786 | Residual
|  | 503.0595 | 335.373 | NPV

## Option3b
Option 3b:
Stage 1: Install wind monitoring facility on Ballarat-Bendigo 220 kV line in 2015-16
Stage 2: Install a third Moorabool-Ballarat 220 kV line in 2017-18
Stage 3: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 82 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 0.6 | 27.8 | 77.2 |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% | 2% |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 0.11735 | 5.4372 | 15.0989 |  | Scenario 1 | 20%
Project Cost ($M) | 0.71735 | 33.2372 | 92.2989 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 0.073356 | 3.3988 | 9.4384 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 126.2534 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 12.9106
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 43.5 | 235.41 | 107.9529 | 6.6877 | 0.073356 | 6.6143 | Y1 | 6.6877
2016-17 | 40.4 | 276.59 | 156.9977 | 9.726 | 0.073356 | 9.6526 | Y1 | 9.726
2017-18 | 318.52 | 1312.82 | 631.3759 | 39.1137 | 3.4722 | 35.6416 | Y2 | 39.1137
2018-19 | 306.24 | 1512.24 | 691.3685 | 42.8303 | 3.4722 | 39.3581 | Y2 | 42.8303
2019-20 | 302.52 | 2402.16 | 954.9436 | 59.1588 | 12.9106 | 46.2482 | Y | 59.1588
2020-21 | 341.38 | 2927.33 | 1059.4221 | 65.6312 | 12.9106 | 52.7206 | Y | 65.6312
2021-22 | 306.24 | 3242.85 | 984.8583 | 61.012 | 12.9106 | 48.1014 | Y | 61.012
2022-23 | 321.02 | 4411.14 | 1179.8886 | 73.0941 | 12.9106 | 60.1835 | Y | 73.0941
[7 empty] | 8 | 696.3218 | Residual
[8 empty] | 443.6241 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 312.1024 | 814.2995 | 314.5291 | 570.9799 | 206.2095 | 443.6241 | 126.2534 | 317.3707
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.59 | 8763.48 | 7320.4771 | 453503.5576
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 597.82 | 8920.63 | 7324.187 | 453733.3822
2015-16 | 41.49 | 156.85 | 121.9874 | Y1 | 7557.117 |  | 2015-16 | 664.38 | 9325.03 | 7568.1868 | 468849.1723
2016-17 | 30.36 | 140.79 | 147.1375 | Y1 | 9115.1694 |  | 2016-17 | 700.25 | 9479 | 7596.6123 | 470610.1332
2017-18 | 263.47 | 612.02 | 371.5475 | Y2 | 23017.3689 |  | 2017-18 | 797.07 | 9809.81 | 7711.8154 | 477746.9665
2018-19 | 209.45 | 422.61 | 337.8249 | Y2 | 20928.2513 |  | 2018-19 | 919.63 | 10611.72 | 8133.3475 | 503860.8789
2019-20 | 205.02 | 1310.42 | 865.1958 | Y | 53598.8773 |  | 2019-20 | 1011.33 | 11798.81 | 8605.2558 | 533095.5943
2020-21 | -33.61 | 1444.07 | 965.1246 | Y | 59789.4665 |  | 2020-21 | 1305.82 | 13028.34 | 9039.6962 | 560009.1821
2021-22 | 306.24 | 1273 | 787.9367 | Y | 48812.6798 |  | 2021-22 | 1002.69 | 14328.27 | 9477.4423 | 587127.5517
2022-23 | 141.88 | 1127.55 | 787.5192 | Y | 48786.8144 |  | 2022-23 | 1291.4 | 16935.97 | 10509.3914 | 651056.7948
|  |  |  | 8 | 464761.5183 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.59 | 8763.48 | 7320.4771 | 453503.5576
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 599.06 | 8923.95 | 7322.8577 | 453651.0333
2015-16 | 13.66 | 78.68 | 57.6051 | Y1 | 3568.6372 |  | 2015-16 | 671.37 | 9330.36 | 7568.1994 | 468849.9504
2016-17 | 40.24 | 227.07 | 143.7031 | Y1 | 8902.4083 |  | 2016-17 | 742.68 | 9636.18 | 7758.3511 | 480629.8519
2017-18 | 21.15 | 1312.82 | 665.3103 | Y2 | 41215.9743 |  | 2017-18 | 1050.32 | 10328.71 | 8076.106 | 500314.7667
2018-19 | 254.62 | 1512.24 | 798.0883 | Y2 | 49441.5714 |  | 2018-19 | 1082.54 | 10863.83 | 8414.6617 | 521288.2911
2019-20 | 112.01 | 2402.16 | 1515.3725 | Y | 93877.3251 |  | 2019-20 | 1291.75 | 12275.81 | 8879.2047 | 550066.7324
2020-21 | -0.74 | 2927.33 | 1748.0206 | Y | 108289.8786 |  | 2020-21 | 1442.25 | 13590.05 | 9368.0374 | 580349.9194
2021-22 | -95.81 | 3242.85 | 1838.7396 | Y | 113909.9182 |  | 2021-22 | 1761.71 | 15922.38 | 10475.4631 | 648954.9403
2022-23 | 52.45 | 4411.14 | 2406.5138 | Y | 149083.5324 |  | 2022-23 | 1897.38 | 18745.9 | 11585.8139 | 717741.1723
|  |  |  | 8 | 1420225.7242 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8755.13 | 7262.8642 | 449934.4397
2015-16 | 43.5 | 143.6 | 96.5295 | Y1 | 5980.0038 |  | 2015-16 | 566.91 | 8864.56 | 7329.6573 | 454072.2685
2016-17 | 40.4 | 144.59 | 134.5954 | Y1 | 8338.1875 |  | 2016-17 | 573.49 | 8918.24 | 7343.1711 | 454909.4509
2017-18 | 318.52 | 1166.31 | 867.2875 | Y2 | 53728.4619 |  | 2017-18 | 650 | 9142.68 | 7446.8621 | 461333.1059
2018-19 | 306.24 | 1261.61 | 988.5483 | Y2 | 61240.5684 |  | 2018-19 | 728.7 | 9501.39 | 7665.5856 | 474883.0279
2019-20 | 302.52 | 1165.43 | 705.193 | Y | 43686.7088 |  | 2019-20 | 765.04 | 9879.31 | 7825.7411 | 484804.6624
2020-21 | 253.82 | 1175.97 | 720.1596 | Y | 44613.8872 |  | 2020-21 | 845.3 | 10358.64 | 8043.9876 | 498325.0318
2021-22 | 306.04 | 977.57 | 599.294 | Y | 37126.2633 |  | 2021-22 | 737.04 | 10513.27 | 7967.657 | 493596.3487
2022-23 | 321.02 | 1175.55 | 705.743 | Y | 43720.7813 |  | 2022-23 | 763.1 | 11326.98 | 8232.4457 | 510000.0099
|  |  |  | 8 | 416500.5841 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8750.58 | 7261.0217 | 449820.2931
2015-16 | 16.96 | 71.28 | 42.0689 | Y1 | 2606.1671 |  | 2015-16 | 566.91 | 8864.05 | 7329.5022 | 454062.6638
2016-17 | 39.96 | 200.28 | 129.8518 | Y1 | 8044.3165 |  | 2016-17 | 609.04 | 9050.4 | 7475.526 | 463108.8357
2017-18 | 49.77 | 1045.49 | 595.8253 | Y2 | 36911.3761 |  | 2017-18 | 911.06 | 9572.23 | 7713.1305 | 477828.4332
2018-19 | 139.37 | 1021.62 | 602.621 | Y2 | 37332.3734 |  | 2018-19 | 995.01 | 10001.91 | 7983.155 | 494556.4547
2019-20 | 164.12 | 1889.4 | 1161.4536 | Y | 71952.0505 |  | 2019-20 | 960.53 | 10209.14 | 8059.2726 | 499271.9351
2020-21 | 341.38 | 2100.3 | 1262.5805 | Y | 78216.8607 |  | 2020-21 | 961.6 | 10621.77 | 8229.7433 | 509832.5962
2021-22 | 131.96 | 2103.08 | 1314.1431 | Y | 81411.1663 |  | 2021-22 | 1078.51 | 11214.55 | 8481.8313 | 525449.4478
2022-23 | 145.41 | 2598.25 | 1637.1158 | Y | 101419.3213 |  | 2022-23 | 1258.31 | 12342.06 | 8865.5957 | 549223.6524
|  |  |  | 8 | 966158.5474 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.72 | 8882.12 | 7312.4799 | 453008.131
2015-16 | 4.14 | 235.41 | 221.5735 | Y1 | 13726.4796 |  | 2015-16 | 645.58 | 9265.52 | 7550.0958 | 467728.4323
2016-17 | 32.92 | 276.59 | 229.7005 | Y1 | 14229.9447 |  | 2016-17 | 692.4 | 9449.52 | 7594.3181 | 470468.0051
2017-18 | 125.18 | 614.62 | 656.909 | Y2 | 40695.5101 |  | 2017-18 | 764.91 | 9729.43 | 7664.8434 | 474837.0511
2018-19 | 169.05 | 780.54 | 729.7598 | Y2 | 45208.6221 |  | 2018-19 | 864.18 | 10402.05 | 7976.4134 | 494138.8126
2019-20 | 175.66 | 780.36 | 527.5032 | Y | 32678.8232 |  | 2019-20 | 897.22 | 11500.82 | 8475.1618 | 525036.276
2020-21 | 181.25 | 891.52 | 601.2254 | Y | 37245.9111 |  | 2020-21 | 937.18 | 12758.76 | 8916.2275 | 552360.2949
2021-22 | 105.35 | 580.13 | 384.1782 | Y | 23799.837 |  | 2021-22 | 966.34 | 14258.09 | 9377.4387 | 580932.3287
2022-23 | 109.04 | 480.69 | 362.551 | Y | 22460.032 |  | 2022-23 | 1073.68 | 16729.2 | 10335.4865 | 640283.3874
|  |  |  | 8 | 213962.7004 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | Y1 | 8.0252 | 5.3501
2016-17 | Y1 | 11.6712 | 7.7808
2017-18 | Y2 | 46.9365 | 31.291
2018-19 | Y2 | 51.3963 | 34.2642
2019-20 | Y | 70.9905 | 47.327
2020-21 | Y | 78.7574 | 52.505
2021-22 | Y | 73.2144 | 48.8096
2022-23 | Y | 87.7129 | 58.4753
| 8 | 835.5862 | 557.0575 | Residual
|  | 532.3489 | 354.8993 | NPV

## Option4a
Option 4a:
Stage 1: Install a third Moorabool-Ballarat 220 kV line in 2017-18
Stage 2: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 90 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 27.8 | 82.3 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 5.4372 | 16.0963 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 33.2372 | 98.3963 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 3.3988 | 10.0619 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 131.6335 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 13.4608
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 294.98 | 1065.14 | 448.6556 | 27.7942 | 3.3988 | 24.3954 | Y1 | 27.7942
2018-19 | 296.5 | 1239.25 | 454.6758 | 28.1672 | 3.3988 | 24.7684 | Y1 | 28.1672
2019-20 | 302.52 | 2406.39 | 956.2095 | 59.2372 | 13.4608 | 45.7764 | Y | 59.2372
2020-21 | 341.38 | 2919.63 | 1060.772 | 65.7148 | 13.4608 | 52.2541 | Y | 65.7148
2021-22 | 308.53 | 3237.06 | 984.459 | 60.9872 | 13.4608 | 47.5265 | Y | 60.9872
2022-23 | 321.02 | 4408.48 | 1180.6036 | 73.1384 | 13.4608 | 59.6776 | Y | 73.1384
[7 empty] | 6 | 702.7557 | Residual
[8 empty] | 419.2175 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 289.0961 | 795.1712 | 293.1917 | 551.015 | 167.6133 | 419.2175 | 131.6335 | 287.584
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 597.82 | 8920.64 | 7324.19 | 453733.5705
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 664.38 | 9325.03 | 7568.1868 | 468849.1723
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 700.25 | 9467.1 | 7595.9458 | 470568.8398
2017-18 | 232.94 | 457.29 | 210.6301 | Y1 | 13048.5335 |  | 2017-18 | 800.55 | 9808.02 | 7708.8979 | 477566.2261
2018-19 | 193.81 | 212.32 | 121.9321 | Y1 | 7553.6924 |  | 2018-19 | 919.63 | 10611.72 | 8133.9113 | 503895.8038
2019-20 | 205.02 | 1310.47 | 868.1063 | Y | 53779.1865 |  | 2019-20 | 1011.33 | 11798.76 | 8602.3452 | 532915.2851
2020-21 | -33.57 | 1446.89 | 967.7984 | Y | 59955.1109 |  | 2020-21 | 1305.78 | 13025.52 | 9037.0224 | 559843.5377
2021-22 | 308.53 | 1274.02 | 788.3999 | Y | 48841.375 |  | 2021-22 | 1000.4 | 14327.25 | 9476.9791 | 587098.8565
2022-23 | 143.9 | 1126.48 | 791.1054 | Y | 49008.982 |  | 2022-23 | 1289.38 | 16937.04 | 10505.8051 | 650834.6272
|  |  |  | 6 | 470906.4729 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 599.05 | 8923.51 | 7325.0625 | 453787.6206
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 667.14 | 9327.79 | 7564.4392 | 468617.0084
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 742.38 | 9645.24 | 7762.5252 | 480888.4361
2017-18 | 54.61 | 1065.14 | 522.5732 | Y1 | 32373.4097 |  | 2017-18 | 1050.24 | 10327.14 | 8077.661 | 500411.1014
2018-19 | 233.08 | 1239.25 | 526.887 | Y1 | 32640.6521 |  | 2018-19 | 1082.21 | 10863.48 | 8414.5553 | 521281.6996
2019-20 | 112 | 2406.39 | 1519.6025 | Y | 94139.3736 |  | 2019-20 | 1291.76 | 12271.58 | 8874.9747 | 549804.6839
2020-21 | -0.74 | 2919.63 | 1747.8096 | Y | 108276.8047 |  | 2020-21 | 1442.25 | 13597.75 | 9368.2485 | 580362.9933
2021-22 | -95.04 | 3237.06 | 1837.1952 | Y | 113814.2426 |  | 2021-22 | 1760.94 | 15928.17 | 10477.0075 | 649050.6159
2022-23 | 52.89 | 4408.48 | 2405.7052 | Y | 149033.4371 |  | 2022-23 | 1896.94 | 18748.56 | 11586.6226 | 717791.2676
|  |  |  | 6 | 1431998.9389 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8755.13 | 7262.8155 | 449931.4215
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.91 | 8864.56 | 7329.6573 | 454072.2685
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 573.49 | 8918.43 | 7345.0246 | 455024.2715
2017-18 | 294.98 | 970.65 | 701.2423 | Y1 | 43441.9617 |  | 2017-18 | 650 | 9142.68 | 7449.8131 | 461515.9228
2018-19 | 296.5 | 1025.25 | 782.861 | Y1 | 48498.2414 |  | 2018-19 | 728.45 | 9502.24 | 7665.837 | 474898.6046
2019-20 | 302.52 | 1165.43 | 705.193 | Y | 43686.7088 |  | 2019-20 | 765.04 | 9879.31 | 7825.7411 | 484804.6624
2020-21 | 253.82 | 1175.97 | 720.1666 | Y | 44614.3184 |  | 2020-21 | 845.3 | 10358.64 | 8043.9806 | 498324.6006
2021-22 | 306.04 | 974.16 | 598.2574 | Y | 37062.0435 |  | 2021-22 | 737.04 | 10516.68 | 7968.6936 | 493660.5685
2022-23 | 321.02 | 1182.55 | 709.973 | Y | 43982.8249 |  | 2022-23 | 763.1 | 11319.98 | 8228.2158 | 509737.9663
|  |  |  | 6 | 422612.2658 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8754.81 | 7262.3076 | 449899.9558
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.91 | 8864.08 | 7329.5114 | 454063.2288
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 609.04 | 9050.4 | 7473.09 | 462957.9255
2017-18 | 52.06 | 802.76 | 433.5111 | Y1 | 26856.0139 |  | 2017-18 | 911.06 | 9576.46 | 7711.5698 | 477731.7466
2018-19 | 164.8 | 776.59 | 361.4817 | Y1 | 22393.7901 |  | 2018-19 | 995.01 | 10000.05 | 7982.5896 | 494521.4257
2019-20 | 164.12 | 1889.4 | 1159.0524 | Y | 71803.2962 |  | 2019-20 | 960.53 | 10209.14 | 8061.6738 | 499420.6894
2020-21 | 341.38 | 2100.3 | 1263.3182 | Y | 78262.565 |  | 2020-21 | 961.6 | 10621.77 | 8229.0055 | 509786.892
2021-22 | 131.94 | 2098.83 | 1312.8511 | Y | 81331.1269 |  | 2021-22 | 1078.53 | 11218.8 | 8483.1233 | 525529.4872
2022-23 | 144.52 | 2595.45 | 1633.3205 | Y | 101184.2037 |  | 2022-23 | 1259.2 | 12344.86 | 8869.391 | 549458.77
|  |  |  | 6 | 972235.9972 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.72 | 8882.12 | 7312.4799 | 453008.131
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 645.71 | 9267.41 | 7547.7193 | 467581.2094
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 692.39 | 9449.48 | 7594.5426 | 470481.9116
2017-18 | 77.94 | 345.63 | 375.3214 | Y1 | 23251.1583 |  | 2017-18 | 768.38 | 9727.48 | 7663.2902 | 474740.8254
2018-19 | 128.41 | 490.65 | 480.217 | Y1 | 29749.4407 |  | 2018-19 | 864.18 | 10401.27 | 7976.1763 | 494124.123
2019-20 | 175.66 | 785.59 | 529.0931 | Y | 32777.3188 |  | 2019-20 | 897.22 | 11495.59 | 8473.5719 | 524937.7804
2020-21 | 181.25 | 894.7 | 604.7673 | Y | 37465.333 |  | 2020-21 | 937.18 | 12755.58 | 8912.6856 | 552140.8729
2021-22 | 107.63 | 581.23 | 385.5914 | Y | 23887.3848 |  | 2021-22 | 964.06 | 14256.99 | 9376.0255 | 580844.781
2022-23 | 109.04 | 480.19 | 362.914 | Y | 22482.5223 |  | 2022-23 | 1073.68 | 16729.7 | 10335.1234 | 640260.8971
|  |  |  | 6 | 216024.9988 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | Y1 | 33.3531 | 22.2354
2018-19 | Y1 | 33.8006 | 22.5337
2019-20 | Y | 71.0846 | 47.3897
2020-21 | Y | 78.8578 | 52.5719
2021-22 | Y | 73.1847 | 48.7898
2022-23 | Y | 87.7661 | 58.5107
| 6 | 843.3069 | 562.2046 | Residual
|  | 503.0609 | 335.374 | NPV

## Option4b
Option 4a:
Stage 1: Install wind monitoring facility on Ballarat-Bendigo 220 kV line in 2015-16
Stage 2: Install a third Moorabool-Ballarat 220 kV line in 2017-18
Stage 3: Up-rate existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 90 degC in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 0.6 | 27.8 | 82.3 |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% | 2% |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 0.11735 | 5.4372 | 16.0963 |  | Scenario 1 | 20%
Project Cost ($M) | 0.71735 | 33.2372 | 98.3963 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 0.073356 | 3.3988 | 10.0619 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 132.3508 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 13.5341
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 43.5 | 235.41 | 107.9529 | 6.6877 | 0.073356 | 6.6143 | Y1 | 6.6877
2016-17 | 40.4 | 276.59 | 156.9977 | 9.726 | 0.073356 | 9.6526 | Y1 | 9.726
2017-18 | 318.52 | 1312.82 | 631.3759 | 39.1137 | 3.4722 | 35.6416 | Y2 | 39.1137
2018-19 | 306.24 | 1512.24 | 691.3685 | 42.8303 | 3.4722 | 39.3581 | Y2 | 42.8303
2019-20 | 302.52 | 2402.16 | 954.9436 | 59.1588 | 13.5341 | 45.6246 | Y | 59.1588
2020-21 | 341.38 | 2927.33 | 1059.4221 | 65.6312 | 13.5341 | 52.0971 | Y | 65.6312
2021-22 | 308.53 | 3242.85 | 984.9203 | 61.0158 | 13.5341 | 47.4817 | Y | 61.0158
2022-23 | 321.02 | 4411.14 | 1179.8515 | 73.0918 | 13.5341 | 59.5577 | Y | 73.0918
[7 empty] | 8 | 696.2999 | Residual
[8 empty] | 443.6164 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 312.0639 | 814.2995 | 314.5291 | 570.9799 | 206.2095 | 443.6164 | 132.3508 | 311.2656
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.59 | 8763.48 | 7320.4771 | 453503.5576
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 597.82 | 8920.63 | 7324.187 | 453733.3822
2015-16 | 41.49 | 156.85 | 121.9874 | Y1 | 7557.117 |  | 2015-16 | 664.38 | 9325.03 | 7568.1868 | 468849.1723
2016-17 | 30.36 | 140.79 | 147.1375 | Y1 | 9115.1694 |  | 2016-17 | 700.25 | 9479 | 7596.6123 | 470610.1332
2017-18 | 263.47 | 612.02 | 371.5475 | Y2 | 23017.3689 |  | 2017-18 | 797.07 | 9809.81 | 7711.8154 | 477746.9665
2018-19 | 209.45 | 422.61 | 337.8249 | Y2 | 20928.2513 |  | 2018-19 | 919.63 | 10611.72 | 8133.3475 | 503860.8789
2019-20 | 205.02 | 1310.42 | 865.1958 | Y | 53598.8773 |  | 2019-20 | 1011.33 | 11798.81 | 8605.2558 | 533095.5943
2020-21 | -33.61 | 1444.07 | 965.1246 | Y | 59789.4665 |  | 2020-21 | 1305.82 | 13028.34 | 9039.6962 | 560009.1821
2021-22 | 308.53 | 1274.02 | 788.2468 | Y | 48831.8893 |  | 2021-22 | 1000.4 | 14327.25 | 9477.1322 | 587108.3423
2022-23 | 141.88 | 1126.94 | 787.3338 | Y | 48775.3264 |  | 2022-23 | 1291.4 | 16936.58 | 10509.5768 | 651068.2828
|  |  |  | 8 | 464652.0792 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.59 | 8763.48 | 7320.4771 | 453503.5576
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 599.06 | 8923.95 | 7322.8577 | 453651.0333
2015-16 | 13.66 | 78.68 | 57.6051 | Y1 | 3568.6372 |  | 2015-16 | 671.37 | 9330.36 | 7568.1994 | 468849.9504
2016-17 | 40.24 | 227.07 | 143.7031 | Y1 | 8902.4083 |  | 2016-17 | 742.68 | 9636.18 | 7758.3511 | 480629.8519
2017-18 | 21.15 | 1312.82 | 665.3103 | Y2 | 41215.9743 |  | 2017-18 | 1050.32 | 10328.71 | 8076.106 | 500314.7667
2018-19 | 254.62 | 1512.24 | 798.0883 | Y2 | 49441.5714 |  | 2018-19 | 1082.54 | 10863.83 | 8414.6617 | 521288.2911
2019-20 | 112.01 | 2402.16 | 1515.3725 | Y | 93877.3251 |  | 2019-20 | 1291.75 | 12275.81 | 8879.2047 | 550066.7324
2020-21 | -0.74 | 2927.33 | 1748.0206 | Y | 108289.8786 |  | 2020-21 | 1442.25 | 13590.05 | 9368.0374 | 580349.9194
2021-22 | -95.81 | 3242.85 | 1838.7396 | Y | 113909.9182 |  | 2021-22 | 1761.71 | 15922.38 | 10475.4631 | 648954.9403
2022-23 | 52.45 | 4411.14 | 2406.5138 | Y | 149083.5324 |  | 2022-23 | 1897.38 | 18745.9 | 11585.8139 | 717741.1723
|  |  |  | 8 | 1420225.7242 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8755.13 | 7262.8642 | 449934.4397
2015-16 | 43.5 | 143.6 | 96.5295 | Y1 | 5980.0038 |  | 2015-16 | 566.91 | 8864.56 | 7329.6573 | 454072.2685
2016-17 | 40.4 | 144.59 | 134.5954 | Y1 | 8338.1875 |  | 2016-17 | 573.49 | 8918.24 | 7343.1711 | 454909.4509
2017-18 | 318.52 | 1166.31 | 867.2875 | Y2 | 53728.4619 |  | 2017-18 | 650 | 9142.68 | 7446.8621 | 461333.1059
2018-19 | 306.24 | 1261.61 | 988.5483 | Y2 | 61240.5684 |  | 2018-19 | 728.7 | 9501.39 | 7665.5856 | 474883.0279
2019-20 | 302.52 | 1165.43 | 705.193 | Y | 43686.7088 |  | 2019-20 | 765.04 | 9879.31 | 7825.7411 | 484804.6624
2020-21 | 253.82 | 1175.97 | 720.1596 | Y | 44613.8872 |  | 2020-21 | 845.3 | 10358.64 | 8043.9876 | 498325.0318
2021-22 | 306.04 | 977.57 | 599.294 | Y | 37126.2633 |  | 2021-22 | 737.04 | 10513.27 | 7967.657 | 493596.3487
2022-23 | 321.02 | 1175.55 | 705.743 | Y | 43720.7813 |  | 2022-23 | 763.1 | 11326.98 | 8232.4457 | 510000.0099
|  |  |  | 8 | 416500.5841 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.23 | 8617.95 | 7210.812 | 446709.8034
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.64 | 8750.58 | 7261.0217 | 449820.2931
2015-16 | 16.96 | 71.28 | 42.0689 | Y1 | 2606.1671 |  | 2015-16 | 566.91 | 8864.05 | 7329.5022 | 454062.6638
2016-17 | 39.96 | 200.28 | 129.8518 | Y1 | 8044.3165 |  | 2016-17 | 609.04 | 9050.4 | 7475.526 | 463108.8357
2017-18 | 49.77 | 1045.49 | 595.8253 | Y2 | 36911.3761 |  | 2017-18 | 911.06 | 9572.23 | 7713.1305 | 477828.4332
2018-19 | 139.37 | 1021.62 | 602.621 | Y2 | 37332.3734 |  | 2018-19 | 995.01 | 10001.91 | 7983.155 | 494556.4547
2019-20 | 164.12 | 1889.4 | 1161.4536 | Y | 71952.0505 |  | 2019-20 | 960.53 | 10209.14 | 8059.2726 | 499271.9351
2020-21 | 341.38 | 2100.3 | 1262.5805 | Y | 78216.8607 |  | 2020-21 | 961.6 | 10621.77 | 8229.7433 | 509832.5962
2021-22 | 131.96 | 2103.08 | 1314.1431 | Y | 81411.1663 |  | 2021-22 | 1078.51 | 11214.55 | 8481.8313 | 525449.4478
2022-23 | 145.41 | 2598.25 | 1637.1158 | Y | 101419.3213 |  | 2022-23 | 1258.31 | 12342.06 | 8865.5957 | 549223.6524
|  |  |  | 8 | 966158.5474 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.71 | 8763.6 | 7320.5136 | 453505.8175
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.72 | 8882.12 | 7312.4799 | 453008.131
2015-16 | 4.14 | 235.41 | 221.5735 | Y1 | 13726.4796 |  | 2015-16 | 645.58 | 9265.52 | 7550.0958 | 467728.4323
2016-17 | 32.92 | 276.59 | 229.7005 | Y1 | 14229.9447 |  | 2016-17 | 692.4 | 9449.52 | 7594.3181 | 470468.0051
2017-18 | 125.18 | 614.62 | 656.909 | Y2 | 40695.5101 |  | 2017-18 | 764.91 | 9729.43 | 7664.8434 | 474837.0511
2018-19 | 169.05 | 780.54 | 729.7598 | Y2 | 45208.6221 |  | 2018-19 | 864.18 | 10402.05 | 7976.4134 | 494138.8126
2019-20 | 175.66 | 780.36 | 527.5032 | Y | 32678.8232 |  | 2019-20 | 897.22 | 11500.82 | 8475.1618 | 525036.276
2020-21 | 181.25 | 891.52 | 601.2254 | Y | 37245.9111 |  | 2020-21 | 937.18 | 12758.76 | 8916.2275 | 552360.2949
2021-22 | 105.35 | 580.13 | 384.1782 | Y | 23799.837 |  | 2021-22 | 966.34 | 14258.09 | 9377.4387 | 580932.3287
2022-23 | 109.04 | 480.69 | 362.551 | Y | 22460.032 |  | 2022-23 | 1073.68 | 16729.2 | 10335.4865 | 640283.3874
|  |  |  | 8 | 213962.7004 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | Y1 | 8.0252 | 5.3501
2016-17 | Y1 | 11.6712 | 7.7808
2017-18 | Y2 | 46.9365 | 31.291
2018-19 | Y2 | 51.3963 | 34.2642
2019-20 | Y | 70.9905 | 47.327
2020-21 | Y | 78.7574 | 52.505
2021-22 | Y | 73.219 | 48.8127
2022-23 | Y | 87.7102 | 58.4734
| 8 | 835.5599 | 557.0399 | Residual
|  | 532.3397 | 354.8931 | NPV

## Option5
Option 5:
Stage 1: Up-rate the existing Ballarat-Bendigo 220 kV line to maximum operating temperature of 82 degC in 2019-20
Stage 2: Replace the existing Moorabool-Ballarat 220 kV line with a new double circuit 220 kV line in 2019-20
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 77.2 | 94.7 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 15.0989 | 18.5215 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 92.2989 | 113.2215 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 9.4384 | 11.578 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 205.5204 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 21.0164
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2019-20 | 288.83 | 2376.34 | 954.6497 | 59.1405 | 21.0164 | 38.1242 | Y | 59.1405
2020-21 | 345.15 | 2890.91 | 1059.062 | 65.6089 | 21.0164 | 44.5925 | Y | 65.6089
2021-22 | 288.49 | 3266.05 | 973.3107 | 60.2966 | 21.0164 | 39.2802 | Y | 60.2966
2022-23 | 303.24 | 4332.69 | 1165.0575 | 72.1753 | 21.0164 | 51.1589 | Y | 72.1753
[7 empty] | 4 | 698.405 | Residual
[8 empty] | 383.6192 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 271.1284 | 754.9198 | 236.0798 | 526.0494 | 129.9186 | 383.6192 | 205.5204 | 178.0988
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.72 | 8765.28 | 7322.0057 | 453598.2519
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 599.86 | 8926.71 | 7322.3813 | 453621.5203
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 662.27 | 9318.47 | 7559.0794 | 468284.9713
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 699.54 | 9463.19 | 7580.343 | 469602.2464
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 799.35 | 9827.66 | 7703.1339 | 477209.1463
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 923.21 | 10637.19 | 8130.4903 | 503683.8753
2019-20 | 152.21 | 1259 | 861.7719 | Y | 53386.7704 |  | 2019-20 | 1064.14 | 11850.23 | 8608.6796 | 533307.7012
2020-21 | -9.33 | 1395.87 | 959.2066 | Y | 59422.8464 |  | 2020-21 | 1281.54 | 13076.54 | 9045.6142 | 560375.8022
2021-22 | 288.34 | 1199.14 | 768.5944 | Y | 47614.4231 |  | 2021-22 | 1020.59 | 14402.13 | 9496.7846 | 588325.8084
2022-23 | 109.26 | 1047.54 | 767.9081 | Y | 47571.9056 |  | 2022-23 | 1324.02 | 17015.98 | 10529.0025 | 652271.7036
|  |  |  | 4 | 460329.9322 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.72 | 8765.28 | 7322.0057 | 453598.2519
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 601.11 | 8929.81 | 7326.5392 | 453879.1034
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 666.49 | 9326.3 | 7560.5062 | 468373.3616
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 747.84 | 9643.66 | 7746.3918 | 479888.9745
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 1033.27 | 10339.1 | 8068.7689 | 499860.2321
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 1055.81 | 10890.44 | 8416.2366 | 521385.8549
2019-20 | 124.19 | 2376.34 | 1512.6945 | Y | 93711.423 |  | 2019-20 | 1279.57 | 12301.63 | 8881.8827 | 550232.6345
2020-21 | 5.04 | 2890.91 | 1751.8225 | Y | 108525.4026 |  | 2020-21 | 1436.47 | 13626.47 | 9364.2356 | 580114.3954
2021-22 | -8.33 | 3266.05 | 1834.9905 | Y | 113677.6602 |  | 2021-22 | 1674.23 | 15899.18 | 10479.2122 | 649187.1983
2022-23 | 48.99 | 4332.69 | 2384.2658 | Y | 147705.2688 |  | 2022-23 | 1900.84 | 18824.35 | 11608.0619 | 719119.4359
|  |  |  | 4 | 1429271.2382 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.5 | 8617.55 | 7211.6718 | 446763.0655
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.65 | 8753.95 | 7260.8908 | 449812.1851
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 563.82 | 8862.23 | 7329.297 | 454049.9467
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 575.37 | 8914.73 | 7331.9564 | 454214.699
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 657.87 | 9150 | 7440.6866 | 460950.5373
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 740.81 | 9514.5 | 7655.129 | 474235.244
2019-20 | 288.83 | 1144.45 | 710.2017 | Y | 43996.9941 |  | 2019-20 | 778.73 | 9900.29 | 7820.7325 | 484494.3771
2020-21 | 273.89 | 1166.36 | 727.1492 | Y | 45046.8929 |  | 2020-21 | 825.23 | 10368.25 | 8036.998 | 497892.0261
2021-22 | 288.49 | 948.73 | 592.378 | Y | 36697.8171 |  | 2021-22 | 754.59 | 10542.11 | 7974.573 | 494024.7949
2022-23 | 303.24 | 1129.65 | 693.8148 | Y | 42981.8269 |  | 2022-23 | 780.88 | 11372.88 | 8244.3739 | 510738.9643
|  |  |  | 4 | 415913.9982 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.5 | 8617.55 | 7211.6718 | 446763.0655
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.65 | 8753.6 | 7260.325 | 449777.1362
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.92 | 8864.57 | 7329.9039 | 454087.5478
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 614.96 | 9063.98 | 7469.1726 | 462715.2401
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 916 | 9599.35 | 7712.6819 | 477800.6449
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 1010.05 | 10022.86 | 7976.4669 | 494142.1232
2019-20 | 171.31 | 1863.49 | 1160.6344 | Y | 71901.3011 |  | 2019-20 | 953.34 | 10235.05 | 8060.0918 | 499322.6845
2020-21 | 345.15 | 2059.7 | 1263.4969 | Y | 78273.6317 |  | 2020-21 | 957.83 | 10662.37 | 8228.8269 | 509775.8252
2021-22 | 172.17 | 2095.43 | 1318.5548 | Y | 81684.4699 |  | 2021-22 | 1038.3 | 11222.2 | 8477.4196 | 525176.1442
2022-23 | 185.17 | 2604.16 | 1639.1838 | Y | 101547.4389 |  | 2022-23 | 1218.55 | 12336.15 | 8863.5276 | 549095.5348
|  |  |  | 4 | 982624.6207 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 549.59 | 8761.16 | 7320.7532 | 453520.6607
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 579.09 | 8879.45 | 7311.6682 | 452957.8475
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 644.85 | 9261.62 | 7540.5512 | 467137.1468
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 692.23 | 9443.13 | 7580.0424 | 469583.6267
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 774.91 | 9756.1 | 7658.4117 | 474438.6036
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 874.61 | 10418.78 | 7971.5466 | 493837.3094
2019-20 | 139.7 | 720.39 | 527.946 | Y | 32706.2547 |  | 2019-20 | 933.18 | 11560.79 | 8474.719 | 525008.8445
2020-21 | 142.67 | 826.12 | 593.6351 | Y | 36775.6957 |  | 2020-21 | 975.76 | 12824.16 | 8923.8178 | 552830.5102
2021-22 | 92.77 | 460.09 | 352.036 | Y | 21808.6302 |  | 2021-22 | 978.92 | 14378.13 | 9409.5809 | 582923.5355
2022-23 | 105.37 | 381.84 | 340.1148 | Y | 21070.1119 |  | 2022-23 | 1077.35 | 16828.05 | 10357.9226 | 641673.3075
|  |  |  | 4 | 203885.1093 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | N | 0 | 0
2018-19 | N | 0 | 0
2019-20 | Y | 70.9687 | 47.3124
2020-21 | Y | 78.7307 | 52.4871
2021-22 | Y | 72.3559 | 48.2373
2022-23 | Y | 86.6104 | 57.7402
| 4 | 838.086 | 558.724 | Residual
|  | 460.343 | 306.8954 | NPV

## Option6
Option 6:
Stage 1: Up-rate existing Moorabool-Ballarat 220 kV line to maximum operating temperature of 82 degC in 2019-20
Stage 2: Replace existing Ballarat-Bendigo 220 kV line with a new double circuit 220 kV line in 2020-21
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 48.4 | 171.8 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 9.4661 | 33.6008 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 57.8661 | 205.4008 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 5.9174 | 21.0042 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 263.2669 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 26.9215
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2018-19 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2019-20 | 163.6 | 1127.81 | 250.0427 | 15.4901 | 5.9174 | 9.5728 | Y1 | 15.4901
2020-21 | 274.45 | 2675.97 | 965.8052 | 59.8316 | 26.9215 | 32.9101 | Y | 59.8316
2021-22 | 173.17 | 3449.35 | 941.9347 | 58.3529 | 26.9215 | 31.4313 | Y | 58.3529
2022-23 | 136.79 | 3983.54 | 1064.2654 | 65.9312 | 26.9215 | 39.0097 | Y | 65.9312
[7 empty] | 4 | 637.9842 | Residual
[8 empty] | 331.998 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 210.1635 | 630.4921 | 218.2871 | 459.2331 | 141.814 | 331.998 | 263.2669 | 68.731
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 568.95 | 8781.34 | 7327.389 | 453931.751
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 627.5 | 8960.47 | 7337.7878 | 454575.9517
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 685.1 | 9361.46 | 7588.581 | 470112.5905
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 737.84 | 9553.98 | 7647.1558 | 473741.2993
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 836.69 | 9866.45 | 7777.5104 | 481816.7693
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 1001.45 | 10621.49 | 8191.5313 | 507465.3628
2019-20 | -176.65 | 189.23 | 176.4515 | Y1 | 10931.1717 |  | 2019-20 | 1123.12 | 11720.11 | 8619.2421 | 533962.0469
2020-21 | 13.33 | 1358.22 | 828.8911 | Y | 51349.8049 |  | 2020-21 | 1258.88 | 13114.19 | 9175.9297 | 568448.8437
2021-22 | 30.72 | 1055.95 | 651.8106 | Y | 40379.6691 |  | 2021-22 | 1278.21 | 14545.32 | 9613.5684 | 595560.5624
2022-23 | -5.59 | 1011.14 | 641.0698 | Y | 39714.2766 |  | 2022-23 | 1438.87 | 17052.38 | 10655.8407 | 660129.3326
|  |  |  | 4 | 384295.5214 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 568.93 | 8781.32 | 7327.383 | 453931.3744
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 634.15 | 8974.57 | 7342.0742 | 454841.4942
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 715.56 | 9406.74 | 7600.801 | 470869.6195
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 794.85 | 9795.3 | 7842.2126 | 485825.073
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 1117.39 | 10448.89 | 8157.4074 | 505351.3909
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 1162.86 | 10882.73 | 8443.8625 | 523097.2806
2019-20 | -115.18 | -850.94 | -349.4581 | Y1 | -21648.9281 |  | 2019-20 | 1312.65 | 12210.89 | 8903.6511 | 551581.1869
2020-21 | -104.75 | 2675.97 | 1576.2482 | Y | 97648.5785 |  | 2020-21 | 1546.26 | 13841.41 | 9539.8098 | 590991.2196
2021-22 | 45.15 | 3449.35 | 1794.61 | Y | 111176.0895 |  | 2021-22 | 1620.75 | 15715.88 | 10519.5927 | 651688.769
2022-23 | 136.79 | 3983.54 | 2152.5241 | Y | 133348.8668 |  | 2022-23 | 1813.04 | 19173.5 | 11839.8037 | 733475.838
|  |  |  | 4 | 1290351.3969 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8625.31 | 7214.518 | 446939.3901
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8764.78 | 7267.2664 | 450207.1535
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.93 | 8872.26 | 7334.4341 | 454368.1913
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 584.85 | 8944.6 | 7364.0258 | 456201.3958
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 655.19 | 9189.71 | 7501.0818 | 464692.015
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 724.69 | 9495.27 | 7702.3949 | 477163.3628
2019-20 | 83.37 | 713.56 | 647.6975 | Y1 | 40124.8614 |  | 2019-20 | 805.39 | 9893.17 | 7883.7414 | 488397.7822
2020-21 | 199.25 | 1184.48 | 671.4027 | Y | 41593.3985 |  | 2020-21 | 899.87 | 10350.13 | 8092.7445 | 501345.5205
2021-22 | 134.2 | 902.5 | 553.637 | Y | 34297.8097 |  | 2021-22 | 908.88 | 10588.34 | 8013.314 | 496424.8023
2022-23 | 66.34 | 1081.61 | 642.1417 | Y | 39780.6771 |  | 2022-23 | 1017.78 | 11420.92 | 8296.047 | 513940.1141
|  |  |  | 4 | 384938.0462 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 523.51 | 8625.31 | 7214.518 | 446939.3901
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 546.66 | 8757.43 | 7265.032 | 450068.7324
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 577.46 | 8882.18 | 7337.5402 | 454560.6179
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 638.08 | 9132.92 | 7524.29 | 466129.7655
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 949.08 | 9631.09 | 7766.7287 | 481148.8442
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 922.18 | 9894.68 | 7995.6858 | 495332.7328
2019-20 | -37.02 | -262.74 | -123.185 | Y1 | -7631.3132 |  | 2019-20 | 962.01 | 10165.81 | 8084.596 | 500840.7222
2020-21 | 274.45 | 2160.29 | 1243.658 | Y | 77044.6131 |  | 2020-21 | 1028.53 | 10561.78 | 8248.6658 | 511004.8438
2021-22 | 173.17 | 2276.78 | 1358.9787 | Y | 84188.7317 |  | 2021-22 | 1037.3 | 11040.85 | 8436.9957 | 522671.8824
2022-23 | 49.94 | 2567.58 | 1535.2937 | Y | 95111.4435 |  | 2022-23 | 1353.78 | 12372.73 | 8967.4178 | 555531.5302
|  |  |  | 4 | 920346.6586 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 553.73 | 8771.7 | 7324.4585 | 453750.2028
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 582.74 | 8888.5 | 7316.417 | 453252.0307
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 637.73 | 9274.29 | 7563.0696 | 468532.1617
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 706.58 | 9500.56 | 7649.3879 | 473879.5816
2017-18 | 0 | 0 | 0 | N | 0 |  | 2017-18 | 771.94 | 9720.1 | 7729.9089 | 478867.8551
2018-19 | 0 | 0 | 0 | N | 0 |  | 2018-19 | 860.17 | 10349.7 | 7996.7189 | 495396.7346
2019-20 | 163.6 | 1127.81 | 898.7077 | Y1 | 55674.9408 |  | 2019-20 | 1007.83 | 11408.74 | 8526.2421 | 528200.6969
2020-21 | -7.2 | 905.01 | 508.8259 | Y | 31521.7657 |  | 2020-21 | 1125.63 | 12745.27 | 9008.627 | 558084.4402
2021-22 | -92.17 | 481.52 | 350.6372 | Y | 21721.9745 |  | 2021-22 | 1163.86 | 14356.7 | 9410.9797 | 583010.1912
2022-23 | -99.45 | 363.96 | 350.2975 | Y | 21700.9314 |  | 2022-23 | 1282.17 | 16845.93 | 10347.7399 | 641042.488
|  |  |  | 4 | 209989.2394 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | N | 0 | 0
2018-19 | N | 0 | 0
2019-20 | Y1 | 18.5882 | 12.3921
2020-21 | Y | 71.798 | 47.8653
2021-22 | Y | 70.0234 | 46.6823
2022-23 | Y | 79.1175 | 52.745
| 4 | 765.581 | 510.3873 | Residual
|  | 398.3976 | 265.5984 | NPV

## Option7
Option 7:
Stage 1: Install a third Moorabool-Ballarat 220 kV line in 2017-18
Stage 2: Replace existing Ballarat-Bendigo 220 kV line with a new double circuit 220 kV line in 2020-21
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 27.8 | 171.8 |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% | 2% |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 5.4372 | 33.6008 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 33.2372 | 205.4008 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 3.3988 | 21.0042 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 238.638 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 24.403
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2015-16 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2016-17 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2017-18 | 294.98 | 1065.14 | 448.6556 | 27.7942 | 3.3988 | 24.3954 | Y1 | 27.7942
2018-19 | 296.5 | 1239.25 | 454.6758 | 28.1672 | 3.3988 | 24.7684 | Y1 | 28.1672
2019-20 | 277.91 | 1338.25 | 567.7101 | 35.1696 | 3.3988 | 31.7708 | Y1 | 35.1696
2020-21 | 367.43 | 2901.15 | 921.0599 | 57.0597 | 24.403 | 32.6567 | Y | 57.0597
2021-22 | 151.21 | 3719.71 | 927.3756 | 57.4509 | 24.403 | 33.0479 | Y | 57.4509
2022-23 | 180.36 | 4414.43 | 1068.9969 | 66.2244 | 24.403 | 41.8214 | Y | 66.2244
[7 empty] | 6 | 636.3217 | Residual
[8 empty] | 373.0507 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 228.0696 | 721.9789 | 260.7821 | 489.99 | 164.4329 | 373.0507 | 238.638 | 134.4127
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.96 | 8803.04 | 7345.1427 | 455031.5915
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 596.1 | 8964.08 | 7357.0786 | 455771.0217
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 672.99 | 9392 | 7618.2301 | 471949.3535
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 751.99 | 9590.41 | 7718.7477 | 478176.4188
2017-18 | 232.94 | 457.29 | 210.6301 | Y1 | 13048.5335 |  | 2017-18 | 815.97 | 9903.87 | 7844.9489 | 485994.5831
2018-19 | 193.81 | 212.32 | 121.9321 | Y1 | 7553.6924 |  | 2018-19 | 978.32 | 10653.27 | 8270.4722 | 512355.7553
2019-20 | 145.35 | 424.23 | 177.4515 | Y1 | 10993.1217 |  | 2019-20 | 1098.23 | 11728.73 | 8693.2513 | 538546.9168
2020-21 | 42.45 | 1391.51 | 774.4155 | Y | 47975.0415 |  | 2020-21 | 1229.76 | 13080.9 | 9230.4053 | 571823.6071
2021-22 | 58.36 | 1166.66 | 648.5924 | Y | 40180.2992 |  | 2021-22 | 1250.57 | 14434.61 | 9616.7866 | 595759.9323
2022-23 | 37.82 | 1266.69 | 673.4614 | Y | 41720.9313 |  | 2022-23 | 1395.46 | 16796.83 | 10623.4492 | 658122.6779
|  |  |  | 6 | 400878.6916 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 552.96 | 8803.04 | 7345.1427 | 455031.5915
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 597.08 | 8965.13 | 7356.6879 | 455746.8166
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 668.42 | 9386.98 | 7615.3746 | 471772.4589
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 737.82 | 9748.61 | 7865.8604 | 487290.0518
2017-18 | 54.61 | 1065.14 | 522.5732 | Y1 | 32373.4097 |  | 2017-18 | 982.23 | 10365.01 | 8185.1798 | 507071.8861
2018-19 | 233.08 | 1239.25 | 526.887 | Y1 | 32640.6521 |  | 2018-19 | 1043.93 | 10837.24 | 8501.7633 | 526684.2352
2019-20 | 103.74 | 1338.25 | 741.1029 | Y1 | 45911.3234 |  | 2019-20 | 1197.52 | 12170.55 | 8964.774 | 555367.7493
2020-21 | 123.17 | 2901.15 | 1579.0423 | Y | 97821.6717 |  | 2020-21 | 1318.34 | 13616.23 | 9537.0158 | 590818.1263
2021-22 | 132.05 | 3719.71 | 1852.3629 | Y | 114753.8804 |  | 2021-22 | 1533.85 | 15445.52 | 10461.8398 | 648110.9781
2022-23 | 161.6 | 4414.43 | 2232.1916 | Y | 138284.2696 |  | 2022-23 | 1788.23 | 18742.61 | 11760.1362 | 728540.4351
|  |  |  | 6 | 1328714.758 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 534.23 | 8682.92 | 7242.381 | 448665.5005
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 545.48 | 8812.01 | 7293.7347 | 451846.8659
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 565.78 | 8911.13 | 7362.1124 | 456082.8632
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 590.5 | 8987.72 | 7415.1498 | 459368.5276
2017-18 | 294.98 | 970.65 | 701.2423 | Y1 | 43441.9617 |  | 2017-18 | 644.85 | 9259.2 | 7576.9123 | 469389.7182
2018-19 | 296.5 | 1025.25 | 782.861 | Y1 | 48498.2414 |  | 2018-19 | 693.92 | 9541.45 | 7764.1444 | 480988.7456
2019-20 | 277.91 | 1065.22 | 803.4822 | Y1 | 49775.7248 |  | 2019-20 | 811.95 | 9951.18 | 7959.9031 | 493115.9983
2020-21 | 206.64 | 1138.29 | 611.8913 | Y | 37906.6648 |  | 2020-21 | 892.48 | 10396.32 | 8152.2559 | 505032.2542
2021-22 | 143.01 | 875.55 | 509.6628 | Y | 31573.6105 |  | 2021-22 | 900.07 | 10615.29 | 8057.2882 | 499149.0015
2022-23 | 75.38 | 1055.89 | 591.2682 | Y | 36629.0675 |  | 2022-23 | 1008.74 | 11446.64 | 8346.9205 | 517091.7237
|  |  |  | 6 | 351953.1372 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 534.23 | 8682.92 | 7242.381 | 448665.5005
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 544.52 | 8816.9 | 7294.8524 | 451916.1062
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 566.19 | 8915.79 | 7363.3063 | 456156.8265
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 610.98 | 9148.45 | 7563.3239 | 468547.9168
2017-18 | 52.06 | 802.76 | 433.5111 | Y1 | 26856.0139 |  | 2017-18 | 855.79 | 9611.03 | 7800.7479 | 483256.3336
2018-19 | 164.8 | 776.59 | 361.4817 | Y1 | 22393.7901 |  | 2018-19 | 794.45 | 9800.31 | 8014.9656 | 496527.1189
2019-20 | 120.08 | 1146.02 | 577.6386 | Y1 | 35784.7088 |  | 2019-20 | 874.21 | 10140.94 | 8127.1336 | 503475.9265
2020-21 | 367.43 | 2184.32 | 1198.8745 | Y | 74270.274 |  | 2020-21 | 935.55 | 10537.75 | 8293.4493 | 513779.1829
2021-22 | 151.21 | 2216.92 | 1285.6094 | Y | 79643.4999 |  | 2021-22 | 1059.26 | 11100.71 | 8510.365 | 527217.1142
2022-23 | 180.36 | 2648.4 | 1475.5982 | Y | 91413.311 |  | 2022-23 | 1223.36 | 12291.91 | 9027.1132 | 559229.6627
|  |  |  | 6 | 878351.6425 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 554.96 | 8811.53 | 7348.19 | 455220.3705
2014-15 | 0 | 0 | 0 | N | 0 |  | 2014-15 | 584.34 | 8935.86 | 7350.9079 | 455388.7456
2015-16 | 0 | 0 | 0 | N | 0 |  | 2015-16 | 649.29 | 9316.33 | 7596.2982 | 470590.676
2016-17 | 0 | 0 | 0 | N | 0 |  | 2016-17 | 714.7 | 9560.81 | 7717.795 | 478117.4027
2017-18 | 77.94 | 345.63 | 375.3214 | Y1 | 23251.1583 |  | 2017-18 | 781.53 | 9759.39 | 7795.2154 | 482913.5916
2018-19 | 128.41 | 490.65 | 480.217 | Y1 | 29749.4407 |  | 2018-19 | 856.21 | 10398.12 | 8082.9386 | 500738.0487
2019-20 | 111.81 | 530.37 | 538.8751 | Y1 | 33383.3137 |  | 2019-20 | 1020.31 | 11462.91 | 8629.0903 | 534572.1453
2020-21 | -23.95 | 862.33 | 441.076 | Y | 27324.6582 |  | 2020-21 | 1142.38 | 12787.95 | 9076.3769 | 562281.5477
2021-22 | -92.26 | 531.41 | 340.6503 | Y | 21103.2873 |  | 2021-22 | 1163.95 | 14306.81 | 9420.9666 | 583628.8784
2022-23 | -99.8 | 526.65 | 372.4651 | Y | 23074.2142 |  | 2022-23 | 1282.52 | 16683.24 | 10325.5723 | 639669.2052
|  |  |  | 6 | 221710.3146 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | N | 0 | 0
2015-16 | N | 0 | 0
2016-17 | N | 0 | 0
2017-18 | Y1 | 33.3531 | 22.2354
2018-19 | Y1 | 33.8006 | 22.5337
2019-20 | Y1 | 42.2036 | 28.1357
2020-21 | Y | 68.4716 | 45.6477
2021-22 | Y | 68.9411 | 45.9607
2022-23 | Y | 79.4692 | 52.9795
| 6 | 763.5861 | 509.0574 | Residual
|  | 447.6608 | 298.4406 | NPV

## Option8
Option 8:
Non-network demand side management in 2014
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Project Cost ($M) | 18.1906 |  |  |  | Discount Rate | 10%
Establishment Cost ($k/MW) | 80 |  |  |  | Years | 40
Availability Charge ($k/MW/year) | 90 |  |  |  | Scenario 1 | 20%
Dispatch Fee ($k/MWh) | 0.9 | 0 | 0 |  | Scenario 2 | 20%
Demand Side Management Reduction (MW) | 21 | 0 | 0 |  | Scenario 3 | 20%
Annualised Project Cost ($M) | 1.89 | 0 | 0 |  | Scenario 4 | 20%
[5 empty] | Scenario 5 | 20%
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Dispatch Cost ($'000) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits Based ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | 0
2014-15 | 21.01 | 167.38 | 90.4555 | 81.41 | 5.5223 | 3.57 | 1.9523 | Y | 5.5223
2015-16 | 22.66 | 184.7 | 104.7952 | 94.3157 | 6.3977 | 1.89 | 4.5077 | Y | 6.3977
2016-17 | 21.91 | 311.21 | 128.9321 | 116.0389 | 7.8713 | 1.89 | 5.9813 | Y | 7.8713
2017-18 | 22.48 | 400.15 | 133.5252 | 120.1727 | 8.1517 | 1.89 | 6.2617 | Y | 8.1517
2018-19 | 23.85 | 429.58 | 147.0086 | 132.3078 | 8.9749 | 1.89 | 7.0849 | Y | 8.9749
2019-20 | 28.71 | 408.7 | 162.9591 | 146.6632 | 9.9487 | 1.89 | 8.0587 | Y | 9.9487
2020-21 | 28.32 | 661.85 | 190.4688 | 171.4219 | 11.6281 | 1.89 | 9.7381 | Y | 11.6281
2021-22 | 27.49 | 843.58 | 196.0396 | 176.4356 | 11.9682 | 1.89 | 10.0782 | Y | 11.9682
2022-23 | 28.28 | 1180.84 | 239.9591 | 215.9632 | 14.6495 | 1.89 | 12.7595 | Y | 14.6495
[6 empty] | 17.9153 | Residual | 9 | 138.8628 | Residual
[6 empty] | 18.1906 | NPV |  | 99.6657 | NPV
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 64.9435 | 202.6981 | 59.903 | 126.2926 | 44.4911 | 99.6657 | 18.1906 | 81.475
Scenario 1 - Market Benefits | [7 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Dispatch Cost ($'000) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 784.46 | 10062.91 | 7975.6826 | 494093.5346
2014-15 | 19.35 | 152.35 | 97.8532 | 88.0679 | Y | 5973.9379 |  | 2014-15 | 830.79 | 10000.18 | 7887.0753 | 488604.3136
2015-16 | 17.58 | 140.86 | 119.5833 | 107.625 | Y | 7300.5592 |  | 2015-16 | 922.48 | 10319.5 | 8109.1571 | 502362.2836
2016-17 | 12.76 | 139.48 | 107.0394 | 96.3355 | Y | 6534.7578 |  | 2016-17 | 979.8 | 10566.67 | 8220.5306 | 509261.8682
2017-18 | 21.99 | 124.49 | 109.4077 | 98.4669 | Y | 6679.3389 |  | 2017-18 | 1107.95 | 10932.8 | 8350.2224 | 517296.2777
2018-19 | 22.72 | 152.25 | 121.7304 | 109.5574 | Y | 7431.6409 |  | 2018-19 | 1146.09 | 11565.07 | 8759.2017 | 542632.5441
2019-20 | 15.22 | 175.17 | 139.4026 | 125.4623 | Y | 8510.5263 |  | 2019-20 | 1201.13 | 12934.06 | 9331.049 | 578058.4831
2020-21 | 15.74 | 214.53 | 144.9022 | 130.4119 | Y | 8846.2769 |  | 2020-21 | 1256.47 | 14257.88 | 9859.9186 | 610821.9597
2021-22 | 22.43 | 135.39 | 111.8095 | 100.6286 | Y | 6825.9712 |  | 2021-22 | 1286.5 | 15465.88 | 10153.5695 | 629013.6318
2022-23 | 21.22 | 133.59 | 122.9551 | 110.6596 | Y | 7506.4101 |  | 2022-23 | 1412.06 | 17929.93 | 11173.9554 | 692226.5395
[5 empty] | 9 | 71153.3598 | Residual
Scenario 2 - Market Benefits | [7 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Dispatch Cost ($'000) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 784.46 | 10062.91 | 7975.6826 | 494093.5346
2014-15 | 21.01 | 167.38 | 100.5153 | 90.4638 | Y | 6136.4578 |  | 2014-15 | 830.13 | 10153.28 | 7948.8253 | 492429.7261
2015-16 | 22.66 | 184.7 | 124.5378 | 112.084 | Y | 7603.0302 |  | 2015-16 | 916.68 | 10682.24 | 8264.3708 | 511977.7711
2016-17 | 21.91 | 311.21 | 199.4394 | 179.4954 | Y | 12175.7729 |  | 2016-17 | 1034.34 | 11384.87 | 8686.3249 | 538117.8263
2017-18 | 22.07 | 400.15 | 217.4639 | 195.7175 | Y | 13276.1723 |  | 2017-18 | 1133.53 | 12092.35 | 9093.119 | 563318.7196
2018-19 | 22.58 | 429.58 | 240.2541 | 216.2287 | Y | 14667.5116 |  | 2018-19 | 1360.83 | 12878.81 | 9567.7153 | 592719.9616
2019-20 | 28.71 | 408.7 | 251.8216 | 226.6394 | Y | 15373.7087 |  | 2019-20 | 1375.05 | 14269.27 | 10142.7556 | 628343.7094
2020-21 | 28.32 | 661.85 | 344.7176 | 310.2458 | Y | 21045.0095 |  | 2020-21 | 1413.19 | 15855.53 | 10771.3405 | 667284.5427
2021-22 | 27.49 | 843.58 | 429.4043 | 386.4639 | Y | 26215.1337 |  | 2021-22 | 1638.41 | 18321.65 | 11884.7984 | 736263.2609
2022-23 | 28.28 | 1180.84 | 560.5161 | 504.4645 | Y | 34219.5067 |  | 2022-23 | 1921.55 | 21976.2 | 13431.8117 | 832100.7336
[5 empty] | 9 | 324367.1539 | Residual
Scenario 3 - Market Benefits | [7 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Dispatch Cost ($'000) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 746.61 | 9777.73 | 7802.7256 | 483378.8509
2014-15 | 20.19 | 135.14 | 89.9487 | 80.9538 | Y | 5491.3694 |  | 2014-15 | 779.35 | 9678.27 | 7740.4877 | 479523.2118
2015-16 | 19.27 | 137.06 | 103.5337 | 93.1803 | Y | 6320.7312 |  | 2015-16 | 806.14 | 9710.55 | 7783.6879 | 482199.4666
2016-17 | 21.25 | 148.48 | 98.9874 | 89.0887 | Y | 6043.1832 |  | 2016-17 | 831.64 | 9803.74 | 7849.365 | 486268.1642
2017-18 | 22.48 | 108.41 | 88.7271 | 79.8544 | Y | 5416.7907 |  | 2017-18 | 943.22 | 10139.23 | 7998.7655 | 495523.524
2018-19 | 23.85 | 123.25 | 104.1935 | 93.7742 | Y | 6361.0144 |  | 2018-19 | 982.53 | 10399.69 | 8190.934 | 507428.3613
2019-20 | 22.57 | 136.87 | 125.908 | 113.3172 | Y | 7686.6834 |  | 2019-20 | 1044.99 | 10907.87 | 8405.0262 | 520691.3706
2020-21 | 22.65 | 161.17 | 130.0518 | 117.0467 | Y | 7939.6648 |  | 2020-21 | 1076.47 | 11373.44 | 8634.0954 | 534882.2076
2021-22 | 22.98 | 107.04 | 118.4683 | 106.6215 | Y | 7232.4909 |  | 2021-22 | 1020.1 | 11383.8 | 8448.4826 | 523383.4995
2022-23 | 23.04 | 124.35 | 116.8402 | 105.1561 | Y | 7133.0918 |  | 2022-23 | 1061.08 | 12378.18 | 8821.3486 | 546482.5433
[5 empty] | 9 | 67614.6707 | Residual
Scenario 4 - Market Benefits | [7 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Dispatch Cost ($'000) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 746.61 | 9777.73 | 7802.7256 | 483378.8509
2014-15 | 16.58 | 128.26 | 90.3419 | 81.3077 | Y | 5515.3742 |  | 2014-15 | 778.15 | 9817.29 | 7796.5375 | 482995.4994
2015-16 | 16.06 | 137.34 | 97.7654 | 87.9889 | Y | 5968.5801 |  | 2015-16 | 805.97 | 9997.03 | 7916.0805 | 490401.1857
2016-17 | 20.99 | 279.32 | 178.6018 | 160.7417 | Y | 10903.6423 |  | 2016-17 | 889.95 | 10454.48 | 8221.3083 | 509310.0504
2017-18 | 8.3 | 266.45 | 187.2104 | 168.4894 | Y | 11429.1949 |  | 2017-18 | 985.27 | 10962.74 | 8512.4929 | 527348.9339
2018-19 | 22.55 | 274.16 | 176.6434 | 158.9791 | Y | 10784.082 |  | 2018-19 | 1077.17 | 11227.91 | 8794.0258 | 544789.9008
2019-20 | 16.34 | 300.34 | 184.8736 | 166.3862 | Y | 11286.5333 |  | 2019-20 | 1108.31 | 11798.2 | 9035.8526 | 559771.0661
2020-21 | 22.29 | 409.96 | 219.1794 | 197.2615 | Y | 13380.9048 |  | 2020-21 | 1280.69 | 12312.11 | 9273.1443 | 574471.2906
2021-22 | 27.2 | 453.24 | 236.6309 | 212.9678 | Y | 14446.3152 |  | 2021-22 | 1183.27 | 12864.39 | 9559.3435 | 592201.3311
2022-23 | 27.23 | 600.77 | 318.0966 | 286.2869 | Y | 19419.795 |  | 2022-23 | 1376.49 | 14339.54 | 10184.6149 | 630936.8918
[5 empty] | 9 | 184080.4921 | Residual
Scenario 5 - Market Benefits | [7 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Dispatch Cost ($'000) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 0 | 0 | 0 | 0 | N | 0 |  | 2013-14 | 783.13 | 9931.39 | 7865.9543 | 487295.8701
2014-15 | 20.8 | 153.22 | 73.6185 | 66.2566 | Y | 4494.4082 |  | 2014-15 | 743.15 | 9563.75 | 7598.8724 | 470750.1452
2015-16 | 15.11 | 97 | 78.556 | 70.7004 | Y | 4795.8438 |  | 2015-16 | 740.08 | 9720.24 | 7801.201 | 483284.3995
2016-17 | 15.3 | 95.33 | 60.5926 | 54.5334 | Y | 3699.1807 |  | 2016-17 | 785.36 | 9855.87 | 7851.5918 | 486406.1145
2017-18 | 11.63 | 87.27 | 64.817 | 58.3353 | Y | 3957.0803 |  | 2017-18 | 879.2 | 10220.3 | 8037.7693 | 497939.8069
2018-19 | 13.26 | 120.89 | 92.2218 | 82.9996 | Y | 5630.1384 |  | 2018-19 | 980.14 | 10823.91 | 8237.6645 | 510323.3145
2019-20 | 10.41 | 131.7 | 112.7897 | 101.5107 | Y | 6885.81 |  | 2019-20 | 1062.47 | 12149.48 | 8889.8754 | 550727.7786
2020-21 | 11.21 | 172.98 | 113.4929 | 102.1436 | Y | 6928.7403 |  | 2020-21 | 1107.22 | 13477.3 | 9403.96 | 582575.322
2021-22 | 12.01 | 83.14 | 83.8847 | 75.4962 | Y | 5121.1622 |  | 2021-22 | 1059.68 | 14755.08 | 9677.7322 | 599535.5073
2022-23 | 13.28 | 95.92 | 81.3875 | 73.2488 | Y | 4968.7081 |  | 2022-23 | 1169.44 | 17113.97 | 10616.6499 | 657701.4625
[5 empty] | 9 | 47098.4494 | Residual
NPV of Net Market Benefit (PV, $M) for Table 18 Calculation Purpose
Year | VCR ($k) | 74.34 | 49.56
| Year in Service | Annualised Gross Market Benefits ($M) | Annualised Gross Market Benefits ($M)
2013-14 | N | 0 | 0
2014-15 | Y | 6.6431 | 4.4016
2015-16 | Y | 7.6962 | 5.0993
2016-17 | Y | 9.4688 | 6.2738
2017-18 | Y | 9.8061 | 6.4973
2018-19 | Y | 10.7963 | 7.1534
2019-20 | Y | 11.9677 | 7.9296
2020-21 | Y | 13.988 | 9.2682
2021-22 | Y | 14.3971 | 9.5393
2022-23 | Y | 17.6226 | 11.6764
| 9 | 167.0448 | 110.6808 | Residual
|  | 119.8926 | 79.4387 | NPV

## DoubleCircuit_MLTS-BATS
Stage 1: Installation of a double circuit Moorabool-Ballarat 220 kV line only
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 94.7 |  |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% |  |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 18.5215 | 0 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 113.2215 | 0 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 11.578 | 0 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 113.2215 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 11.578
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits Based on Year 1 ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 211.05 | 1162.68 | 599.3079 | 37.1271 | 11.578 | 25.5492 | Y | 37.1271
2014-15 | 209.14 | 889.2 | 423.6282 | 26.2438 | 11.578 | 14.6658 | Y | 26.2438
2015-16 | 221.36 | 905.79 | 401.1752 | 24.8528 | 11.578 | 13.2748 | Y | 24.8528
2016-17 | 248.83 | 1043.39 | 483.7884 | 29.9707 | 11.578 | 18.3927 | Y | 29.9707
2017-18 | 297.01 | 1112.35 | 476.3357 | 29.509 | 11.578 | 17.931 | Y | 29.509
2018-19 | 304.94 | 1271.89 | 481.9545 | 29.8571 | 11.578 | 18.2791 | Y | 29.8571
2019-20 | 286.62 | 1403.24 | 598.1983 | 37.0584 | 11.578 | 25.4804 | Y | 37.0584
2020-21 | 289.53 | 1469.58 | 632.7664 | 39.1999 | 11.578 | 27.6219 | Y | 39.1999
2021-22 | 259.03 | 1746.66 | 605.4559 | 37.508 | 11.578 | 25.93 | Y | 37.508
2022-23 | 274.68 | 2103.83 | 632.5252 | 39.1849 | 11.578 | 27.607 | Y | 39.1849
[7 empty] | 10 | 369.393 | Residual
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 149.1995 | 474.9309 | 458.4347 | 360.7198 | 269.9573 | 342.6485 | 113.2215 | 229.4269
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 157.2 | 1008.13 | 552.257 | Y | 34212.3187 |  | 2013-14 | 642.59 | 9233.71 | 7533.2985 | 466687.8408
2014-15 | 169.48 | 718.16 | 397.2066 | Y | 24606.9464 |  | 2014-15 | 680.66 | 9434.37 | 7587.7219 | 470059.3729
2015-16 | 195.77 | 466.49 | 300.5358 | Y | 18618.1903 |  | 2015-16 | 744.29 | 9993.87 | 7928.2046 | 491152.2774
2016-17 | 194.11 | 498.43 | 299.8194 | Y | 18573.8143 |  | 2016-17 | 798.45 | 10207.72 | 8027.7506 | 497319.1472
2017-18 | 233.16 | 476.03 | 239.0698 | Y | 14810.3766 |  | 2017-18 | 896.78 | 10581.26 | 8220.5602 | 509263.7069
2018-19 | 191.94 | 230.64 | 153.1056 | Y | 9484.8919 |  | 2018-19 | 976.87 | 11486.68 | 8727.8265 | 540688.8504
2019-20 | 146.47 | 444.51 | 210.0624 | Y | 13013.3657 |  | 2019-20 | 1069.88 | 12664.72 | 9260.3891 | 573681.106
2020-21 | -32.89 | 387 | 217.1134 | Y | 13450.1727 |  | 2020-21 | 1305.1 | 14085.41 | 9787.7074 | 606348.4759
2021-22 | 57.23 | 398.97 | 275.0194 | Y | 17037.4494 |  | 2021-22 | 1251.7 | 15202.3 | 9990.3597 | 618902.7822
2022-23 | -124.69 | 111.37 | 144.0263 | Y | 8922.4305 |  | 2022-23 | 1557.97 | 17952.15 | 11152.8842 | 690921.1787
|  |  |  | 10 | 85382.5954 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 161.39 | 1012.5 | 554.2884 | Y | 34338.1664 |  | 2013-14 | 642.59 | 9233.71 | 7533.2985 | 466687.8408
2014-15 | 170.02 | 889.2 | 465.9276 | Y | 28864.2148 |  | 2014-15 | 681.12 | 9431.46 | 7583.413 | 469792.4329
2015-16 | 191.97 | 905.79 | 478.5365 | Y | 29645.3349 |  | 2015-16 | 747.37 | 9961.15 | 7910.3721 | 490047.5504
2016-17 | 215.48 | 1043.39 | 558.4311 | Y | 34594.8079 |  | 2016-17 | 840.77 | 10652.69 | 8327.3331 | 515878.2868
2017-18 | 87.28 | 1112.35 | 566.8043 | Y | 35113.5276 |  | 2017-18 | 1068.32 | 11380.15 | 8743.7786 | 541677.0818
2018-19 | 298.35 | 1271.89 | 569.1666 | Y | 35259.8733 |  | 2018-19 | 1085.06 | 12036.5 | 9238.8027 | 572343.8285
2019-20 | 120.42 | 1403.24 | 787.5375 | Y | 48787.9494 |  | 2019-20 | 1283.34 | 13274.73 | 9607.0397 | 595156.1082
2020-21 | -76.47 | 1469.58 | 878.9753 | Y | 54452.5186 |  | 2020-21 | 1517.98 | 15047.8 | 10237.0828 | 634187.2795
2021-22 | -85.5 | 1746.66 | 894.3941 | Y | 55407.7133 |  | 2021-22 | 1751.4 | 17418.57 | 11419.8086 | 707457.1452
2022-23 | 12.29 | 2103.83 | 1023.2552 | Y | 63390.6596 |  | 2022-23 | 1937.54 | 21053.21 | 12969.0726 | 803434.0451
|  |  |  | 10 | 606612.6295 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 194.73 | 1122.67 | 727.168 | Y | 45048.0576 |  | 2013-14 | 571.75 | 8815.41 | 7181.4804 | 444892.7108
2014-15 | 209.14 | 876.44 | 596.2304 | Y | 36936.4733 |  | 2014-15 | 590.4 | 8936.97 | 7234.206 | 448159.0617
2015-16 | 221.36 | 756.51 | 540.2419 | Y | 33467.9869 |  | 2015-16 | 604.05 | 9091.1 | 7346.9797 | 455145.3912
2016-17 | 248.83 | 933.86 | 672.338 | Y | 41651.3391 |  | 2016-17 | 604.06 | 9018.36 | 7276.0145 | 450749.097
2017-18 | 297.01 | 986.12 | 718.0486 | Y | 44483.1132 |  | 2017-18 | 668.69 | 9261.52 | 7369.444 | 456537.0558
2018-19 | 304.94 | 1048.23 | 805.7993 | Y | 49919.2654 |  | 2018-19 | 701.44 | 9474.71 | 7489.3282 | 463963.8845
2019-20 | 286.62 | 1089.5 | 827.5117 | Y | 51264.3486 |  | 2019-20 | 780.94 | 9955.24 | 7703.4225 | 477227.0226
2020-21 | 289.53 | 1110.86 | 851.7183 | Y | 52763.9499 |  | 2020-21 | 809.59 | 10423.75 | 7912.4289 | 490174.9691
2021-22 | 259.03 | 986.2 | 756.5409 | Y | 46867.7075 |  | 2021-22 | 784.05 | 10504.64 | 7810.4101 | 483854.9045
2022-23 | 274.68 | 1115.3 | 819.0546 | Y | 50740.43 |  | 2022-23 | 809.44 | 11387.23 | 8119.1342 | 502980.3612
|  |  |  | 10 | 485557.1126 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 154.16 | 885.5 | 481.9105 | Y | 29854.3542 |  | 2013-14 | 612.32 | 9052.58 | 7426.7379 | 460086.4141
2014-15 | 156.8 | 753.77 | 387.5766 | Y | 24010.3679 |  | 2014-15 | 637.93 | 9191.78 | 7499.3029 | 464581.8134
2015-16 | 165.88 | 790.85 | 410.1937 | Y | 25411.4985 |  | 2015-16 | 656.15 | 9343.52 | 7603.6522 | 471046.2563
2016-17 | 220.74 | 976.53 | 502.7141 | Y | 31143.1373 |  | 2016-17 | 690.2 | 9757.27 | 7897.1961 | 489231.2972
2017-18 | 23.53 | 828.21 | 468.7399 | Y | 29038.438 |  | 2017-18 | 970.04 | 10400.98 | 8230.9634 | 509908.1802
2018-19 | 135.34 | 793.69 | 393.4552 | Y | 24374.5496 |  | 2018-19 | 964.38 | 10708.38 | 8577.2141 | 531358.4123
2019-20 | 92.07 | 1181.25 | 612.2561 | Y | 37929.2642 |  | 2019-20 | 1032.58 | 10917.29 | 8608.4701 | 533294.7215
2020-21 | 277.94 | 1283.47 | 653.423 | Y | 40479.5524 |  | 2020-21 | 1025.04 | 11438.6 | 8838.9008 | 547569.9046
2021-22 | 159.88 | 1180.84 | 606.4242 | Y | 37567.9817 |  | 2021-22 | 1050.59 | 12136.79 | 9189.5502 | 569292.6324
2022-23 | 201.34 | 1377.1 | 741.9582 | Y | 45964.313 |  | 2022-23 | 1202.38 | 13563.21 | 9760.7532 | 604678.6607
|  |  |  | 10 | 439852.3838 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 211.05 | 1162.68 | 680.9158 | Y | 42182.7313 |  | 2013-14 | 587.12 | 8947.76 | 7298.4836 | 452141.059
2014-15 | 132.85 | 520.73 | 271.2001 | Y | 16800.845 |  | 2014-15 | 631.1 | 9196.24 | 7401.2908 | 458509.9651
2015-16 | 63.22 | 269.06 | 276.368 | Y | 17120.9976 |  | 2015-16 | 691.97 | 9548.18 | 7603.389 | 471029.9461
2016-17 | 84.41 | 395.46 | 385.6394 | Y | 23890.3633 |  | 2016-17 | 716.25 | 9555.74 | 7526.545 | 466269.4652
2017-18 | 84.15 | 359.38 | 389.0157 | Y | 24099.5214 |  | 2017-18 | 806.68 | 9948.19 | 7713.5706 | 477855.7011
2018-19 | 127.99 | 491.03 | 488.246 | Y | 30246.8397 |  | 2018-19 | 865.41 | 10453.77 | 7841.6402 | 485789.6129
2019-20 | 107.75 | 531.7 | 553.624 | Y | 34297.0068 |  | 2019-20 | 965.13 | 11749.48 | 8449.041 | 523418.0924
2020-21 | 115.7 | 551.32 | 562.6022 | Y | 34853.2038 |  | 2020-21 | 1002.73 | 13098.96 | 8954.8507 | 554753.0021
2021-22 | 103.26 | 452.41 | 494.9008 | Y | 30659.1046 |  | 2021-22 | 968.43 | 14385.81 | 9266.7161 | 574073.0612
2022-23 | 99.34 | 290.03 | 434.3317 | Y | 26906.8476 |  | 2022-23 | 1083.38 | 16919.86 | 10263.7058 | 635836.5718
|  |  |  | 10 | 257483.2578 | Residual

## DoubleCircuit_BATS-BETS
Stage 1: Installation of a double circuit Ballarat-Bendigo 220 kV line only
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 171.8 |  |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% |  |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 33.6008 | 0 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 205.4008 | 0 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 21.0042 | 0 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 205.4008 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 21.0042
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits Based on Year 1 ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 31.98 | -9.1 | -56.2354 | -3.4838 | 21.0042 | -24.488 | Y | -3.4838
2014-15 | 34.88 | 98.1 | 11.0529 | 0.68473 | 21.0042 | -20.3194 | Y | 0.68473
2015-16 | 30.49 | 390.48 | 78.9022 | 4.888 | 21.0042 | -16.1162 | Y | 4.888
2016-17 | 82.71 | 560.73 | 110.3046 | 6.8334 | 21.0042 | -14.1708 | Y | 6.8334
2017-18 | 155.19 | 740.04 | 169.1695 | 10.48 | 21.0042 | -10.5241 | Y | 10.48
2018-19 | 184.37 | 853.74 | 290.3761 | 17.9888 | 21.0042 | -3.0154 | Y | 17.9888
2019-20 | 163.6 | 1127.81 | 250.0427 | 15.4901 | 21.0042 | -5.514 | Y | 15.4901
2020-21 | 86.8 | 1228.17 | 228.3181 | 14.1443 | 21.0042 | -6.8599 | Y | 14.1443
2021-22 | 20.08 | 777.1 | 97.0406 | 6.0117 | 21.0042 | -14.9925 | Y | 6.0117
2022-23 | 0.05 | 811.65 | 66.8318 | 4.1402 | 21.0042 | -16.8639 | Y | 4.1402
[7 empty] | 10 | 39.0296 | Residual
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | -16.9285 | -278.8635 | 309.8714 | -58.5568 | 326.3184 | 56.3682 | 205.4008 | -149.0326
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | -17.21 | -362.16 | -170.4446 | Y | -10559.0405 |  | 2013-14 | 817 | 10604 | 8256 | 511459.2
2014-15 | -12.86 | -187.47 | -63.0715 | Y | -3907.2807 |  | 2014-15 | 863 | 10340 | 8048 | 498573.6
2015-16 | 4.06 | -126.64 | -22.2596 | Y | -1378.9822 |  | 2015-16 | 936 | 10587 | 8251 | 511149.45
2016-17 | -6.44 | -206.85 | -23.43 | Y | -1451.4885 |  | 2016-17 | 999 | 10913 | 8351 | 517344.45
2017-18 | 5.94 | 9.29 | 44.6301 | Y | 2764.8335 |  | 2017-18 | 1124 | 11048 | 8415 | 521309.25
2018-19 | -87.19 | 48.32 | 78.9321 | Y | 4889.8424 |  | 2018-19 | 1256 | 11669 | 8802 | 545283.9
2019-20 | -176.65 | 189.23 | 176.4515 | Y | 10931.1717 |  | 2019-20 | 1393 | 12920 | 9294 | 575763.3
2020-21 | -255.79 | 193.41 | 172.8208 | Y | 10706.2486 |  | 2020-21 | 1528 | 14279 | 9832 | 609092.4
2021-22 | -231.07 | -14.73 | 49.379 | Y | 3059.0315 |  | 2021-22 | 1540 | 15616 | 10216 | 632881.2
2022-23 | -236.72 | -358.48 | -73.0894 | Y | -4527.8908 |  | 2022-23 | 1670 | 18422 | 11370 | 704371.5
|  |  |  | 10 | -43329.3448 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | -13.07 | -357.38 | -168.0889 | Y | -10413.1061 |  | 2013-14 | 817.05 | 10603.59 | 8255.6758 | 511439.1133
2014-15 | -15.45 | -252.34 | -141.2166 | Y | -8748.3708 |  | 2014-15 | 866.59 | 10573 | 8190.5572 | 507405.0185
2015-16 | -17.51 | -351.95 | -201.4539 | Y | -12480.0703 |  | 2015-16 | 956.85 | 11218.89 | 8590.3625 | 532172.9556
2016-17 | 21.91 | -367.29 | -212.2003 | Y | -13145.8098 |  | 2016-17 | 1034.34 | 12063.37 | 9097.9646 | 563618.9045
2017-18 | -44.86 | -393.64 | -220.4891 | Y | -13659.301 |  | 2017-18 | 1200.46 | 12886.14 | 9531.072 | 590449.9104
2018-19 | -46.02 | -226.97 | -15.1702 | Y | -939.7964 |  | 2018-19 | 1429.43 | 13535.36 | 9823.1396 | 608543.4982
2019-20 | -115.18 | -850.94 | -349.4581 | Y | -21648.9281 |  | 2019-20 | 1518.94 | 15528.91 | 10744.0353 | 665592.9856
2020-21 | -289.21 | -1290.61 | -494.038 | Y | -30605.6541 |  | 2020-21 | 1730.72 | 17807.99 | 11610.0961 | 719245.4522
2021-22 | -441.59 | -1739.34 | -615.6202 | Y | -38137.6689 |  | 2021-22 | 2107.49 | 20904.57 | 12929.8229 | 801002.5274
2022-23 | -297.29 | -2189.43 | -765.4697 | Y | -47420.8467 |  | 2022-23 | 2247.12 | 25346.47 | 14757.7974 | 914245.5514
|  |  |  | 10 | -453790.5846 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | -1.17 | -24.19 | 97.3942 | Y | 6033.5732 |  | 2013-14 | 767.65 | 9962.27 | 7811.2542 | 483907.1952
2014-15 | 15.24 | 98.1 | 186.9026 | Y | 11578.6185 |  | 2014-15 | 784.3 | 9715.31 | 7643.5338 | 473516.9164
2015-16 | 25.45 | 259.57 | 260.6906 | Y | 16149.7802 |  | 2015-16 | 799.96 | 9588.04 | 7626.531 | 472463.5979
2016-17 | 26.1 | 350.23 | 335.7184 | Y | 20797.7549 |  | 2016-17 | 826.79 | 9601.99 | 7612.6341 | 471602.6813
2017-18 | 93.27 | 494.57 | 446.3859 | Y | 27653.6077 |  | 2017-18 | 872.43 | 9753.07 | 7641.1067 | 473366.5613
2018-19 | 125.3 | 687.17 | 651.9942 | Y | 40391.0382 |  | 2018-19 | 881.08 | 9835.77 | 7643.1334 | 473492.1117
2019-20 | 83.37 | 713.56 | 647.6975 | Y | 40124.8614 |  | 2019-20 | 984.19 | 10331.18 | 7883.2366 | 488366.5098
2020-21 | 24.31 | 751.28 | 673.7038 | Y | 41735.9529 |  | 2020-21 | 1074.81 | 10783.33 | 8090.4434 | 501202.9662
2021-22 | -17.54 | 685.2 | 621.4116 | Y | 38496.4486 |  | 2021-22 | 1060.62 | 10805.64 | 7945.5394 | 492226.1634
2022-23 | -103.12 | 811.65 | 681.8182 | Y | 42238.635 |  | 2022-23 | 1187.24 | 11690.88 | 8256.3706 | 511482.1562
|  |  |  | 10 | 404199.7606 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 5.06 | -219.38 | -112.5649 | Y | -6973.3943 |  | 2013-14 | 761.42 | 10157.46 | 8021.2133 | 496914.1627
2014-15 | -2.5 | -153.78 | -88.7527 | Y | -5498.231 |  | 2014-15 | 797.23 | 10099.33 | 7975.6322 | 494090.4123
2015-16 | 0.19 | -173.35 | -103.8753 | Y | -6435.0736 |  | 2015-16 | 821.84 | 10307.72 | 8117.7212 | 502892.8283
2016-17 | 40.91 | -92.57 | -65.6487 | Y | -4066.9382 |  | 2016-17 | 870.03 | 10826.37 | 8465.5589 | 524441.3726
2017-18 | -20.3 | -132.62 | -74.4901 | Y | -4614.6605 |  | 2017-18 | 1013.87 | 11361.81 | 8774.1934 | 543561.2787
2018-19 | 14.57 | 23.77 | 101.0678 | Y | 6261.1477 |  | 2018-19 | 1085.15 | 11478.3 | 8869.6015 | 549471.8142
2019-20 | -37.02 | -262.74 | -123.185 | Y | -7631.3132 |  | 2019-20 | 1161.67 | 12361.28 | 9343.9112 | 578855.2988
2020-21 | -88.25 | -411.63 | -173.3196 | Y | -10737.1492 |  | 2020-21 | 1391.23 | 13133.7 | 9665.6434 | 598786.6062
2021-22 | -290.95 | -484.82 | -191.1219 | Y | -11840.0029 |  | 2021-22 | 1501.42 | 13802.45 | 9987.0963 | 618700.617
2022-23 | -188.03 | -328.67 | -106.0962 | Y | -6572.6571 |  | 2022-23 | 1591.75 | 15268.98 | 10608.8076 | 657215.6308
|  |  |  | 10 | -62896.5976 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 31.98 | -9.1 | 72.5269 | Y | 4493.0402 |  | 2013-14 | 766.19 | 10119.54 | 7906.8725 | 489830.7501
2014-15 | 34.88 | 27.59 | 161.403 | Y | 9998.9134 |  | 2014-15 | 729.07 | 9689.38 | 7511.0879 | 465311.8966
2015-16 | 30.49 | 390.48 | 461.4094 | Y | 28584.3099 |  | 2015-16 | 724.7 | 9426.76 | 7418.3476 | 459566.6338
2016-17 | 82.71 | 560.73 | 517.0838 | Y | 32033.3439 |  | 2016-17 | 717.95 | 9390.47 | 7395.1006 | 458126.4846
2017-18 | 155.19 | 740.04 | 649.8106 | Y | 40255.7642 |  | 2017-18 | 735.64 | 9567.53 | 7452.7758 | 461699.4583
2018-19 | 184.37 | 853.74 | 635.0568 | Y | 39341.7688 |  | 2018-19 | 809.03 | 10091.06 | 7694.8294 | 476694.6838
2019-20 | 163.6 | 1127.81 | 898.7077 | Y | 55674.9408 |  | 2019-20 | 909.28 | 11153.37 | 8103.9574 | 502040.1585
2020-21 | 86.8 | 1228.17 | 962.4233 | Y | 59622.1222 |  | 2020-21 | 1031.63 | 12422.11 | 8555.0296 | 529984.0837
2021-22 | 20.08 | 777.1 | 621.1542 | Y | 38480.5052 |  | 2021-22 | 1051.61 | 14061.12 | 9140.4626 | 566251.6605
2022-23 | 0.05 | 597.72 | 596.9962 | Y | 36983.9121 |  | 2022-23 | 1182.67 | 16612.17 | 10101.0413 | 625759.5073
|  |  |  | 10 | 353915.0452 | Residual

## Third_Line_MLTS-BATS
Stage 1: Installation of a new third Moorabool-Ballarat 220 kV line only
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 27.8 |  |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% |  |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 5.4372 | 0 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 33.2372 | 0 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 3.3988 | 0 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 33.2372 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 3.3988
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits Based on Year 1 ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 207.9 | 1121.89 | 575.3058 | 35.6402 | 3.3988 | 32.2414 | Y | 35.6402
2014-15 | 199.84 | 872.05 | 400.3042 | 24.7988 | 3.3988 | 21.4 | Y | 24.7988
2015-16 | 217.47 | 884.79 | 370.6421 | 22.9613 | 3.3988 | 19.5625 | Y | 22.9613
2016-17 | 243.06 | 959.59 | 447.4287 | 27.7182 | 3.3988 | 24.3194 | Y | 27.7182
2017-18 | 294.98 | 1065.14 | 448.6556 | 27.7942 | 3.3988 | 24.3954 | Y | 27.7942
2018-19 | 296.5 | 1239.25 | 454.6758 | 28.1672 | 3.3988 | 24.7684 | Y | 28.1672
2019-20 | 277.91 | 1338.25 | 567.7101 | 35.1696 | 3.3988 | 31.7708 | Y | 35.1696
2020-21 | 288.25 | 1387.94 | 592.2557 | 36.6902 | 3.3988 | 33.2914 | Y | 36.6902
2021-22 | 268.91 | 1601.31 | 569.0812 | 35.2546 | 3.3988 | 31.8558 | Y | 35.2546
2022-23 | 280.52 | 2004.76 | 594.056 | 36.8018 | 3.3988 | 33.403 | Y | 36.8018
[7 empty] | 10 | 346.9271 | Residual
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 136.831 | 434.538 | 444.6372 | 333.2139 | 262.3663 | 322.3173 | 33.2372 | 289.0801
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 153.79 | 973.84 | 532.5554 | Y | 32991.8095 |  | 2013-14 | 646 | 9268 | 7553 | 467908.35
2014-15 | 171.14 | 699.53 | 380.9285 | Y | 23598.5193 |  | 2014-15 | 679 | 9453 | 7604 | 471067.8
2015-16 | 187.06 | 451.36 | 273.7404 | Y | 16958.2178 |  | 2015-16 | 753 | 10009 | 7955 | 492812.25
2016-17 | 179.56 | 477.15 | 262.57 | Y | 16266.2115 |  | 2016-17 | 813 | 10229 | 8065 | 499626.75
2017-18 | 232.94 | 457.29 | 210.6301 | Y | 13048.5335 |  | 2017-18 | 897 | 10600 | 8249 | 511025.55
2018-19 | 193.81 | 212.32 | 121.9321 | Y | 7553.6924 |  | 2018-19 | 975 | 11505 | 8759 | 542620.05
2019-20 | 145.35 | 424.23 | 177.4515 | Y | 10993.1217 |  | 2019-20 | 1071 | 12685 | 9293 | 575701.35
2020-21 | -21.79 | 352.41 | 176.8208 | Y | 10954.0486 |  | 2020-21 | 1294 | 14120 | 9828 | 608844.6
2021-22 | 26.93 | 389.27 | 259.379 | Y | 16068.5315 |  | 2021-22 | 1282 | 15212 | 10006 | 619871.7
2022-23 | -121.72 | 116.52 | 132.9106 | Y | 8233.8092 |  | 2022-23 | 1555 | 17947 | 11164 | 691609.8
|  |  |  | 10 | 78792.8801 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 158.44 | 978.69 | 534.9413 | Y | 33139.6123 |  | 2013-14 | 645.54 | 9267.52 | 7552.6456 | 467886.3949
2014-15 | 175.13 | 872.05 | 448.882 | Y | 27808.2399 |  | 2014-15 | 676.01 | 9448.61 | 7600.4586 | 470848.4078
2015-16 | 184.68 | 884.79 | 443.526 | Y | 27476.4357 |  | 2015-16 | 754.66 | 9982.15 | 7945.3826 | 492216.4496
2016-17 | 217.22 | 959.59 | 498.6362 | Y | 30890.5101 |  | 2016-17 | 839.03 | 10736.49 | 8387.1281 | 519582.5846
2017-18 | 54.61 | 1065.14 | 522.5732 | Y | 32373.4097 |  | 2017-18 | 1100.99 | 11427.36 | 8788.0097 | 544417.1997
2018-19 | 233.08 | 1239.25 | 526.887 | Y | 32640.6521 |  | 2018-19 | 1150.33 | 12069.14 | 9281.0823 | 574963.0497
2019-20 | 103.74 | 1338.25 | 741.1029 | Y | 45911.3234 |  | 2019-20 | 1300.02 | 13339.72 | 9653.4743 | 598032.7341
2020-21 | -77.6 | 1387.94 | 806.0422 | Y | 49934.3168 |  | 2020-21 | 1519.11 | 15129.44 | 10310.0158 | 638705.4813
2021-22 | -171.88 | 1601.31 | 807.2227 | Y | 50007.4475 |  | 2021-22 | 1837.78 | 17563.92 | 11506.98 | 712857.411
2022-23 | -43.25 | 2004.76 | 923.3639 | Y | 57202.3948 |  | 2022-23 | 1993.08 | 21152.28 | 13068.9638 | 809622.3099
|  |  |  | 10 | 547394.4481 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 192.86 | 1078.68 | 695.2258 | Y | 43069.2358 |  | 2013-14 | 573.62 | 8859.4 | 7213.4226 | 446871.5325
2014-15 | 199.84 | 834.28 | 563.3481 | Y | 34899.4136 |  | 2014-15 | 599.7 | 8979.13 | 7267.0883 | 450196.1214
2015-16 | 217.47 | 704.53 | 505.6062 | Y | 31322.3066 |  | 2015-16 | 607.94 | 9143.08 | 7381.6154 | 457291.0716
2016-17 | 243.06 | 910.36 | 649.6941 | Y | 40248.5483 |  | 2016-17 | 609.83 | 9041.86 | 7298.6584 | 452151.8879
2017-18 | 294.98 | 970.65 | 701.2423 | Y | 43441.9617 |  | 2017-18 | 670.72 | 9276.99 | 7386.2503 | 457578.2073
2018-19 | 296.5 | 1025.25 | 782.861 | Y | 48498.2414 |  | 2018-19 | 709.88 | 9497.69 | 7512.2665 | 465384.9084
2019-20 | 277.91 | 1065.22 | 803.4822 | Y | 49775.7248 |  | 2019-20 | 789.65 | 9979.52 | 7727.4519 | 478715.6464
2020-21 | 288.25 | 1087.61 | 823.7773 | Y | 51033.0025 |  | 2020-21 | 810.87 | 10447 | 7940.3699 | 491905.9165
2021-22 | 268.91 | 984.27 | 731.6081 | Y | 45323.1206 |  | 2021-22 | 774.17 | 10506.57 | 7835.3429 | 485399.4914
2022-23 | 280.52 | 1107.44 | 802.933 | Y | 49741.7018 |  | 2022-23 | 803.6 | 11395.09 | 8135.2557 | 503979.0894
|  |  |  | 10 | 475999.851 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 150.11 | 858.68 | 465.085 | Y | 28812.0182 |  | 2013-14 | 616.37 | 9079.4 | 7443.5634 | 461128.7502
2014-15 | 159.86 | 726.07 | 369.5649 | Y | 22894.5443 |  | 2014-15 | 634.87 | 9219.48 | 7517.3146 | 465697.637
2015-16 | 158.56 | 756.72 | 387.4502 | Y | 24002.5424 |  | 2015-16 | 663.47 | 9377.65 | 7626.3957 | 472455.2124
2016-17 | 210 | 918.15 | 464.8313 | Y | 28796.2978 |  | 2016-17 | 700.94 | 9815.65 | 7935.0789 | 491578.1366
2017-18 | 52.06 | 802.76 | 433.5111 | Y | 26856.0139 |  | 2017-18 | 941.51 | 10426.43 | 8266.1922 | 512090.6043
2018-19 | 164.8 | 776.59 | 361.4817 | Y | 22393.7901 |  | 2018-19 | 934.92 | 10725.48 | 8609.1876 | 533339.1718
2019-20 | 120.08 | 1146.02 | 577.6386 | Y | 35784.7088 |  | 2019-20 | 1004.57 | 10952.52 | 8643.0876 | 535439.2768
2020-21 | 216.27 | 1216.14 | 611.9285 | Y | 37908.9693 |  | 2020-21 | 1086.71 | 11505.93 | 8880.3953 | 550140.4876
2021-22 | 104.39 | 1107.87 | 550.6315 | Y | 34111.6227 |  | 2021-22 | 1106.08 | 12209.76 | 9245.3429 | 572748.9914
2022-23 | 142.59 | 1295.75 | 675.6627 | Y | 41857.3055 |  | 2022-23 | 1261.13 | 13644.56 | 9827.0487 | 608785.6682
|  |  |  | 10 | 400550.6537 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 207.9 | 1121.89 | 648.7214 | Y | 40188.2883 |  | 2013-14 | 590.27 | 8988.55 | 7330.678 | 454135.5021
2014-15 | 125.18 | 478.66 | 238.7975 | Y | 14793.5064 |  | 2014-15 | 638.77 | 9238.31 | 7433.6934 | 460517.3037
2015-16 | 54.34 | 230.84 | 242.8878 | Y | 15046.8967 |  | 2015-16 | 700.85 | 9586.4 | 7636.8692 | 473104.0469
2016-17 | 73.89 | 375.36 | 361.4122 | Y | 22389.4833 |  | 2016-17 | 726.77 | 9575.84 | 7550.7723 | 467770.3452
2017-18 | 77.94 | 345.63 | 375.3214 | Y | 23251.1583 |  | 2017-18 | 812.89 | 9961.94 | 7727.265 | 478704.0643
2018-19 | 128.41 | 490.65 | 480.217 | Y | 29749.4407 |  | 2018-19 | 864.99 | 10454.15 | 7849.6693 | 486287.0119
2019-20 | 111.81 | 530.37 | 538.8751 | Y | 33383.3137 |  | 2019-20 | 961.07 | 11750.81 | 8463.7899 | 524331.7855
2020-21 | 108.95 | 527.53 | 542.7098 | Y | 33620.8696 |  | 2020-21 | 1009.48 | 13122.75 | 8974.7431 | 555985.3363
2021-22 | 89.29 | 481.03 | 496.5647 | Y | 30762.1844 |  | 2021-22 | 982.4 | 14357.19 | 9265.0522 | 573969.9813
2022-23 | 94.34 | 326.43 | 435.4097 | Y | 26973.6297 |  | 2022-23 | 1088.38 | 16883.46 | 10262.6278 | 635769.7897
|  |  |  | 10 | 258122.3246 | Residual

## WindMonitoring_BATS-BETS
Stage 1: Installation of wind monitoring facilities on Ballarat-Bendigo 220 kV line only
Types of Costs | Stage 1 | Stage 2 | Stage 3 |  | VCR ($k) | 61.95
Capital Cost ($M) | 0.6 |  |  |  | Discount Rate | 10%
Operational & Maintenance Cost (%) | 2% |  |  |  | Years | 40
Operational & Maintenance Cost in PV ($M) | 0.11735 | 0 | 0 |  | Scenario 1 | 20%
Project Cost ($M) | 0.71735 | 0 | 0 |  | Scenario 2 | 20%
Annualised Project Cost ($M) | 0.073356 | 0 | 0 |  | Scenario 3 | 20%
[5 empty] | Scenario 4 | 20%
Total Project Cost ($M) | 0.71735 |  |  |  | Scenario 5 | 20%
Annualised Total Project Cost ($M) | 0.073356
Weighted - Market Benefits
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Annualised Gross Market Benefits ($M) | Annualised Project Cost ($M) | Annualised Net Market Benefits Based on Year 1 ($M) | Year in Service | Annualised Gross Market Benefits Based on Year in Service ($M)
2013-14 | 35.34 | 74.41 | 32.3375 | 2.0033 | 0.073356 | 1.93 | Y | 2.0033
2014-15 | 30.07 | 83.6 | 60.5019 | 3.7481 | 0.073356 | 3.6747 | Y | 3.7481
2015-16 | 43.5 | 235.41 | 107.9529 | 6.6877 | 0.073356 | 6.6143 | Y | 6.6877
2016-17 | 40.4 | 276.59 | 156.9977 | 9.726 | 0.073356 | 9.6526 | Y | 9.726
2017-18 | 47.24 | 268.99 | 182.7203 | 11.3195 | 0.073356 | 11.2462 | Y | 11.3195
2018-19 | 40.64 | 289.89 | 236.6927 | 14.6631 | 0.073356 | 14.5898 | Y | 14.6631
2019-20 | 46.03 | 367.85 | 202.2215 | 12.5276 | 0.073356 | 12.4543 | Y | 12.5276
2020-21 | 50.39 | 429.75 | 225.8315 | 13.9903 | 0.073356 | 13.9169 | Y | 13.9903
2021-22 | 37.44 | 402.26 | 203.2852 | 12.5935 | 0.073356 | 12.5202 | Y | 12.5935
2022-23 | 40.08 | 704.76 | 257.7251 | 15.9661 | 0.073356 | 15.8927 | Y | 15.9661
[7 empty] | 10 | 150.5108 | Residual
| Scenario 1 ($M) | Scenario 2 ($M) | Scenario 3 ($M) | Scenario 4 ($M) | Scenario 5 ($M) | Weighted Gross Market Benefits ($M) | Total Project Cost ($M) | Net Market Benefits ($M)
Net Present Value (NPV) | 94.909 | 145.2829 | 90.8428 | 105.6274 | 139.5841 | 115.2492 | 0.71735 | 114.5319
Scenario 1 - Market Benefits | [6 empty] | Scenario 1 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 25.11 | 65.16 | 31.4179 | Y | 1946.3401 |  | 2013-14 | 774.68 | 10176.68 | 8054.1375 | 498953.8194
2014-15 | 20.79 | 72.14 | 56.6331 | Y | 3508.4218 |  | 2014-15 | 829.35 | 10080.39 | 7928.2954 | 491157.8976
2015-16 | 41.49 | 156.85 | 121.9874 | Y | 7557.117 |  | 2015-16 | 898.57 | 10303.51 | 8106.753 | 502213.3508
2016-17 | 30.36 | 140.79 | 147.1375 | Y | 9115.1694 |  | 2016-17 | 962.2 | 10565.36 | 8180.4325 | 506777.7921
2017-18 | 30.53 | 154.73 | 160.9174 | Y | 9968.8354 |  | 2017-18 | 1099.41 | 10902.56 | 8298.7126 | 514105.248
2018-19 | 15.64 | 210.29 | 215.8928 | Y | 13374.559 |  | 2018-19 | 1153.17 | 11507.03 | 8665.0393 | 536799.1834
2019-20 | 0.08 | 251.31 | 238.1974 | Y | 14756.3265 |  | 2019-20 | 1216.27 | 12857.92 | 9232.2542 | 571938.1452
2020-21 | 3.24 | 307.57 | 257.9661 | Y | 15980.9987 |  | 2020-21 | 1268.97 | 14164.84 | 9746.8547 | 603817.6499
2021-22 | 28.2 | 168.39 | 164.4994 | Y | 10190.7354 |  | 2021-22 | 1280.73 | 15432.88 | 10100.8797 | 625749.4962
2022-23 | 16.26 | 169.96 | 179.2377 | Y | 11103.7743 |  | 2022-23 | 1417.02 | 17893.56 | 11117.6729 | 688739.8349
|  |  |  | 10 | 106256.8168 | Residual
Scenario 2 - Market Benefits | [6 empty] | Scenario 2 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 21.87 | 73.73 | 34.7262 | Y | 2151.2856 |  | 2013-14 | 782.11 | 10172.48 | 8052.8607 | 498874.7216
2014-15 | 14.46 | 78.35 | 44.1346 | Y | 2734.1409 |  | 2014-15 | 836.68 | 10242.31 | 8005.2059 | 495922.5067
2015-16 | 13.66 | 78.68 | 57.6051 | Y | 3568.6372 |  | 2015-16 | 925.68 | 10788.26 | 8331.3034 | 516124.2481
2016-17 | 40.24 | 227.07 | 143.7031 | Y | 8902.4083 |  | 2016-17 | 1016.01 | 11469.01 | 8742.0611 | 541570.6864
2017-18 | -33.46 | 247.68 | 142.7371 | Y | 8842.5646 |  | 2017-18 | 1189.06 | 12244.82 | 9167.8458 | 567948.0448
2018-19 | 21.54 | 272.99 | 271.2013 | Y | 16800.9193 |  | 2018-19 | 1361.87 | 13035.4 | 9536.7681 | 590802.7826
2019-20 | 20.46 | 132.17 | 133.214 | Y | 8252.6073 |  | 2019-20 | 1383.3 | 14545.8 | 10261.3632 | 635691.4502
2020-21 | -8.1 | 240.47 | 187.2121 | Y | 11597.7884 |  | 2020-21 | 1449.61 | 16276.91 | 10928.846 | 677042.0097
2021-22 | -57 | 402.26 | 256.0513 | Y | 15862.3768 |  | 2021-22 | 1722.9 | 18762.97 | 12058.1514 | 747002.4817
2022-23 | -17.76 | 704.76 | 399.9259 | Y | 24775.4107 |  | 2022-23 | 1967.59 | 22452.28 | 13592.4018 | 842049.294
|  |  |  | 10 | 237086.6172 | Residual
Scenario 3 - Market Benefits | [6 empty] | Scenario 3 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 18.55 | 63.4 | 29.6092 | Y | 1834.2899 |  | 2013-14 | 747.93 | 9874.68 | 7879.0392 | 488106.4784
2014-15 | 30.07 | 70.54 | 49.9732 | Y | 3095.8397 |  | 2014-15 | 769.47 | 9742.87 | 7780.4632 | 481999.6952
2015-16 | 43.5 | 143.6 | 96.5295 | Y | 5980.0038 |  | 2015-16 | 781.91 | 9704.01 | 7790.6921 | 482633.3744
2016-17 | 40.4 | 144.59 | 134.5954 | Y | 8338.1875 |  | 2016-17 | 812.49 | 9807.63 | 7813.757 | 484062.2486
2017-18 | 23.54 | 195.66 | 166.0452 | Y | 10286.5001 |  | 2017-18 | 942.16 | 10051.98 | 7921.4474 | 490733.6689
2018-19 | 9.74 | 236.36 | 205.6873 | Y | 12742.327 |  | 2018-19 | 996.64 | 10286.58 | 8089.4402 | 501140.8229
2019-20 | 9.24 | 239.56 | 207.2169 | Y | 12837.0857 |  | 2019-20 | 1058.32 | 10805.18 | 8323.7173 | 515654.2855
2020-21 | 13.38 | 253.36 | 209.8739 | Y | 13001.6893 |  | 2020-21 | 1085.74 | 11281.25 | 8554.2733 | 529937.2297
2021-22 | 9.17 | 158.18 | 181.4542 | Y | 11241.0902 |  | 2021-22 | 1033.91 | 11332.66 | 8385.4967 | 519481.5218
2022-23 | 7.41 | 163.3 | 179.9553 | Y | 11148.2296 |  | 2022-23 | 1076.71 | 12339.23 | 8758.2334 | 542572.5616
|  |  |  | 10 | 106682.229 | Residual
Scenario 4 - Market Benefits | [6 empty] | Scenario 4 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 18.55 | 63.4 | 29.6092 | Y | 1834.2899 |  | 2013-14 | 747.93 | 9874.68 | 7879.0392 | 488106.4784
2014-15 | 18.53 | 78.88 | 40.1476 | Y | 2487.1438 |  | 2014-15 | 776.2 | 9866.67 | 7846.7318 | 486105.0375
2015-16 | 16.96 | 71.28 | 42.0689 | Y | 2606.1671 |  | 2015-16 | 805.07 | 10063.09 | 7971.777 | 493851.5876
2016-17 | 39.96 | 200.28 | 129.8518 | Y | 8044.3165 |  | 2016-17 | 870.98 | 10533.52 | 8270.0584 | 512330.1179
2017-18 | -2.29 | 242.73 | 162.3142 | Y | 10055.3622 |  | 2017-18 | 995.86 | 10986.46 | 8537.3891 | 528891.256
2018-19 | -25.43 | 245.03 | 241.1394 | Y | 14938.5834 |  | 2018-19 | 1125.15 | 11257.04 | 8729.5299 | 540794.3785
2019-20 | -9.24 | 76.12 | 128.8698 | Y | 7983.4866 |  | 2019-20 | 1133.89 | 12022.42 | 9091.8563 | 563240.499
2020-21 | 16.96 | 127.75 | 138.9278 | Y | 8606.5747 |  | 2020-21 | 1286.02 | 12594.32 | 9353.396 | 579442.8822
2021-22 | -10.46 | 219.67 | 156.1113 | Y | 9671.0938 |  | 2021-22 | 1220.93 | 13097.96 | 9639.8631 | 597189.5203
2022-23 | -0.03 | 458.4 | 267.6334 | Y | 16579.8867 |  | 2022-23 | 1403.75 | 14481.91 | 10235.0781 | 634063.0871
|  |  |  | 10 | 158660.1038 | Residual
Scenario 5 - Market Benefits | [6 empty] | Scenario 5 - Limitation
Year | Maximum Load at risk reduction (MW) | Maximum Energy at risk reduction (MWh) | Expected unserved energy reduction (MWh) | Year in Service | Limitation cost ($ '000) |  | Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 35.34 | 74.41 | 36.3249 | Y | 2250.3263 |  | 2013-14 | 762.83 | 10036.03 | 7943.0745 | 492073.464
2014-15 | 8.63 | 83.6 | 111.621 | Y | 6914.9185 |  | 2014-15 | 755.32 | 9633.37 | 7560.8699 | 468395.8915
2015-16 | 4.14 | 235.41 | 221.5735 | Y | 13726.4796 |  | 2015-16 | 751.05 | 9581.83 | 7658.1834 | 474424.4641
2016-17 | 32.92 | 276.59 | 229.7005 | Y | 14229.9447 |  | 2016-17 | 767.74 | 9674.61 | 7682.484 | 475929.8838
2017-18 | 47.24 | 268.99 | 281.5876 | Y | 17444.3518 |  | 2017-18 | 843.59 | 10038.58 | 7820.9987 | 484510.8707
2018-19 | 40.64 | 289.89 | 249.5429 | Y | 15459.1814 |  | 2018-19 | 952.76 | 10654.91 | 8080.3434 | 500577.2712
2019-20 | 46.03 | 367.85 | 303.6092 | Y | 18808.5899 |  | 2019-20 | 1026.85 | 11913.33 | 8699.0558 | 538906.5093
2020-21 | 50.39 | 429.75 | 335.1775 | Y | 20764.2474 |  | 2020-21 | 1068.04 | 13220.53 | 9182.2754 | 568841.9586
2021-22 | 37.44 | 252.54 | 258.3098 | Y | 16002.2946 |  | 2021-22 | 1034.25 | 14585.68 | 9503.307 | 588729.8711
2022-23 | 40.08 | 302.13 | 261.8734 | Y | 16223.0547 |  | 2022-23 | 1142.64 | 16907.76 | 10436.1641 | 646520.3648
|  |  |  | 10 | 155245.4241 | Residual

## Base
Existing Limitation: Includes all relevant contraints
VCR ($k) | 61.95
Discount Rate | 10%
Years | 40
Scenario 1 | 20%
Scenario 2 | 20%
Scenario 3 | 20%
Scenario 4 | 20%
Scenario 5 | 20%
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2013-14 | 803.98 | 10246.21 | 7993.9677 | 495.2263
2014-15 | 851.14 | 10320.66 | 7884.8152 | 488.4643
2015-16 | 940.06 | 10866.94 | 8079.6947 | 500.5371
2016-17 | 1056.25 | 11696.08 | 8294.7563 | 513.8602
2017-18 | 1155.6 | 12492.5 | 8531.999 | 528.5573
2018-19 | 1383.41 | 13308.39 | 8856.9169 | 548.686
2019-20 | 1403.76 | 14677.97 | 9323.8708 | 577.6138
2020-21 | 1441.51 | 16517.38 | 9778.9605 | 605.8066
2021-22 | 1665.9 | 19165.23 | 10140.8248 | 628.2241
2022-23 | 1949.83 | 23157.04 | 11085.6352 | 686.7551
Scenario 1 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 799.79 | 10241.84 | 8085.5554 | 500900.1595
2014-15 | 850.14 | 10152.53 | 7984.9285 | 494666.3193
2015-16 | 940.06 | 10460.36 | 8228.7404 | 509770.4678
2016-17 | 992.56 | 10706.15 | 8327.57 | 515892.9615
2017-18 | 1129.94 | 11057.29 | 8459.6301 | 524074.0835
2018-19 | 1168.81 | 11717.32 | 8880.9321 | 550173.7424
2019-20 | 1216.35 | 13109.23 | 9470.4515 | 586694.4717
2020-21 | 1272.21 | 14472.41 | 10004.8208 | 619798.6486
2021-22 | 1308.93 | 15601.27 | 10265.379 | 635940.2315
2022-23 | 1433.28 | 18063.52 | 11296.9106 | 699843.6092
Scenario 2 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 803.98 | 10246.21 | 8087.5869 | 501026.0072
2014-15 | 851.14 | 10320.66 | 8049.3406 | 498656.6477
2015-16 | 939.34 | 10866.94 | 8388.9086 | 519692.8853
2016-17 | 1056.25 | 11696.08 | 8885.7642 | 550473.0947
2017-18 | 1155.6 | 12492.5 | 9310.5829 | 576790.6094
2018-19 | 1383.41 | 13308.39 | 9807.9694 | 607603.7019
2019-20 | 1403.76 | 14677.97 | 10394.5772 | 643944.0575
2020-21 | 1441.51 | 16517.38 | 11116.0581 | 688639.7981
2021-22 | 1665.9 | 19165.23 | 12314.2027 | 762864.8585
2022-23 | 1949.83 | 23157.04 | 13992.3278 | 866824.7047
Scenario 3 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 766.48 | 9938.08 | 7908.6484 | 489940.7684
2014-15 | 799.54 | 9813.41 | 7830.4364 | 485095.535
2015-16 | 825.41 | 9847.61 | 7887.2216 | 488613.3781
2016-17 | 852.89 | 9952.22 | 7948.3525 | 492400.4361
2017-18 | 965.7 | 10247.64 | 8087.4926 | 501020.169
2018-19 | 1006.38 | 10522.94 | 8295.1275 | 513883.1499
2019-20 | 1067.56 | 11044.74 | 8530.9342 | 528491.3712
2020-21 | 1099.12 | 11534.61 | 8764.1472 | 542938.919
2021-22 | 1043.08 | 11490.84 | 8566.951 | 530722.612
2022-23 | 1084.12 | 12502.53 | 8938.1887 | 553720.7912
Scenario 4 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 766.48 | 9938.08 | 7908.6484 | 489940.7684
2014-15 | 794.73 | 9945.55 | 7886.8794 | 488592.1813
2015-16 | 822.03 | 10134.37 | 8013.8459 | 496457.7547
2016-17 | 910.94 | 10733.8 | 8399.9102 | 520374.4344
2017-18 | 993.57 | 11229.19 | 8699.7033 | 538946.6182
2018-19 | 1099.72 | 11502.07 | 8970.6693 | 555732.9619
2019-20 | 1124.65 | 12098.54 | 9220.7262 | 571223.9856
2020-21 | 1302.98 | 12722.07 | 9492.3238 | 588049.4569
2021-22 | 1210.47 | 13317.63 | 9795.9744 | 606860.6141
2022-23 | 1403.72 | 14940.31 | 10502.7114 | 650642.9737
Scenario 5 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 798.17 | 10110.44 | 7979.3994 | 494323.7904
2014-15 | 763.95 | 9716.97 | 7672.4909 | 475310.81
2015-16 | 755.19 | 9817.24 | 7879.757 | 488150.9437
2016-17 | 800.66 | 9951.2 | 7912.1845 | 490159.8285
2017-18 | 890.83 | 10307.57 | 8102.5863 | 501955.2225
2018-19 | 993.4 | 10944.8 | 8329.8862 | 516036.4526
2019-20 | 1072.88 | 12281.18 | 9002.665 | 557715.0992
2020-21 | 1118.43 | 13650.28 | 9517.4529 | 589606.2059
2021-22 | 1071.69 | 14838.22 | 9761.6169 | 604732.1657
2022-23 | 1182.72 | 17209.89 | 10698.0374 | 662743.4194

## Base_Unconstraint
Limitation: Unconstrained on Ballarat-Bendigo 220 kV line and Moorabool-Ballarat No.1 220 kV line but includes all other relevant constraints
VCR ($k) | 61.95
Discount Rate | 10%
Years | 40
Scenario 1 | 20%
Scenario 2 | 20%
Scenario 3 | 20%
Scenario 4 | 20%
Scenario 5 | 20%
Weighted - Market Benefits
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($M)
2013-14 | 552.93 | 8766.41 | 7424.3 | 459.9354
2014-15 | 601.99 | 8933.68 | 7298.9651 | 452.1709
2015-16 | 667.9 | 9328.92 | 7463.3884 | 462.3569
2016-17 | 751.47 | 9659.37 | 7543.2763 | 467.306
2017-18 | 1061 | 10366.07 | 7717.5196 | 478.1003
2018-19 | 1103.45 | 10929.8 | 8032.3922 | 497.6067
2019-20 | 1325.58 | 12312.18 | 8369.8576 | 518.5127
2020-21 | 1282.93 | 13541.26 | 8717.1927 | 540.0301
2021-22 | 1546.13 | 15714.17 | 9146.252 | 566.6103
2022-23 | 1736.21 | 18335.35 | 9846.0198 | 609.9609
Scenario 1 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 552.93 | 8766.41 | 7453.5 | 461744.325
2014-15 | 600.73 | 8930.42 | 7327.7338 | 453953.1114
2015-16 | 662.25 | 9319.49 | 7558.6796 | 468260.2012
2016-17 | 697.22 | 9473.92 | 7580.9322 | 469638.7523
2017-18 | 798.57 | 9831.2 | 7704.231 | 477277.108
2018-19 | 923.07 | 10650.4 | 8136.8865 | 504080.1174
2019-20 | 1046.82 | 11856.52 | 8609.6313 | 533366.6578
2020-21 | 1091 | 13066.45 | 9042.4634 | 560180.6052
2021-22 | 1023.93 | 14354.52 | 9482.3321 | 587430.4724
2022-23 | 1228.45 | 16738.88 | 10443.1981 | 646956.1211
Scenario 2 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 552.93 | 8766.41 | 7372.5 | 456726.375
2014-15 | 601.99 | 8933.68 | 7328.2655 | 453986.049
2015-16 | 667.9 | 9328.92 | 7558.6231 | 468256.7023
2016-17 | 751.47 | 9659.37 | 7748.7526 | 480035.2211
2017-18 | 1061 | 10366.07 | 8075.0816 | 500251.3051
2018-19 | 1103.45 | 10929.8 | 8424.3114 | 521886.0888
2019-20 | 1325.58 | 12312.18 | 8880.378 | 550139.4171
2020-21 | 1282.93 | 13541.26 | 9345.0899 | 578928.3205
2021-22 | 1546.13 | 15714.17 | 10430.3677 | 646161.2778
2022-23 | 1736.21 | 18335.35 | 11450.8173 | 709378.1305
Scenario 3 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 523.51 | 8619.28 | 7356.6 | 455741.37
2014-15 | 546.66 | 8755.49 | 7261.9854 | 449879.9931
2015-16 | 566.93 | 8867.14 | 7331.409 | 454180.79
2016-17 | 576.21 | 8917.98 | 7337.7468 | 454573.4143
2017-18 | 661.15 | 9157.32 | 7440.3506 | 460929.7221
2018-19 | 741.15 | 9524.17 | 7653.0018 | 474103.464
2019-20 | 782.97 | 9911.63 | 7822.231 | 484587.2129
2020-21 | 828.43 | 10377.29 | 8038.9875 | 498015.2769
2021-22 | 758.18 | 10551.74 | 7975.6213 | 494089.7383
2022-23 | 784.75 | 11385.88 | 8248.6948 | 511006.6429
Scenario 4 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 523.51 | 8619.28 | 7299.6 | 452210.22
2014-15 | 546.66 | 8755.12 | 7264.3158 | 450024.3663
2015-16 | 562.4 | 8861.67 | 7328.3542 | 453991.5402
2016-17 | 617.66 | 9068.5 | 7472.4467 | 462918.0743
2017-18 | 922.7 | 9610.98 | 7713.4891 | 477850.651
2018-19 | 981.29 | 10011.06 | 7973.9654 | 493987.159
2019-20 | 981.39 | 10259.6 | 8066.6223 | 499727.2527
2020-21 | 1004.84 | 10670.24 | 8233.899 | 510090.0406
2021-22 | 980.96 | 11127.6 | 8449.8722 | 523469.5853
2022-23 | 1073.45 | 12153.07 | 8808.0383 | 545657.9739
Scenario 5 - Limitation
Year | Maximum Load at risk (MW) | Maximum Energy at risk (MWh) | Expected unserved energy (MWh) | Limitation cost ($ '000)
2013-14 | 552.93 | 8766.41 | 7639.3 | 473254.635
2014-15 | 578.25 | 8880.39 | 7312.5247 | 453010.9064
2015-16 | 641.08 | 9259.88 | 7539.8761 | 467095.3232
2016-17 | 693.14 | 9446.37 | 7576.5034 | 469364.3832
2017-18 | 775.63 | 9756.86 | 7654.4458 | 474192.9198
2018-19 | 874.64 | 10427.37 | 7973.796 | 493976.6622
2019-20 | 932.94 | 11566.47 | 8470.4254 | 524742.8511
2020-21 | 971.26 | 12839.25 | 8925.5237 | 552936.192
2021-22 | 975.34 | 14321.93 | 9393.0668 | 581900.4883
2022-23 | 1075.67 | 16570.78 | 10279.3506 | 636805.7721