## Index
The National Electricity Market Constraint Report 2014
Electronic Material – supplementary data
This supplement provides:
* Binding constraint equations (energy and FCAS separately)
* Market Impact of constraint equations
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page

## Binding 2014
Constraint Equation ID | 2014 Hours (2013 Hours) | Description | Type | Region
N_X_MBTE_3A & N_X_MBTE_3B | 1,662 (3,773) | Out = all three Directlink cables | Outage | NSW
Q>NIL_BI_FB | 1,063 (493) | Out = Nil, avoid overloading on Boyne Island feeder bushing on Calliope River to Boyne Island 132 kV lines, for the contingent loss of a single Calliope River to Boyne Island 132 kV line | NIL | Qld
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 844 (202) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. | NIL | Vic
N_MBTE1_B | 834 (1) | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
Q:N_NIL_AR_2L-G | 800 (0) | Out = Nil, avoid transient instability for a 2 line to Ground fault at Armidale | NIL | Qld
N_X_MBTE2_A & N_X_MBTE2_B | 580 (196) | Out = two Directlink cables | Outage | NSW
S>>V_NIL_SETX_SETX | 517 (456) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer This constraint equation binds when there is export from South Australia to Victoria and high generation from the wind farms and gas turbines in the south east of South Australia. | NIL | SA
T_TAMARCCGT_GCS | 504 (358) | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) | NIL | Tas
V>S_NIL_HYTX_HYTX | 474 (992) | Out = Nil, avoid overloading the remaining Heywood 275/500 kV transformer on trip of one Heywood 275/500 kV transformer With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
Q:N_AR_2L-G_-200 | 430 (0) | Out = Bulli Creek CBs (8L2 and 99012) or (8M2 and 99022) | Outage | Qld
V_T_NIL_FCSPS | 335 (1) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
V::N_NIL_xxx | 317 (11) | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
V>>S_NIL_SETB_SGKH | 288 (652) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line This will bind for high import into SA with high levels of generation from the wind farms and gas turbines in the south east. | NIL | SA
S>V_NIL_NIL_RBNW | 242 (52) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink. | NIL | SA
N^^V_NIL_1 | 210 (104) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
S>>NIL_SETB_KHTB1 | 197 (27) | Out = Nil, avoid overloading Keith - Tailem Bend #1 132kV on trip of South East - Tailem Bend 275kV line | NIL | SA
V^^S_NIL_MAXG_xxx | 179 (209) | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off There are two constraint equations that make up the voltage stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
SVML_ZERO | 170 (175) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
Q>NIL_TR_TX1_4 | 165 (121) | Out = Nil, avoid overloading a Tarong 275/132 kV transformer ( No.1 or No.4) on trip of the other Tarong 275/132 kV transformer (No.1 or No.4) | NIL | Qld
V_T_NIL_BL1 | 164 (9) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
V>S_460 | 159 (301) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
S>>V_NIL_RBTX_MW4RB | 135 (0) | Out= Nil, avoid O/L Morgan Whyalla 4 to Robertstown line on trip of one Robertstown 275/132kV transformer, Feedback | NIL | SA
T_MRWF_QLIM_xx | 133 (217) | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 133 (1) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
N^N_KKLS_1 | 110 (82) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
T>T_NIL_110_1 | 104 (189) | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
V>>V-MSUT_1 | 90 (43) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | Outage | Vic
T^V_NIL_BL_6 | 87 (133) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 72 (531) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
NSA_Q_GSTONE34_xxx | 69 (284) | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
V>>S_NIL_PWKN_SGKH | 69 (41) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL | SA
V^SML_NSWRB_2 | 65 (54) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
#GULLRWF1_E | 64 (0) | NGUR1G.ENERGY * 1 <= 166 (Wt = 360) | Outage | Quick
V>V_NIL_GGMS_1 | 60 (35) | Out = Nil, avoid overloading Guthega to Murray (97G/3) 132 kV line | NIL | Vic
NC_V_YWPS1 | 56 (43) | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Outage | Non-Conformance
NC_V_YWPS1 | 56 (43) | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Vic
S>NIL_NIL_MYSG-T | 55 (55) | Out = Nil, avoid overloading Mayura to Snuggery 132 kV line on no line trips | NIL | SA
T^V_NIL_8 | 54 (16) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
NSA_Q_BARCALDN | 54 (30) | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
Q:N_ARSVC_AR_2L-G | 52 (0) | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
V>V_NIL_RADIAL_9 | 52 (0) | Out = Nil, avoid O/L of Hazelwood to Jeeralang No. 4 220 kV line for trip of Hazelwood A4 500/220 kV transformer, Yallourn unit 1 in 500kV mode, radial mode, Hazelwood 3,4 busses split, feedback. | NIL | Vic
S>>NIL_SETB_KHTB2 | 51 (19) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
VSML_ZERO | 47 (424) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
T_V_NIL_BL1 | 46 (5) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
S_LB3_0 | 46 (156) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
V>>SML_NIL_8 | 44 (29) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V>>SML_NIL_7A | 43 (72) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line This constraint equation only binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for high flows on Murraylink into SA. | NIL | Vic
NC_V_APS | 42 (96) | Non Conformance constraint equation for Anglesea Power Station | Outage | Non-Conformance
NC_V_YWPS2 | 37 (32) | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Outage | Non-Conformance
V>>S_NIL_KHTB2_KHTB1 | 36 (3) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV one trip of Keith - Tailem Bend #2 132kV line, Feedback | NIL | SA
V::N_HWSM_xxx | 31 (8) | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
V>>SML_NIL_7B | 31 (21) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
NC_V_YWPS3 | 30 (19) | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Outage | Non-Conformance
T_PMPO_110 | 29 (0) | Out=A single Palmerston-Poatina 110KV line. One line out of service only | Outage | Tas
V>>SML_NIL_1 | 29 (13) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
NC_V_YWPS4 | 27 (25) | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Outage | Non-Conformance
NC_N_MP2 | 24 (4) | Non Conformance Constraint for Mt Piper 2 Power Station | Outage | Non-Conformance
NSA_S_PORxxx | 24 (20) | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
V>SMLBAHO1 | 23 (6) | Out = Ballarat to Horsham, or Bendigo to Kerang line, avoid overloading or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang or Ballarat to Horsham line | Outage | Vic
#MERCER01_E | 23 (0) | VELT1M.ENERGY * 1 <= 50 (Wt = 360) | Outage | Quick
V>>V_NIL1A_R | 23 (30) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line This constraint equation only binds for high flows from Victoria to NSW | NIL | Vic
I_CTRL_ISSUE_TE | 23 (4) | DC Link Control Issue Constraint for Terranora | Outage | Other
V>>V_MLTS_TX_2A_R | 23 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage | Vic
Q:N_AR_2L-G_-150 | 21 (0) | Nominated Offset -150MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | Outage | Qld
V^S_HYCP | 21 (0) | Out = Nil, limit Vic to SA to avoid voltage collapse in Heywood area for loss of a 500 kV circuit between Moorabool and Heywood with automatic allowance for Heywood 275 kV capacitor bank status | NIL | Vic
V::N_MSUT_xxx | 21 (17) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
Q>N-MUTE_758 | 21 (0) | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
V>>S_HYML_1 | 20 (90) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 1 | Outage | SA
T>T_FASH_1_2_C1 | 18 (11) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hampshire link closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
S>NIL_WERB_WEWT | 17 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
Q>N-MUTE_757 | 16 (0) | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
T::T_NIL_4 | 16 (0) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
V>V_NIL_7 | 16 (2) | Out = Nil, avoid overloading either of Mount Beauty - Dederang 220 kV line for trip of Eildon - Thomastown 220 kV line | NIL | Vic
V>>V_MLTS_TX_2B_R | 16 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood | Outage | Vic
T>T_LIPM_110_2A | 16 (0) | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
V>V_NIL_ROYP56_R2_1 | 16 (0) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 220 kV, feedback | NIL | Vic
T>T_HAGT_N-2 | 15 (14) | Out=NIL, Loss of both Hadspen to George Town 220kV lines or Palmerston to Hadspen 220kV lines declared credible, Restrict the power flow on HA-GT corridor based on AETV CCGT service status | Outage | Tas
T>T_NIL_LIPM_N-2_2A | 14 (14) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to North) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
V>>V_NIL_5 | 14 (6) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
NC_N_HUMENSW | 14 (1) | Non Conformance Constraint for Hume Hydro Power Station | Outage | Non-Conformance
V::N_MLTX_xxx | 14 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
T>>T_NIL_BL_EXP_6E | 13 (73) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
T>TU_LE_WA1_TUO_2 | 13 (0) | Out = Tungatinah to Lake Echo to Waddamana No. 1 110kV line open at Tungatinah only (i.e. TU CB G152 OPEN), avoid O/L Tungatinah to Waddamana No.2 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
I_CTRL_ISSUE_ML | 13 (0) | DC Link Control Issue Constraint for Murraylink | Outage | Other
V>>V_KTS_TX_A2_2A_R | 13 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
V>>V_NIL_1B | 12 (15) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
TVBL_ROC | 12 (13) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
T>T_NIL_BL_3C | 12 (136) | Out = Nil, avoid overloading a Hadspen to Palmerston 220 kV line for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action | NIL | Tas
T>T_NIL_BL_IMP_5F | 12 (327) | Out = Nil, avoid overloading Hadspen to Georgetown No.1 220 kV line (flow to North) for trip of the Hadspen to Georgetown No.2 220 kV line with no SPS action This constraint only binds when the NCSPS control scheme is unavailable. | NIL | Tas
S^NIL_PL_MAX | 12 (4) | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
T_TA_60 | 11 (0) | Discretionary 60 MW upper limit on total Tarraleah generation | Outage | Tas
N>N-LSTN_TE_C1 | 11 (1) | Out = Lismore to Tenterfield (96L) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
NC_N_REDBANK1 | 11 (21) | Non Conformance Constraint for Redbank Power Station | Outage | Non-Conformance
NC_T_POAT110 | 11 (11) | Non Conformance Constraint for Poatina 110kV Power Station | Outage | Non-Conformance
V^^S_RBTU2_MAXG | 11 (0) | Out= Robertstown - Para and Robertstown - Tungkillo 275 kV lines; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
S_BRBG_CM | 11 (0) | Out = Brinkworth to Redhill to Bungama 132kV lines. | Outage | SA
V>>V_LTMS_1 | 11 (0) | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage | Vic
N_WOODLWN1_ZERO | 11 (1) | Discretionary upper limit for Woodlawn generation of 0 MW | Outage | NSW
NRM_QLD1_NSW1 | 10 (30) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V::S_HYSE | 10 (3) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of one NPS unit or the remaining South East - Heywood 275 kV line. | Outage | SA
VTBL_ROC | 10 (15) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
V:T_SHGT_BL_1 | 10 (0) | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
NSA_V_BDL0xxx | 10 (7) | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
T_T_FASH_7_N-2 | 10 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, Hampshire link open, limit all West Coast generation <= 110% of West Coast load | Outage | Tas
V>>V_KTS_TX_A3_2B_R | 10 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Vic
S_LB2WF_CONF | 9 (5) | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
T>T_NIL_TOV_5F | 9 (0) | Out = Nil, avoid TOV following NCSPS slow action for O/L of Hadspen to Georgetown No. 1 220 kV lines (flow to North) for trip of the Hadspen to Georgetown No. 2 220 kV line, considering status of Tamar CCGT, feedback equation | NIL | Tas
T>T_NIL_LIPM_N-2_2B | 9 (1) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
V>>V_ROTS_TX_2B_R | 9 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
V::N_DDSM_xxx | 9 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
T>T_PM_TX_1A | 9 (0) | Out= Palmerston 220/110kV transformer, prevent overload of either Palmerston to Hadspen 110kV line (flow to North) for trip of the parallel Palmerston to Hadspen 110 kV line, feedback | Outage | Tas
N^^Q_AR_VC_B1 | 9 (1) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V::N_JNWO_xxx | 8 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
N>N-X_9U6_9G2_2 | 8 (0) | Out = one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5), avoid O/L remaining 132kV line, Qld to NSW limit | Outage | NSW
N>Q_LSLS_9U8 | 8 (4) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage | NSW
V>>S_HYML_2 | 8 (58) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 2 | Outage | SA
V>V_NIL_RADIAL_10 | 8 (0) | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Vic
T>>T_NIL_BL_EXP_5F | 7 (43) | Out = Nil, avoid overloading a Hadspen to George Town 220 kV line for trip of the other Hadspen to George Town 220 kV line considering NCSPS action | NIL | Tas
V>SMLBAHO4 | 7 (42) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage | Vic
NC_N_TALWA1 | 7 (7) | Non Conformance Constraint for Tallawarra Power Station | Outage | Non-Conformance
#NSW1-QLD1_RAMP_I_F | 7 (1) | NSW1-QLD1 >= MIN(-424, InitialFlow + 200) (Wt=35) | Outage | Quick
N^^V_MSUT_1 | 7 (2) | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
N^Q_TW_330_BUS3_1 | 7 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage | NSW
#SNOWNTH1_E | 6 (4) | SBLWS1.ENERGY * 1 <= 144 (Wt = 360) | Outage | Quick
N^Q_AR_330_BS1_1 | 6 (0) | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage | NSW
V>SML_BUDP_2 | 6 (13) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
N>LSDU9U6_LSDU9U7 | 6 (1) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
Q:N_30+38+KCTX_AR | 6 (0) | Out= Liverpool-SydneyWest & Regentville-SydneyWest & one KempsCreek Tie Tx (30+38+KCTX), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
NC_N_SITHE01 | 6 (61) | Non Conformance Constraint for Smithfield Energy Facility | Outage | Non-Conformance
T>T_NIL_BL_IMP_7CC | 6 (0) | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V::N_SMCSV_xxx | 6 (0) | Out = South Morang 330kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
NC_N_VP6 | 6 (10) | Non Conformance Constraint for Vales Point VP6 Power Station | Outage | Non-Conformance
T>T_GT_HA_3A_N-2 | 6 (12) | Out = NIL, Loss of both Hadspen to Georgetown 220kV lines declared credible, avoid O/L the Sheffield to Palmerston 220 kV line (flow to North) for loss of both Hadspen to Georgetown 220 kV lines | Outage | Tas
T>T_TUBUS_TATU1_1 | 6 (0) | Out = Tungatinah 110 kV bus section and Tarraleah to Tungatinah No. 1 110 kV line, avoid O/L Tungatinah to New Norfolk No. 1 110 kV line on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
V::N_LTWG_xxx | 6 (2) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
#MM4_E | 5 (0) | NMNP4.ENERGY * 1 <= 0 (Wt = 360) | Outage | Quick
N_GUNNING1_ZERO | 5 (6) | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
V>>SML_BESH_1 | 5 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Waubra to Horsham 220 kV line section for trip of the Ballarat to Bendigo 220 kV line, feedback | Outage | Vic
S-SNWWF_0 | 5 (0) | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
V>>V_NIL_3 | 5 (1) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL | Vic
V>>V_EPTT_3 | 5 (0) | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to North) for loss of the parallel line, feedback | Outage | Vic
NC_V_MOR1 | 5 (0) | Non Conformance Constraint for MOR1 Energy Brix Power Station | Outage | Non-Conformance
NQTE_ROC | 5 (17) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
N^^V_NIL_2 | 5 (24) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL | NSW
N>Q-MUTW_2 | 5 (2) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage | NSW
V>>N-NIL_HA | 5 (3) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL | Vic
N>>N-NIL__3_OPENED & CLOSED | 5 (0) | Out= NIL, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
N^Q_NIL_A | 5 (33) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
V>>V_KTS_TX_A2_2_P | 5 (1) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage | Vic
VT_ZERO | 5 (8) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
NC_N_VP5 | 4 (4) | Non Conformance Constraint for Vales Point VP5 Power Station | Outage | Non-Conformance
T_T_FASH_1_N-2 | 4 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
T_T_FASH_3_N-2 | 4 (0) | Out = Nil, loss of both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link open, constrain Reece Unit 1 to 0 MW as per Transend advice | Outage | Tas
V>>N_SMHTX_2 | 4 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
VN_0700 | 4 (0) | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
NC_N_MP1 | 4 (0) | Non Conformance Constraint for Mt Piper 1 Power Station | Outage | Non-Conformance
S>NIL_BWPA_HUWT | 4 (2) | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West - Para 275kV line, Feedback | NIL | SA
V>>V_CBTS_TX_2B_R | 4 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage | Vic
QNTE_ROC | 4 (12) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
S>RBTU2_DVBG_WEWT | 4 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines; avoid O/L Waterloo East-Waterloo 132kV line on trip of Davenport - Bungama 275KV line. | Outage | SA
V>>N-X_MSUT_LTUT_B | 4 (0) | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid O/L DDTS to WOTS 330kV line on trip of Lower Tumut to Murray (66) line, Feedback | Outage | Vic
NC_S_OSB-AG | 4 (1) | Non Conformance Constraint for Osborne Power Station | Outage | Non-Conformance
T>T_MBTU_110_1 | 4 (0) | Out = Tungatinah to Meadowbank 110 kV line, avoid O/L Tungatinah to New Norfolk No. 2 110 kV line (flow to South) on trip of Tungatinah to New Norfolk No. 1 110 kV line, feedback | Outage | Tas
T>T_X_TU_LE_WA_TWO | 4 (0) | Out = Both Tungatinah to Waddamana 110kV lines open (direct and via Lake Echo tee), avoid O/L New Norfolk to Creek Rd line for loss of New Norfolk to Chapel St line , feedback | Outage | Tas
CA_SPS_42375E8A_01 | 4 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LHPA on trip of LTSS-MSS (66) 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
V::N_ROSM_xxx | 4 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
Q:N_NIL_BI_POT | 3 (0) | Out = Nil, avoid transient instability for a trip of a Boyne Island potline (400 MW) For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_OSC or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
V^^S_PAVC_MAXG | 3 (36) | Out = Para one SVC, VIC to SA Voltage Stability limit for loss of the largest generation unit in SA | Outage | SA
CA_MQS_42D83B89_01 | 3 (0) | Constraint Automation, O/L 275KV_8859 @H58_LARC for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage | Constraint Automation
NC_Q_TNPS1 | 3 (3) | Non Conformance Constraint for Tarong North Power Station | Outage | Non-Conformance
NC_T_BLNKTAS | 3 (2) | Non Conformance Constraint for Basslink from Tas to Vic | Outage | Non-Conformance
Q:N_BI_POT_-050 | 3 (0) | Nominated Offset -50MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage | Qld
T>T_NIL_BL_IMP_3F | 3 (5) | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Tas
N^^V_MSDD1 | 3 (0) | Out = Murray to Dederang No.1 or No.2 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
S>>BRBG_BGTX_HUWT | 3 (0) | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | SA
V>>V_KTS_TX_A2_2B_R | 3 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Vic
N:Q_AR_BUS5_N-2 | 3 (0) | Out = Nil, loss of Armidale No.5 330kV reclassified as credible, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | NSW
T_T_FASH_4_N-2 | 3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link open, constrain Tribute to 0 MW as per Transend advice | Outage | Tas
V::N_BUDP_xxx | 3 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
V:T_NIL_BL_1 | 3 (0) | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
NC_V_BDL02 | 3 (3) | Non conformance constraint equation for Bairnsdale 2 power station | Outage | Non-Conformance
V>>SML_BESH_3 | 3 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line (flow from MLTS to BATS) for trip of the Moorabool to Elaine to Ballarat 220 kV line and Mt Mercer Wind Farm, feedback | Outage | Vic
V_HWMW | 3 (2) | Out = Hazelwood PS to Morwell PS 220 kV line, Limit Morwell Units 4 & 5 upper limit set to zero | Outage | Vic
CA_MQS_42084A52_01 | 3 (0) | Constraint Automation, O/L ROBNWB_1 @R_TOWN for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1 2&3MWPS. Generated by STNET[MANFR] Host MANEEMP1(MQ) | Outage | Constraint Automation
NC_Q_CPP_3 | 3 (11) | Non Conformance Constraint for Callide C CPP_3 | Outage | Non-Conformance
NC_Q_CPP_4 | 3 (21) | Non Conformance Constraint for Callide C CPP_4 | Outage | Non-Conformance
T_T_BA_JB_RC2_250 | 3 (8) | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
V::N_JNWG_xxx | 3 (1) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
Q:N_AR_2L-G_-100 | 3 (0) | Nominated Offset -100MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | Outage | Qld
V>>S_NIL_NIL_SGKHC | 3 (7) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on Nil trip, Feedback | NIL | SA
V>>V_BAELML_1 | 3 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage | Vic
V>V_HW_TX12_35_OPT1 | 3 (0) | Out = Hazelwood A1 or A2 500/220 kV txfmr, HWTS A3 txfmr switched to HWPS No. 2 bus, avoid O/L Yallourn to Rowville No. 7 or 8 220 kV line on trip of Hazelwood A4 txfmr, 3/5 parallel mode, JLGA connected to HWPS B3/4 side, feedback | Outage | Vic
T_MRWF_UPLIM | 3 (6) | Limit Musselroe generation to current MW + 10 | Outage | Tas
V>>V_KTSY_2_R | 3 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of Keilor to South Morang 500kV line, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
S>>V_NIL_NOTI_x and S>NIL_NOTI_x | 3 (69) | Out = Nil with Torrens Island 66kV CB6W2, CB6W3 & CB6E6 open; avoid O/L of Torrens Island - New Osborne 66kV No.4 line on trip of Torrens Island - New Osborne 66kV No.3 line, Feedback | NIL | SA
T>T_NIL_BL_5C | 3 (89) | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
V>>SML_NIL_1_5M | 3 (0) | Out = Nil, avoid O/L Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Elaine To Moorabool 220 kV line and Mt Mercer Wind Farm, 5 minute line ratings, feedback | NIL | Vic
N^^V_EPMB_1 | 3 (0) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
Q>NIL_MRTA_B | 3 (1) | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line. | NIL | Qld
V>V_X_ROYP_78_8 | 3 (0) | Out = Rowville to Yallourn No. 7 and No. 8 220 kV lines, avoid O/L Yallourn to Hazelwood No. 1 220 kV line on trip of Yallourn to Rowville No. 6 220 kV line, YWG1 on 220 kV side, feedback | Outage | Vic
T>T_NIL_BL_IMP_6EE | 3 (2) | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
NC_V_BDL01 | 2 (2) | Non Conformance constraint equation for Bairnsdale 1 Power Station | Outage | Non-Conformance
NC_V_HWPS8 | 2 (2) | Non Conformance Constraint for Hazelwood HWPS 8 Power Station | Outage | Non-Conformance
T_V_NIL_FCSPS | 2 (4) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
V::N_EPMB_xxx | 2 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V>SMLHORC1 | 2 (0) | Out = Horsham to Red Cliffs 220kV line, avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line | Outage | Vic
N>>V-NIL_O | 2 (1) | Out = Nil, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line and subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | NIL | NSW
VT_300 | 2 (0) | Vic to Tas on Basslink upper limit of 300 MW | Outage | Vic
NC_Q_SWAN_E | 2 (3) | Non Conformance Constraint for Swanbank E Power Station | Outage | Non-Conformance
T_X_TUWA2_CRNN_1 | 2 (0) | Out = Tungatinah to Waddamana No. 2 and New Norfolk to Creek Rd 110 kV lines, avoid O/L Lake Echo Tee to Waddamana No. 1 110 kV line section on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Tas
T>T_X_TUWA_TWO_TUTA | 2 (0) | Out = Both Tungatinah to Waddamana 110kV lines (direct and via Lake Echo tee), avoid O/L remaining Tungatinah to Tarraleah line (flow to South) for loss of the parallel line | Outage | Tas
T_T_FASH_5_N-2 | 2 (1) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Mackintosh P/S unavailable, Hampshire link open, limit Mackintosh + Tribute + Reece 1 <= 110% of West Coast load | Outage | Tas
#N-Q-MNSP1_RAMP_I_F | 2 (1) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage | Quick
NC_Q_GSTONE2 | 2 (1) | Non Conformance Constraint for Gladstone 2 Power Station | Outage | Non-Conformance
T_T_FASH_HM_OPEN_1 | 2 (0) | Out = one Farrell to Sheffield 220kV line, Hampshire link open, Farrell 220 kV bus not split, limit West Coast gen <= 110% of West Coast load | Outage | Tas
V>>S_RBTU2_BRPA_WTTP | 2 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | SA
V>>V_NIL_4A | 2 (1) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. Similar to DBUSS - Line, the DBUSS – Transformer scheme splits the Dederang 330 kV bus on trip of a Dederang transformer. | NIL | Vic
VN_0750 | 2 (0) | Discretionary Vic to NSW transfer upper limit of 750 MW | Outage | Vic
#TORRB3_E | 2 (0) | STSB3.ENERGY * 1 <= 165 (Wt = 360) | Outage | Quick
NRM_NSW1_VIC1 | 2 (4) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
T>T_TUBUS_SPLIT_1 | 2 (0) | Out = Tungatinah 110 kV bus section, Derwent 110 kV system split at Tungatinah, avoid O/L Tungatinah to New Norfolk No. 1 110 kV line on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
T^T_NIL_BL_6_DS | 2 (0) | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah-Waddamana-Palmerston 220 kV line, dispatch equation only | NIL | Tas
V>>V_CBTS_TX_2A_R | 2 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
NC_Q_BARRON-1 | 2 (2) | Non Conformance Constraint for Barron Gorge 1 Power Station | Outage | Non-Conformance
NC_S_MINTARO | 2 (0) | Non Conformance Constraint for Mintaro Gas Turbine | Outage | Non-Conformance
S_PLN_ISL31 | 2 (0) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T_ROCOF_3 | 2 (0) | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | Tas
VSML_220 | 2 (68) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
NC_Q_GSTONE3 | 2 (1) | Non Conformance Constraint for Gladstone 3 Power Station | Outage | Non-Conformance
T>>T_NIL_BL_EXP_7C | 2 (1) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_NIL_BL_IMP_5FF | 2 (107) | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
T>T_X_TU_LE_WA_TWO_1 | 2 (0) | Out = Both Tungatinah to Waddamana 110kV lines (direct and via Lake Echo tee), avoid O/L Meadowbank Tee 2 to New Norfolk on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
V>>V_EPTT_2_P | 2 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, parallel mode, feedback | Outage | Vic
NC_N_GULLRWF1 | 2 (0) | Non Conformance Constraint for GULLEN RANGE WF | Outage | Non-Conformance
NC_Q_GSTONE1 | 2 (1) | Non Conformance Constraint for Gladstone 1 Power Station | Outage | Non-Conformance
NC_Q_KPP_1 | 2 (3) | Non Conformance Constraint for Kogan Creek Power Station | Outage | Non-Conformance
T>T_NIL_BL_IMP_6E | 2 (6) | Out = Nil, avoid overloading Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) on trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action | NIL | Tas
N>>Q-LDTW_2 | 2 (0) | Out= Liddell-Tamworth(84), avoid Liddell->Muswellbrook(83) OL on trip of QLD largest unit; Fb | Outage | NSW
NC_Q_GSTONE5 | 2 (1) | Non Conformance Constraint for Gladstone 5 Power Station | Outage | Non-Conformance
Q:N_AR_CP2_AR_2L-G | 2 (0) | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
T>T_GTSH_IMP_4K | 2 (10) | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
T_FASH_MAXGEN_1 | 2 (8) | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link closed. Constraint swamped if only one machine on line | Outage | Tas
T_X_GTHA_1 | 2 (0) | Outage = Both Hadspen to Georgetown 220kV lines, limit Southern + Poatina + Trevallyn generation <= South + North load + 10MW, limiting PM-SH line flow to 10 MW | Outage | Tas
V>>V_EPTT_2A_R | 2 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode, feedback | Outage | Vic
#SNOWSTH1_E | 1 (14) | SBLWS2.ENERGY * 1 <= 126 (Wt = 360) | Outage | Quick
NC_V_HWPS2 | 1 (2) | Non Conformance Constraint for Hazelwood HWPS 2 Power Station | Outage | Non-Conformance
S>>BWPA_DVBR_RHBG-T | 1 (0) | Out= Blyth West- Para 275kV line with Bungama CB6539 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | SA
T>T_GTSH_IMP_4A | 1 (9) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
NC_Q_GSTONE4 | 1 (1) | Non Conformance Constraint for Gladstone 4 Power Station | Outage | Non-Conformance
NC_S_AGLHAL | 1 (2) | Non Conformance Constraint for AGL Hallet Power Station | Outage | Non-Conformance
NC_Q_STAN-4 | 1 (1) | Non Conformance Constraint for Stanwell STAN-4 Power Station | Outage | Non-Conformance
NC_V_HWPS1 | 1 (1) | Non Conformance Constraint for Hazelwood HWPS 1 Power Station | Outage | Non-Conformance
VS_400 | 1 (0) | Victoria to SA on VicSA upper transfer limit of 400 MW | Outage | Vic
Q>NIL_MRTA_A | 1 (0) | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line. | NIL | Qld
V>V_NIL_RADIAL_3 | 1 (0) | Out = Nil, avoid O/L of Hazelwood A1 500/220kV transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, radial mode, Hazelwood 1,2,3,4 busses split, feedback | NIL | Vic
Q:N_NIL_OSC | 1 (2) | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
T>T_FASH_1_N-2 | 1 (12) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
T^V_NIL_9 | 1 (0) | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
V_HYML1_2 | 1 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
V_MACARTHUR_ZERO | 1 (15) | Macarthur upper limit of 0 MW | Outage | Vic
NC_N_LD04 | 1 (0) | Non Conformance Constraint for Liddell LD04 Power Station | Outage | Non-Conformance
NC_S_NPS2 | 1 (0) | Non Conformance Constraint for Northern NPS2 Power Station | Outage | Non-Conformance
T>T_FASH_2_N-2 | 1 (1) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.2 transformer | Outage | Tas
T>T_HAPM_110_IMP_4Q | 1 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L of Palmerston to Hadspen No. 4 110 kV line (flow to North) for trip of the Palmerston 220/110 kV transformer with no NCSPS action, feedback | Outage | Tas
NC_Q_MPP_2 | 1 (0) | Non Conformance Constraint for Millmerran 2 Power Station | Outage | Non-Conformance
NC_V_HWPS5 | 1 (1) | Non Conformance Constraint for Hazelwood HWPS 5 Power Station | Outage | Non-Conformance
S:V_580 | 1 (0) | Maintain maximum transfer limit of 580 MW on SA-VIC and Murraylink combined to avoid oscillatory instability | NIL | SA
S_PLN_ISL1 | 1 (1) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
T>T_HAPM_110_IMP_4B | 1 (5) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L a Palmerston to Hadspen No. 1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
T>T_TUNN2_1 | 1 (0) | Out = Tungatinah to New Norfolk No. 2 110 kV line, avoid O/L the Tungatinah to New Norfolk No. 1 110 kV line (flow to South) on trip of Tungatinah to New Norfolk No.3 110 kV line, feedback | Outage | Tas
V>V_HWJL3-4_RAD | 1 (0) | Outage = Hazelwood to Jeeralang No.3 or No.4 220kV line, limit HWPS units3,4,5 and Jeeralang A to avoid O/L HWTS A1 Tx for trip of HWPS-JLTS No.4 or No.3 220kV line, Radial Mode with 1&2 busses split and 3&4 busses split or tied | Outage | Vic
V>V_HWRO12_1AR | 1 (0) | Out = Hazelwood to Rowville No. 1 or No. 2 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 7 or No. 8 220 kV line for trip of the parallel No. 8 or No. 7 220 kV line, Yallourn W1 on 220 kV, feedback | Outage | Vic
VSML_000 | 1 (0) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
VT_000 | 1 (0) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
#V-SA_RAMP_E_F | 1 (1) | V-SA <= MAX(250, InitialFlow - 30) (Wt=35) | Outage | Quick
NC_N_URANQ11 | 1 (0) | Non Conformance Constraint for Uranquinty 1 Power Station | Outage | Non-Conformance
T>T_TUNN2_2 | 1 (0) | Out = Tungatinah to New Norfolk No. 2 110 kV line, avoid O/L the Tungatinah to New Norfolk No.3 110 kV line (flow to South) on trip of Tungatinah to New Norfolk No. 1 110 kV line, feedback | Outage | Tas
CA_SPS_4317B056_01 | 1 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
CA_SPS_43667C70_01 | 1 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
NC_N_LD02 | 1 (1) | Non Conformance Constraint for Liddell LD02 Power Station | Outage | Non-Conformance
NC_Q_BRAEMAR2 | 1 (0) | Non Conformance Constraint for Braemar 2 Power Station | Outage | Non-Conformance
NC_Q_YABULU | 1 (1) | Non Conformance Constraint for Yabulu Power Station | Outage | Non-Conformance
NC_T_GORDON | 1 (0) | Non Conformance Constraint for Gordon Power Station | Outage | Non-Conformance
N^Q_AR_330_BS5_1 | 1 (0) | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage | NSW
T>T_PMWA_IMP_4D | 1 (22) | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_SHGT_HAGT_N-2 | 1 (0) | Out= NIL, Loss of both Hadspen to Georgetown 220kV lines declared credible, avoid O/L the Sheffield to Georgetown 220kV line for loss of both Hadspen to Georgetown 220kV lines , Feedback | Outage | Tas
V>>S_MSTU_TBTU_TBMO | 1 (0) | Out= Mt Barker South - Tungkillo 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
V>>S_NIL_SGBL_SGKH | 1 (0) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on trip of Snuggery - Blanche 132kV line, Feedback. | NIL | SA
V>>V_EPTT_2B_R | 1 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage | Vic
#V-S-MNSP1_I_E | 1 (0) | V-S-MNSP1.ENERGY * -1 >= 20 (Wt = 35) | Outage | Quick
NC_N_LD01 | 1 (1) | Non Conformance Constraint for Liddell LD01 Power Station | Outage | Non-Conformance
NC_Q_STAN-3 | 1 (1) | Non Conformance Constraint for Stanwell STAN-3 Power Station | Outage | Non-Conformance
NC_Q_TARONG#3 | 1 (1) | Non Conformance Constraint for Tarong 3 Power Station | Outage | Non-Conformance
NC_T_TREVALLN | 1 (2) | Non Conformance Constraint for Trevallyn Power Station | Outage | Non-Conformance
NC_V_HUMEV | 1 (0) | Non Conformance Constraint for Hume Power Station | Outage | Non-Conformance
S>NIL_HUWT_STBG | 1 (0) | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line. | NIL | SA
S>V_NIL_HYTX_HYTX | 1 (0) | Out = Nil, avoid overloading a Heywood 275/500 kV transformer on trip of the other Heywood 275/500 kV transformer | NIL | SA
V>>S_TB6125+28_KHTB1 | 1 (2) | Out = Tailem Bend CBs 6125 and/or 6128 (both or either CB); Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend 132kV #1 line for loss of Tailem Bend transformer #4. | Outage | SA
NC_Q_BARCALDN | 1 (0) | Non Conformance Constraint for Barcaldine Power Station | Outage | Non-Conformance
NC_Q_BARRON-2 | 1 (1) | Non Conformance Constraint for Barron Gorge 2 Power Station | Outage | Non-Conformance
NC_Q_CPSA | 1 (0) | Non Conformance Constraint for Condamine Power Station | Outage | Non-Conformance
NC_Q_GSTONE6 | 1 (2) | Non Conformance Constraint for Gladstone 6 Power Station | Outage | Non-Conformance
NC_T_POAT220 | 1 (8) | Non Conformance Constraint for Poatina 220kV Power Station | Outage | Non-Conformance
NC_T_TVPP104 | 1 (1) | Non Conformance Constraint for Tamar Valley 110 kV OCGT | Outage | Non-Conformance
NC_V_HWPS4 | 1 (1) | Non Conformance Constraint for Hazelwood HWPS 4 Power Station | Outage | Non-Conformance
NC_V_LOYYB1 | 1 (1) | Non Conformance Constraint for Loy Yang B1 Power Station | Outage | Non-Conformance
N_BLTU_97B | 1 (0) | Blowering PS upper limit set to zero due to outage of Blowering to Tumut 97B 132kV line. | Outage | NSW
S>>BWPA_BRTW_WTTP | 1 (0) | Out= Blyth West- Para 275kV line with Bungama CB6539 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | SA
S_PLN_ISL2 | 1 (1) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
T>T_HAPM_110_IMP_4P | 1 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L of Palmerston to Hadspen No. 3 110 kV line (flow to North) for trip of the Palmerston 220/110 kV transformer with no NCSPS action, feedback | Outage | Tas
T>T_TULEWA1_TUNN2_1 | 1 (0) | Out = Tungatinah to New Norfolk No. 2 and Tungatinah to Lake Echo to Waddamana No. 1 110 kV lines, avoid O/L Tungatinah to Waddamana No. 2 110 kV line (flow to North) on trip of Tungatinah to New Norfolk No.3 110 kV line, feedback | Outage | Tas
V>>V_KTS_TX_A3_2A_R | 1 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
V_MTMERCER_ZERO | 1 (0) | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
N>>N-NIL__2_OPENED & CLOSED | 1 (0) | Out= NIL, avoid O/L Liddell to Tamworth (84) on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
NC_N_BW01 | 1 (0) | Non Conformance Constraint for Bayswater 1 Power Station | Outage | Non-Conformance
NC_N_LD03 | 1 (1) | Non Conformance Constraint for Liddell LD03 Power Station | Outage | Non-Conformance
NC_T_LI_WY_CA | 1 (2) | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations | Outage | Non-Conformance
S:V_420 | 1 (0) | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability This constraint equation was added, in January 2011, to a number of outage constraint sets across the NEM (except for Tasmania). The 420 MW value is the previous system normal limit. Throughout 2011 AEMO conducted studies as to whether the 420 MW limit was appropriate for various outages. In some cases the limit was increased. This work will continue in 2012. | Outage | SA
S_LB2_63 | 1 (0) | Discretionary upper limit for Lake Bonney 2 generation of 63 MW | Outage | SA
T>T_TANN2_110_2 | 1 (0) | Out = Tarraleah to New Norfolk No. 2 110 kV line, avoid O/L the Tungatinah to New Norfolk No. 1 110 kV line (flow to South) on trip of Meadowbank to New Norfolk 110 kV line, feedback | Outage | Tas
T_CESH | 1 (0) | Out=Sheffield-Cethana 220KV line. Energy <= 0MW | Outage | Tas
T_V_FCSPS_RAMP | 1 (0) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
V::N_DDWO_xxx | 1 (0) | Out = Dederang to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V>>N-JNWG_RADIAL_1 | 1 (1) | Out = Jindera to Wagga(62), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
V>SML_NSWRB_10 | 1 (0) | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
V>V_NIL_ROYP56_R5_1 | 1 (1) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 500 kV, feedback | NIL | Vic
N>N-NIL_LSDU | 0 (160) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
NC_N_BW04 | 0 (1) | Non Conformance Constraint for Bayswater 4 Power Station | Outage | Non-Conformance
NC_Q_CALL_B_2 | 0 (0) | Non Conformance Constraint for Callide B_2 | Outage | Non-Conformance
NC_Q_STAN-1 | 0 (0) | Non Conformance Constraint for Stanwell STAN-1 Power Station | Outage | Non-Conformance
NC_Q_TARONG#4 | 0 (0) | Non Conformance Constraint for Tarong 4 Power Station | Outage | Non-Conformance
NC_S_NPS1 | 0 (0) | Non Conformance Constraint for Northern NPS1 Power Station | Outage | Non-Conformance
NC_T_BBTHREE1 | 0 (2) | Non Conformance Constraint for Bell Bay Three Unit 1 Power Station | Outage | Non-Conformance
NC_V_HWPS6 | 0 (2) | Non Conformance Constraint for Hazelwood HWPS 6 Power Station | Outage | Non-Conformance
NC_V_JLA03 | 0 (0) | Non Conformance Constraint for Jeeralang A - 03 Power Station | Outage | Non-Conformance
NC_V_MORTLK11 | 0 (2) | Non Conformance Constraint for Mortlake GT unit 1 | Outage | Non-Conformance
N^^V_DDSM1 | 0 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
S_PLN_ISL32 | 0 (1) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T>T_NIL_TOV_5FF | 0 (0) | Out = Nil, avoid TOV following NCSPS slow action for O/L of Hadspen to Georgetown No. 2 220 kV lines (flow to North) for trip of the Hadspen to Georgetown No. 1 220 kV line, considering status of Tamar CCGT, feedback equation | NIL | Tas
T^T_NIL_LIPM_N-2_DS | 0 (0) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid voltage instability or violations for loss of both Liapootah to Palmerston 220 kV lines, dispatch only | NIL | Tas
T_T_FASH2_A_2 | 0 (0) | Out = Farrell to Sheffield No.1 or 2 line with Tribute and Reece 1 supplying Sheffield, Hampshire link closed, limit Bastyan + Reece 2 + John Butters + Mackintosh >= 90% of West Coast load | Outage | Tas
V>>V_NIL_6_P | 0 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood 3/5 parallel mode, feedback | NIL | Vic
V>>V_ROTT_R_2A | 0 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV side, feedback | Outage | Vic
V>S_NIL_NIL_HYTX2 | 0 (0) | Out = NIL, avoid O/L Heywood M2 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL | Vic
V>V_NIL_ROYP56_R2_3 | 0 (0) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - ROTS No. 7 or No. 8 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 220 kV, feedback | NIL | Vic
#VP5_E | 0 (0) | NVPP5.ENERGY * 1 <= 450 (Wt = 360) | Outage | Quick
CA_SPS_42008454_01 | 0 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
CA_SPS_42009181_01 | 0 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
NC_N_BW03 | 0 (1) | Non Conformance Constraint for Bayswater 3 Power Station | Outage | Non-Conformance
NC_N_ER01 | 0 (0) | Non Conformance Constraint for Eraring ER01 Power Station | Outage | Non-Conformance
NC_S_TORRA2 | 0 (0) | Non Conformance Constraint for Torrens A2 Power Station | Outage | Non-Conformance
NC_V_HWPS7 | 0 (3) | Non Conformance Constraint for Hazelwood HWPS 7 Power Station | Outage | Non-Conformance
NC_V_JLB01 | 0 (1) | Non Conformance Constraint for Jeeralang B - 01 Power Station | Outage | Non-Conformance
Q:N_DM_CB_AR_2L-G | 0 (0) | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
Q_CS_1100 | 0 (9) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer | Outage | Qld
T::T_HA_GT_PM_5 | 0 (0) | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT in service. | Outage | Tas
T>T_NIL_BL_220_6B | 0 (3) | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
T>T_TATU_110_1 | 0 (0) | Out = One Tarraleah to Tungatinah 110 kV line, limit Tarraleah generation to 62 MW, based on maximum 4 machines in service due to fault level limits at Tarraleah | Outage | Tas
V::N_BYPASS_HW_SY_xxx | 0 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V>>S_RBTU2_BUPA_BRPA | 0 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines , avoid O/L Brinkworth - Templers West line on trip of Bungama - Blyth West 275kV line, Feedback | Outage | SA
V>>V_CBTS_TX_3B_R | 0 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage | Vic
V>>V_NIL_8 | 0 (0) | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines; Feedback | NIL | Vic
V>SMLKGRC1 | 0 (0) | Out = Kerang to Redcliffs 220kV line, avoid overloading Darlington Pt to Balranald (X5/1) 220kV line for trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
VT_200 | 0 (0) | Vic to Tas on Basslink upper limit of 200 MW | Outage | Vic
N>>N-NIL_DPTX | 0 (0) | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other | NIL | NSW
NC_Q_BRAEMAR1 | 0 (2) | Non Conformance Constraint for Braemar 1 Power Station | Outage | Non-Conformance
NC_Q_KAREEYA3 | 0 (0) | Non Conformance Constraint for Kareeya 3 Power Station | Outage | Non-Conformance
NC_Q_KAREEYA4 | 0 (0) | Non Conformance Constraint for Kareeya 4 Power Station | Outage | Non-Conformance
NC_S_QPS5 | 0 (0) | Non Conformance Constraint for Quarantine QPS5 Power Station | Outage | Non-Conformance
NC_T_FISHER | 0 (0) | Non Conformance Constraint for Fisher Power Station | Outage | Non-Conformance
NC_V_LOYYB2 | 0 (2) | Non Conformance Constraint for Loy Yang B2 Power Station | Outage | Non-Conformance
NC_V_LYA4 | 0 (1) | Non Conformance Constraint for Loy Yang A4 Power Station | Outage | Non-Conformance
NC_V_NPS | 0 (3) | Non Conformance Constraint for Newport Power Station | Outage | Non-Conformance
S:V_430 | 0 (0) | Maintain maximum transfer limit of 430 MW on SA-VIC and Murraylink combined to avoid oscillatory instability during the outage of one or more of the major transmission lines connecting NEM regions. | Outage | SA
S:V_SA_PSS | 0 (0) | Out= Nil; SA to Vic Oscillatory stability limit based on PSS availability in South Australia. | NIL | SA
S>>NIL_NIL_TINO3 | 0 (0) | Out= Nil with Torrens Island 66kV CB6W2, CB6E4 & CB6C6 open, avoid O/L Torrens Island - New Osborne No.3 66kV line on Nil trip, Feedback | NIL | SA
S>MYTX1_MYTX2 | 0 (0) | Out = Mayura 132/33 kV transformer #1 with the 33kV bus tie isolator 44248 open or closed, avoid O/L Mayura 132/33 kV transformer #2, Feedback | Outage | SA
T>>T_NIL_BL_EXP_3F | 0 (0) | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_HAPM_110_IMP_4A | 0 (1) | Out = Hadspen to Palmerston No. 3 110 kV line, avoid O/L the Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
T>T_X-TUWA_TUTA2_2 | 0 (0) | Out = Multiple 110 kV lines ex Tungatinah - Tungatinah - Tarraleah No. 2, Tungatinah - Lake Echo - Waddamana No. 1 and No. 110 kV lines OOS, avoid O/L Tarraleah to New Norfolk No. 2 110 kV line on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
T_FAJB | 0 (0) | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Tas
V>>V_ROTT_R_2B | 0 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV side, feedback | Outage | Vic
V_HYML1_1 | 0 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No. 1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
#BOCORWF1_E | 0 (0) | NCMA3B.ENERGY * 1 <= 75 (Wt = 360) | Outage | Quick
N>>V-LTMS_5 | 0 (0) | Out = Lower Tumut to Murray (66) 330 kV line, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | Outage | NSW
N>N-CHKK_TE_1 | 0 (0) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
N>N-LS_TX_TE_B | 0 (0) | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. DS only | Outage | NSW
N>N_LSDU_9U6_1 | 0 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | NSW
NC_N_BW02 | 0 (0) | Non Conformance Constraint for Bayswater 2 Power Station | Outage | Non-Conformance
NC_N_CG1 | 0 (0) | Non Conformance Constraint for Colongra 1 Power Station | Outage | Non-Conformance
NC_Q_DDPS1 | 0 (0) | Non Conformance Constraint for Darling Downs Power Station | Outage | Non-Conformance
NC_Q_KAREEYA1 | 0 (2) | Non Conformance Constraint for Kareeya 1 Power Station | Outage | Non-Conformance
NC_Q_KAREEYA2 | 0 (0) | Non Conformance Constraint for Kareeya 2 Power Station | Outage | Non-Conformance
NC_Q_TARONG#1 | 0 (2) | Non Conformance Constraint for Tarong 1 Power Station | Outage | Non-Conformance
NC_S_PPCCGT | 0 (0) | Non Conformance Constraint for Pelican Point Power Station | Outage | Non-Conformance
NC_T_TUNGATIN | 0 (1) | Non Conformance Constraint for Tungatinah Power Station | Outage | Non-Conformance
NC_T_TVCC201 | 0 (0) | Non Conformance Constraint for Tamar Valley 220 kV CCGT | Outage | Non-Conformance
NC_V_LYA2 | 0 (2) | Non Conformance Constraint for Loy Yang A2 Power Station | Outage | Non-Conformance
NC_V_MERCER01 | 0 (0) | Non Conformance Constraint for MT MERCER WIND FARM | Outage | Non-Conformance
NRM_VIC1_SA1 | 0 (2) | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
N^N-89_LSTX_SVC | 0 (3) | Out = Coffs Harbour to Lismore (89) 330 kV line and Lismore 330/132 kV transformer with Lismore SVC in reactive power control mode, avoid voltage collapse on trip of Koolkhan to Lismore (967) 132 kV line | Outage | NSW
N^Q_ARTW_1 | 0 (13) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage | NSW
N^^Q_ARDM_B1 | 0 (3) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage | NSW
N^^V_SMTXH2_2 | 0 (0) | Out = South Morang H1 330/220 kV transformer, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage | NSW
SV_200 | 0 (1) | SA to Victoria on VicSA upper transfer limit of 200 MW | Outage | SA
SV_250 | 0 (0) | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage | SA
S_DVNP_NP1 | 0 (0) | Out=Davenport Northern U1 275kV line | Outage | SA
T>T_GTSH_IMP_4E | 0 (13) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_X-TUWA_TUTA2_1 | 0 (0) | Out = Multiple 110 kV lines ex Tungatinah - Tungatinah - Tarraleah No. 2, Tungatinah - Lake Echo - Waddamana No. 1 and No. 110 kV lines OOS, avoid O/L Tungatinah to Tarraleah No. 1 on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
T_X_GTHA_2 | 0 (0) | Outage = Both Hadspen to Georgetown 220kV lines, limit Southern + Poatina + Trevallyn generation => South + North load - 10MW, limiting SH-PM line flow to 10 MW | Outage | Tas
V>>N-DDWO_RADIAL_1 | 0 (0) | Out = Dederang to Wodonga, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
V>>N-JNWO_RADIAL_2 | 0 (0) | Out = Jindera to Wodonga(060), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V>>N-X_MSUT_LTUT | 0 (0) | Out= Murray-UpperTumut(65) and Lower Tumut-Upper Tumut (64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
V>>N_SMHTX_1 | 0 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V>>V_CBTS_TX_3A_R | 0 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
VT_350 | 0 (0) | Vic to Tas on Basslink upper limit of 350 MW | Outage | Vic
V_HYML1_3 | 0 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
T_LE_ZERO | 0 (1) | Discretionary 0 MW upper limit on Lake Echo generation | Outage | Tas
#GORDON_O_E | 0 (0) | TGO11.ENERGY * 1 <= 70 (Wt = 55) | Outage | Quick
#V-SA_RAMP_I_F | 0 (2) | V-SA >= MIN(-60, InitialFlow + 50) (Wt=35) | Outage | Quick
CA_SPS_428FB629_01 | 0 (0) | Constraint Automation, O/L 94E @MT_PIPER for CTG LNWT on trip of MT_PIPER-WWANG 70 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
CA_SPS_43667C70_02 | 0 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
N>N-NIL_8C_8E | 0 (0) | Out = Nil, avoid O/L Dumaresq to Armidale (8C) on trip of Dumaresq to Armidale (8E) line, Feedback | NIL | NSW
N>N_LSDU_9U6_2 | 0 (0) | Out = one of Lismore to Dunoon (9U6 or 9U7) 132 kV line, avoid overloading on the Mullumbimby 132/66 kV transformer on trip of the remaining Lismore to Dunoon (9U6 or 9U7) 132 kV line | Outage | NSW
NC_N_CG3 | 0 (0) | Non Conformance Constraint for Colongra 3 Power Station | Outage | Non-Conformance
NC_N_CG4 | 0 (0) | Non Conformance Constraint for Colongra 4 Power Station | Outage | Non-Conformance
NC_N_ER02 | 0 (2) | Non Conformance Constraint for Eraring ER02 Power Station | Outage | Non-Conformance
NC_N_SHGEN | 0 (0) | Non Conformance Constraint for Shoalhaven Power Station | Outage | Non-Conformance
NC_N_WW8 | 0 (6) | Non Conformance Constraint for Wallerawang WW8 Power Station | Outage | Non-Conformance
NC_Q_BRAEMAR3 | 0 (3) | Non Conformance Constraint for Braemar 3 Power Station | Outage | Non-Conformance
NC_Q_MPP_1 | 0 (0) | Non Conformance Constraint for Millmerran 1 Power Station | Outage | Non-Conformance
NC_Q_MSTUART2 | 0 (0) | Non Conformance Constraint for Mt Stuart 2 Power Station | Outage | Non-Conformance
NC_Q_MSTUART3 | 0 (0) | Non Conformance Constraint for Mt Stuart 3 Power Station | Outage | Non-Conformance
NC_Q_OAKEY1 | 0 (0) | Non Conformance Constraint for Oakey 1 Power Station | Outage | Non-Conformance
NC_Q_OAKEY2 | 0 (0) | Non Conformance Constraint for Oakey 2 Power Station | Outage | Non-Conformance
NC_Q_STAN-2 | 0 (1) | Non Conformance Constraint for Stanwell STAN-2 Power Station | Outage | Non-Conformance
NC_Q_YABULU2 | 0 (0) | Non Conformance Constraint for Yabulu 2 Power Station | Outage | Non-Conformance
NC_S_TORRA4 | 0 (0) | Non Conformance Constraint for Torrens A4 Power Station | Outage | Non-Conformance
NC_T_BBTHREE2 | 0 (1) | Non Conformance Constraint for Bell Bay Three Unit 2 Power Station | Outage | Non-Conformance
NC_T_CETHANA | 0 (5) | Non Conformance Constraint for Cethana Power Station | Outage | Non-Conformance
NC_V_LYA1 | 0 (2) | Non Conformance Constraint for Loy Yang A1 Power Station | Outage | Non-Conformance
NC_V_WKIEWA1 | 0 (0) | Non Conformance Constraint for West Kiewa 1 Power Station | Outage | Non-Conformance
N^^Q_ARTW_B1 | 0 (0) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
N_MBTE1_A | 0 (0) | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
QNI_ISLE_B | 0 (0) | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage | Qld
Q_KMBG_7143 | 0 (0) | Out= 7143 Kamerunga Barron Gorge PS 132kV line | Outage | Qld
S>>V_NIL_KHTB2_KHTB1 | 0 (0) | Out= Nil, avoid O/L Tailem Bend - Keith #1 132kV on trip of Tailem Bend - Keith #2 132kV line, Feedback | NIL | SA
S>>V_NIL_NIL_HUWT | 0 (2) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL | SA
T>T-X_TUTA | 0 (0) | Out = both Tarraleah to Tungatinah 110 kV line, avoid pre-contingent O/L of the Tarraleah to New Norfolk No. 2 110 kV, feedback | Outage | Tas
T>TU_LE_WA1_TUO_1 | 0 (0) | Out = Tungatinah to Lake Echo to Waddamana No. 1 110kV line open at Tungatinah only (i.e. TU CB G152 OPEN), avoid O/L Tungatinah to Waddamana NO.2 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Tas
T>T_FASH_1_2_C2 | 0 (0) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hampshire link closed, Bastyan + Mackintosh supplying txfmrs, other generators supplying 220kV line to Sheffield, limit Bastyan and Mackintosh >= 90% of Rosebery + Queenstown MW | Outage | Tas
T>T_NIL_BL_110_18_1 | 0 (41) | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
T>T_NIL_BL_IMP_1B | 0 (300) | Out = Nil, avoid overloading either Gordon to Chapel St 220 kV line for trip of the other Gordon to Chapel St 220 kV line with no SPS action This constraint equation binds at times of high Gordon generation when the NCSPS control scheme is unavailable. | NIL | Tas
T>T_NIL_NCSPS5_1B | 0 (27) | Out = Nil, avoid overloading the line terminal equipment of either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line | NIL | Tas
T>T_X-HAPM_2_1N | 0 (0) | Out= Hadspen to Palmerston No. 1 and No. 2 220 kV lines, avoid O/L either of the Hadspen to Palmerston No. 3 or No 4 110 kV lines (flow to North) on trip of Sheffield to Palmerston 220 kV line, Feedback | Outage | Tas
T_MB_ZERO | 0 (0) | Limit Meadowbank to zero MW | Outage | Tas
T_T_TU_105 | 0 (0) | Discretionary 105 MW upper limit on Tungatinah | Outage | Tas
V::N_HYSE_xxx | 0 (22) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
V>>N-MSUT_4 | 0 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
V>>SML_NIL_5 | 0 (0) | Out = NIL, prevent pre-contingent overload of the Ballarat to Bendigo 220 kV line, feedback | NIL | Vic
V>>S_NIL_KHTB1_KHTB2 | 0 (0) | Out = Nil, avoid O/L Keith - Tailem Bend #2 132kV on trip of Keith - Tailem Bend #1 132kV line, Feedback | NIL | SA
V>>V_NIL_4C | 0 (0) | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL | Vic
V>>V_SMTT2_2 | 0 (0) | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the South Morang to Thomastown No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V>SML_BUDP_3 | 0 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Kerang to Wemen 220 kV line section on trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
V>V_HWJL2_RADIAL_7 | 0 (0) | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split | Outage | Vic
V>V_NIL_RADIAL_3-4_3 | 0 (0) | Outage = Nil, limit Yallourn unit 1 +HWPS+JLGS+Bairnsdale+Morwell, avoid O/L Hazelwood 500/220kV A1 txfmr for trip of A2 txfmr, Yallourn unit 1 in 500kV mode, HWPS Radial Mode with 3&4 busses tied, 1&2 busses split. Swamped if HWPS-JLTS 2 line open. | NIL | Vic
V>V_NIL_RADIAL_6 | 0 (0) | Out = Nil, avoid O/L of Hazelwood A3 500/220kV transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, radial mode, Hazelwood 1,2,3,4 busses split, feedback | NIL | Vic
V^SML_NIL_3 | 0 (1) | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW | NIL | Vic

## Binding FCAS 2014
Constraint Equation ID | 2014 Hours (2013 Hours) | Description | Type
F_I+NIL_MG_R5 | 7,678 (7,086) | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL
F_I+NIL_MG_R6 | 6,734 (6,285) | NEM raise 6 second requirement for a NEM generation event | NIL
F_I+NIL_MG_R60 | 6,666 (6,256) | NEM raise 60 second requirement for a NEM generation event | NIL
F_I+NIL_APD_TL_L5 | 5,723 (0) | NEM Lower 5 min Service Requirement for the loss of APD potlines | NIL
F_I+NIL_DYN_LREG | 4,222 (5,354) | NEM lower regulation requirement | NIL
F_I+NIL_APD_TL_L60 | 3,890 (0) | NEM Lower 60 sec Service Requirement for the loss of APD potlines | NIL
F_I+ML_L6_0400 | 3,125 (3,416) | NEM lower 6 second requirement for a NEM load event | NIL
F_T++NIL_TL_L6 | 2,402 (4,629) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_T++NIL_TL_L60 | 2,333 (5,130) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_I+NIL_DYN_RREG | 2,274 (1,880) | NEM raise regulation requirement | NIL
F_MAIN++APD_TL_L5 | 1,979 (0) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 1,855 (0) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 1,840 (2,424) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R6 | 1,583 (1,548) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_I+TL_L5_0500 | 1,275 (13) | NEM lower 5 min Service Requirement for a NEM network event | Outage
F_T+NIL_BL_R60_1 & F_T++NIL_BL_R60_x | 1,104 (205) | Tasmania raise 60 second requirement for loss of Basslink, FCSPS available See note for F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | NIL
F_MAIN++ML_L6_0400 | 1,081 (535) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 1,044 (1,466) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | 1,038 (292) | Tasmania raise 6 second requirement for loss of Basslink, FCSPS available In November 2011 the 4 constraint equations were replaced with 2 constraint equations due to advice that the loss of link time on Basslink was changed to 400ms. The binding results from all the constraint equations have been combined. | NIL
F_T++RREG_0050 | 1,034 (319) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_I+TL_L60_0500 | 977 (6) | Lower 60 sec Service Requirement for a NEM Network Event, TL = 500 | Outage
F_T++LREG_0050 | 807 (926) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 760 (729) | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 760 (729) | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 760 (729) | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_T+NIL_TL_L6 | 757 (760) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_T+NIL_TL_L60 | 757 (760) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_T+NIL_TL_L5 | 751 (691) | Out=Nil, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_T+LREG_0050 | 736 (623) | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T++NIL_TL_L5 | 733 (1,439) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 696 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 693 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T+RREG_0050 | 612 (344) | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+ML_L6_0400 | 565 (367) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++ML_L6_APD | 459 (5) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_MAIN++TL_L5_0500 | 429 (2) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage
F_T+NIL_BL_R5 | 408 (161) | Tasmania raise 5 minute requirement for loss of Basslink, FCSPS available | NIL
F_T+NIL_MG_R6 | 392 (311) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R60 | 391 (310) | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T++NIL_MG_R6 | 338 (570) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_T++NIL_MG_R5 | 320 (231) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_T++NIL_MG_R60 | 308 (327) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_Q++ARDM_L60 | 271 (12) | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 60 sec Requirement | Outage
F_Q++ARDM_L6 | 271 (13) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
F_T+NIL_WF_TG_R6 | 269 (21) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 268 (21) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T++NIL_WF_TG_R6 | 245 (5) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
F_Q++ARDM_L5 | 244 (5) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage
F_T+NIL_WF_TG_R5 | 237 (21) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R5 | 184 (305) | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_DYN_RREG | 183 (109) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL
F_I+ML_L6_APD | 182 (153) | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_MAIN+ML_L6_APD | 172 (2) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_I+ML_L5_0400 | 171 (5,982) | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL
F_MAIN++NIL_DYN_LREG | 143 (4) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL
F_T++NIL_WF_TG_R5 | 119 (6) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
F_MAIN++TL_L60_0500 | 104 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage
F_MAIN+NIL_DYN_LREG | 103 (67) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL
F_I+ML_L60_0400 | 68 (1,610) | NEM lower 60 second requirement for a NEM load event | NIL
F_Q++ARTW_L6 | 59 (10) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
F_Q++ARTW_L60 | 59 (10) | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_Q++ARTW_L5 | 51 (7) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
F_MAIN++NIL_DYN_RREG | 47 (46) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL
F_MAIN+TL_L5_0500 | 45 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS | Outage
F_MAIN+TL_L60_0500 | 45 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS | Outage
F_MAIN++ML_L5_APD | 29 (73) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_MAIN++ML_L60_APD | 27 (48) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_T++NIL_WF_TG_R60 | 26 (5) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
F_I+ML_L5_APD | 25 (326) | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_T++BL_650_R60_3 | 24 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
F_ESTN++MLSY_L60 | 23 (12) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 60 sec Requirement | Outage
F_Q++MUTW_L60 | 20 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_Q++MUTW_L6 | 20 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_ESTN++MLSY_L5 | 19 (9) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 5 min Requirement | Outage
F_I+ML_L60_APD | 18 (83) | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage
F_T++BL_650_R6_3 | 17 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
F_ESTN++MLTR_L60 | 17 (1) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_QNV++MLMO_L60 | 16 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+FASH1_2C_RREG | 16 (0) | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage
F_ESTN++MLTR_L5 | 14 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_Q++MUTW_L5 | 14 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_V+NIL_PTH01_L5 | 14 (15) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_PTH01_R60 | 14 (16) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_PTH01_R6 | 14 (16) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_V+NIL_PTH01_R5 | 14 (16) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_PTH01_L60 | 13 (4) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_S++HYSE_L60 | 12 (105) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
F_T++BL_650_R6_2 | 12 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
F_S++HYML_L60 | 10 (15) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 60 second requirement | Outage
F_MAIN+ML_L5_APD | 10 (2) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_MAIN+ML_L60_APD | 10 (2) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_N_ER02_RREG | 9 (0) | Out= NIL, Eraring 2 RREG Requirement <= 0MW | Outage
F_N_ER02_L6 | 9 (0) | Out= NIL, Eraring 2 L6 Requirement <= 0MW | Outage
F_N_ER02_R6 | 9 (0) | Out= NIL, Eraring 2 R6 Requirement <= 0MW | Outage
F_N_ER02_LREG | 8 (0) | Out= NIL, Eraring 2 LREG Requirement <= 0MW | Outage
F_N_ER02_R5 | 8 (0) | Out= NIL, Eraring 2 R5 Requirement <= 0MW | Outage
F_T_REECE2_DS_R6 | 8 (6) | Determine upper limit for R6 FCAS enablement for Reece 2 based on FCAS Boost Mode status point for unit | NIL
F_Q++LDMU_L6 | 8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
F_Q++LDMU_L5 | 8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
F_Q++LDMU_L60 | 8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
F_V+NIL_PTH01_L6 | 8 (4) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_N_ER02_R60 | 8 (0) | Out= NIL, Eraring 2 R60 Requirement <= 0MW | Outage
F_MAIN++NIL_BL_L60 | 8 (54) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
F_QNV++MLMO_L5 | 7 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_N_ER02_L5 | 7 (0) | Out= NIL, Eraring 2 L5 Requirement <= 0MW | Outage
F_T++FASH_N-2_TG_R60 | 6 (6) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T+BL_650_R60_1 | 6 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage
F_T+BL_650_R6_1 | 6 (1) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage
F_MAIN++ML_L5_0400 | 6 (837) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_Q++LDTW_R60 | 6 (9) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_Q++LDTW_R6 | 5 (11) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
F_ESTN++HYTR_L60 | 5 (24) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_ESTN++HYMO_L60 | 5 (3) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
F_T++FASH_N-2_TG_R6 | 5 (5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_MAIN++NIL_BL_R60 | 5 (4) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
F_QNV++HYMO_L60 | 5 (3) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++LDTW_L6 | 4 (10) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
F_I+LREG_0400 | 4 (0) | NEM Lower Regulation Requirement greater than 400 MW | Outage
F_QNV++MLMO_L6 | 4 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+FASH_N-2_TG_R5 | 4 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_Q++LDTW_L60 | 4 (9) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_QNV++MLSY_L60 | 4 (1) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+FASH_N-2_RREG | 4 (19) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_T+BL_650_R5 | 4 (2) | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 650 ms | Outage
F_T++BL_650_R60_2 | 4 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
F_T++FASH_N-2_TG_R5 | 4 (11) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T+FARE_N-2_TG_R5 | 3 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_T+FASH_N-2_TG_R6 | 3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T+FASH_N-2_TG_R60 | 3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_V+NIL_APD01_R6 | 3 (12) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_QNV++MLSY_L5 | 3 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_Q_MEWV_823_R5 | 3 (0) | Out= Mt England to Wivenhoe (823) line, Raise 5 min requirement of zero for Wivenhoe #1 | Outage
F_I+TG_R60_1000 | 3 (0) | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_I+TG_R5_1000 | 3 (0) | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_V+NIL_APD01_R5 | 3 (12) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_Q_MEWV_824_R5 | 3 (0) | Out= Mt England to Wivenhoe (824) line, Raise 5 min requirement of zero for Wivenhoe #2 | Outage
F_V+NIL_APD01_R60 | 3 (12) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_APD01_L5 | 3 (11) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_T++FARE_N-2_TG_R60 | 3 (8) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_T+NIL_ML_L6 | 3 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T++FARE_N-2_TG_R6 | 3 (4) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_T+NIL_ML_L60 | 3 (0) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_QNV++MLSY_L6 | 2 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q_MACKAYGT_R5 | 2 (0) | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage
F_N_ER02_L60 | 2 (0) | Out= NIL, Eraring 2 L60 Requirement <= 0MW | Outage
F_I+RREG_0350 | 2 (0) | NEM Raise Regulation Requirement greater than 350 MW | Outage
F_Q_GSTONE4_RREG | 2 (0) | Out= NIL, Gladstone 4 RREG Requirement <= 0MW | Outage
F_Q_GSTONE2_R60 | 2 (0) | Out= NIL, Gladstone 2 R60 Requirement <= 0MW | Outage
F_Q_GSTONE2_RREG | 2 (0) | Out= NIL, Gladstone 2 RREG Requirement <= 0MW | Outage
F_Q_GSTONE2_R6 | 2 (0) | Out= NIL, Gladstone 2 R6 Requirement <= 0MW | Outage
F_Q_GSTONE3_RREG | 2 (0) | Out= NIL, Gladstone 3 RREG Requirement <= 0MW | Outage
F_Q_GSTONE1_R6 | 2 (0) | Out= NIL, Gladstone 1 R6 Requirement <= 0MW | Outage
F_Q_GSTONE1_R60 | 2 (0) | Out= NIL, Gladstone 1 R60 Requirement <= 0MW | Outage
F_Q_GSTONE1_RREG | 2 (0) | Out= NIL, Gladstone 1 RREG Requirement <= 0MW | Outage
F_MAIN+ML_L5_0400 | 2 (289) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN+ML_L60_0400 | 2 (271) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_Q_GSTONE1_LREG | 2 (0) | Out= NIL, Gladstone 1 LREG Requirement <= 0MW | Outage
F_T+CSGO_TG_R6 | 2 (1) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_T+NIL_ML_L5 | 2 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_Q_GSTONE2_LREG | 2 (0) | Out= NIL, Gladstone 2 LREG Requirement <= 0MW | Outage
F_ESTN++MLMO_L60 | 2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_S++HYSE_L6 | 2 (25) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 6 second requirement | Outage
F_S++HYML_L6 | 2 (5) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 6 second requirement | Outage
F_T+CSGO_TG_R5 | 2 (1) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_S++HYSE_L5 | 2 (25) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage
F_I+TG_R6_1000 | 2 (0) | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage
F_V+NIL_APD01_L60 | 2 (3) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_V+NIL_APD01_L6 | 1 (4) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_ESTN++HYTR_L5 | 1 (15) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_I+LREG_0250 | 1 (0) | NEM Lower Regulation Requirement greater than 250 MW | Outage
F_Q_GSTONE3_R60 | 1 (0) | Out= NIL, Gladstone 3 R60 Requirement <= 0MW | Outage
F_Q_GSTONE3_LREG | 1 (0) | Out= NIL, Gladstone 3 LREG Requirement <= 0MW | Outage
F_Q_GSTONE4_R60 | 1 (0) | Out= NIL, Gladstone 4 R60 Requirement <= 0MW | Outage
F_Q_GSTONE4_R6 | 1 (0) | Out= NIL, Gladstone 4 R6 Requirement <= 0MW | Outage
F_Q_GSTONE3_R6 | 1 (0) | Out= NIL, Gladstone 3 R6 Requirement <= 0MW | Outage
F_Q_GSTONE4_LREG | 1 (0) | Out= NIL, Gladstone 4 LREG Requirement <= 0MW | Outage
F_Q++LDTW_L5 | 1 (6) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
F_Q_CALL_B_2_LREG | 1 (0) | Out= NIL, Callide B2 LREG Requirement <= 0MW | Outage
F_T++NIL_ML_L60 | 1 (0) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_T++NIL_ML_L6 | 1 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_Q_STAN2_L6_ZERO | 1 (0) | Out= NIL, Stanwell 2 L6 Requirement <= 0MW | Outage
F_T+CSGO_TG_R60 | 1 (1) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_Q_TARONG#4_RREG | 1 (0) | Out= NIL, Tarong 4 RREG Requirement <= 0MW | Outage
F_Q_STAN2_RREG_ZERO | 1 (0) | Out= NIL, Stanwell 2 RREG Requirement <= 0MW | Outage
F_ESTN++MLSY_L6 | 1 (3) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 6 sec Requirement | Outage
F_MAIN++TG_R60_1000 | 1 (0) | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage
F_Q_STAN2_L60_ZERO | 1 (0) | Out= NIL, Stanwell 2 L60 Requirement <= 0MW | Outage
F_MAIN++RREG_0350 | 1 (0) | Mainland Raise Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
F_T++CSGO_TG_R6 | 1 (40) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
F_MAIN++TG_R5_1000 | 1 (0) | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage
F_T++BLSPS_EXP_L6_1 | 1 (1) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_T+FARE_N-2_TG_R6 | 1 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_T++BLSPS_EXP_L60_1 | 1 (1) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_MAIN++ML_L60_0400 | 1 (591) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_T+FARE_N-2_RREG | 1 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_T+FARE_N-2_TG_R60 | 1 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_QNV++HYMO_L5 | 0 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_ML_L5 | 0 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_T++BLSPS_EXP_L5 | 0 (1) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
F_S++HYML_L5 | 0 (2) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 5 minute requirement | Outage
F_Q++MUTW_R6 | 0 (1) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
F_Q++MUTW_R60 | 0 (1) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
F_Q++ARTW_R60 | 0 (19) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_ESTN++HYMO_L5 | 0 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
F_QNV+MLMO_L60 | 0 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T++FASH1_2C_TG_R6 | 0 (1) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T++NIL_BLSPS_L6_1 | 0 (0) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_ESTN++MLMO_L5 | 0 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
F_T++NIL_BLSPS_L60_1 | 0 (0) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_T+NIL_BB_TG_R6 | 0 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T++NIL_BLSPS_L5 | 0 (1) | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
F_Q++NIL_R5 | 0 (0) | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_Q++ARTW_R6 | 0 (26) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage
F_QNV+MLMO_L5 | 0 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN++LREG_0400 | 0 (0) | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
F_T+NIL_BB_TG_R60 | 0 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_Q_STAN2_LREG_ZERO | 0 (0) | Out= NIL, Stanwell 2 LREG Requirement <= 0MW | Outage
F_T++FARE_N-2_TG_R5 | 0 (4) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS | Outage
F_Q+RREG_0110 | 0 (0) | Qld Raise Regulation Requirement greater than 110 MW | Outage
F_Q+MG_R5 | 0 (0) | Raise 5 min Service Requirement for Qld Generation Event | Outage
F_Q+LREG_0110 | 0 (0) | Qld Lower Regulation Requirement greater than 110 MW | Outage
F_Q+ML_L60_0400 | 0 (0) | Lower 60 sec Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+ML_L6_0400 | 0 (0) | Lower 6 sec Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+ML_L5_0400 | 0 (0) | Lower 5 min Service Requirement for Qld Load Event, ML = 390 | Outage
F_T++NIL_BLSPS_L60_2 | 0 (1) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_QNV++HYMO_L6 | 0 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_STHN+LREG_0120 | 0 (0) | Southern Lower Regulation Requirement greater than 120 MW | Outage
F_STHN+APD_TL_L60 | 0 (0) | Lower 60 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_NVS++MG_R60 | 0 (0) | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_Q+MG_R60 | 0 (0) | Raise 60 sec Service Requirement for Qld Generation Event | Outage
F_STHN+MG_R5 | 0 (0) | Raise 5 min Service Requirement for a Southern Generation Event | Outage
F_NVS++MG_R6 | 0 (0) | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_Q+MG_R6 | 0 (0) | Raise 6 sec Service Requirement for Qld Generation Event | Outage
F_STHN+APD_TL_L5 | 0 (0) | Lower 5 min requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_T++NIL_BLSPS_L6_2 | 0 (1) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL

## Market Impact 2014
Constraint Equation ID | 2014 Marginal Values (2013 Marginal Values) | 2013 Hours (2012 Hours) | Description | Type | Region
T_TAMARCCGT_GCS | $4,333,860 ($877,585) | 503.5 (357.7) | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) | NIL | Tas
NSA_S_PORxxx | $3,587,599 ($1,796,463) | 23.3 (19.4) | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
S>V_NIL_NIL_RBNW | $2,478,435 ($433,772) | 239.8 (51.7) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink. | NIL | SA
Q>NIL_TR_TX1_4 | $2,171,661 ($1,479,171) | 164.8 (120.7) | Out = Nil, avoid overloading a Tarong 275/132 kV transformer ( No.1 or No.4) on trip of the other Tarong 275/132 kV transformer (No.1 or No.4) | NIL | Qld
T_MRWF_QLIM_xx | $1,653,083 ($2,720,517) | 133.3 (217.3) | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
V>>SML_NIL_1 | $1,581,992 ($89,828) | 28.3 (13.1) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
T>T_NIL_110_1 | $1,289,227 ($2,345,388) | 104.1 (188.5) | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
V>>SML_NIL_8 | $1,181,275 ($593,900) | 42.4 (29.3) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V>>V_NIL_1B | $729,653 ($40,047) | 10.6 (14.5) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
N^^V_NIL_1 | $701,455 ($28,564) | 208.8 (104.0) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
NSA_Q_BARCALDN | $560,383 ($1,856,454) | 53.4 (29.5) | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
V>>V_NIL_3 | $556,711 ($41,437) | 4.8 (1.3) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL | Vic
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | $522,292 ($898,361) | 72.2 (531.3) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
V_HWMW | $485,500 ($117,900) | 3.1 (0.8) | Out = Hazelwood PS to Morwell PS 220 kV line, Limit Morwell Units 4 & 5 upper limit set to zero | Outage | Vic
N>>N-NIL__3_OPENED | $441,872 (0) | 4.6 (0) | Out = Nil, avoid overloading Liddell to Muswellbrook 330kV line (83) on trip of Liddell to Tamworth 330kV line (84) | NIL | NSW
V>V_NIL_7 | $389,188 ($32,115) | 15.8 (2.0) | Out = Nil, avoid overloading either of Mount Beauty - Dederang 220 kV line for trip of Eildon - Thomastown 220 kV line | NIL | Vic
NSA_V_BDL0xxx | $353,989 ($267,895) | 5.3 (2.1) | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
F_T+LREG_0050 | $310,122 ($323,429) | 735.7 (622.6) | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
S>>V_NIL_SETX_SETX | $291,351 ($283,673) | 517.4 (455.3) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer This constraint equation binds when there is export from South Australia to Victoria and high generation from the wind farms and gas turbines in the south east of South Australia. | NIL | SA
F_T++NIL_TL_L6 | $258,371 ($179,206) | 2,401.8 (4,628.3) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
V>V_NIL_RADIAL_9 | $227,127 (0) | 51.6 (0) | Out = Nil, avoid O/L of Hazelwood to Jeeralang No. 4 220 kV line for trip of Hazelwood A4 500/220 kV transformer, Yallourn unit 1 in 500kV mode, radial mode, Hazelwood 3,4 busses split, feedback. | NIL | Vic
Q>NIL_BI_FB | $212,282 ($205,386) | 1,062.7 (492.6) | Out = Nil, avoid overloading on Boyne Island feeder bushing on Calliope River to Boyne Island 132 kV lines, for the contingent loss of a single Calliope River to Boyne Island 132 kV line | NIL | Qld
N_X_MBTE_3A & N_X_MBTE_3B | $209,639 ($318,168) | 1,661.8 (3,772.9) | Out = all three Directlink cables | Outage | NSW
N>Q-MUTW_2 | $203,895 ($85) | 4.3 (2.2) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage | NSW
V>>SML_NIL_1_5M | $175,148 (0) | 2.4 (0) | Out = Nil, avoid O/L Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Elaine To Moorabool 220 kV line and Mt Mercer Wind Farm, 5 minute line ratings, feedback | NIL | Vic
S>>NIL_SETB_KHTB1 | $166,195 ($5,916) | 196.5 (26.7) | Out = Nil, avoid overloading Keith - Tailem Bend #1 132kV on trip of South East - Tailem Bend 275kV line | NIL | SA
NSA_Q_GSTONE34_xxx | $163,070 ($1,759,776) | 68.9 (283.7) | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
V>S_NIL_HYTX_HYTX | $159,592 ($804,155) | 473.8 (990.8) | Out = Nil, avoid overloading the remaining Heywood 275/500 kV transformer on trip of one Heywood 275/500 kV transformer With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
F_T+NIL_TL_L6 | $155,782 ($122,298) | 757.2 (759.9) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
V^SML_NSWRB_2 | $147,459 ($257,099) | 62.8 (53.3) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
S_PLN_ISL1 | $143,590 ($29,489) | 0.9 (0.4) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
S_BRBG_CM | $139,181 (0) | 11.2 (0) | Out = Brinkworth to Redhill to Bungama 132kV lines. | Outage | SA
T_T_FASH_3_N-2 | $138,213 (0) | 4.3 (0) | Out = Nil, loss of both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link open, constrain Reece Unit 1 to 0 MW as per Transend advice | Outage | Tas
NRM_QLD1_NSW1 | $137,517 ($39,952) | 10.3 (30.4) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
F_T+NIL_BL_R6_1 | $135,791 ($29,906) | 921.4 (292.2) | Tasmania raise 6 second requirement for loss of Basslink, FCSPS available | NIL | FCAS
N_WOODLWN1_ZERO | $132,939 ($7,330) | 10.6 (0.6) | Discretionary upper limit for Woodlawn generation of 0 MW | Outage | NSW
F_I+NIL_MG_R5 | $132,829 ($79,125) | 7,677.7 (7,085.5) | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL | FCAS
F_T++LREG_0050 | $116,582 ($102,409) | 806.7 (926.3) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
N_X_MBTE2_A & N_X_MBTE2_B | $116,128 ($55,736) | 579.0 (196.1) | Out = two Directlink cables | Outage | NSW
T_T_FASH_4_N-2 | $87,578 (0) | 3.2 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link open, constrain Tribute to 0 MW as per Transend advice | Outage | Tas
F_I+NIL_MG_R6 | $86,177 ($60,255) | 6,733.5 (6,284.6) | NEM raise 6 second requirement for a NEM generation event | NIL | FCAS
N_MBTE1_B | $80,031 ($5) | 833.1 (0.3) | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
V>V_NIL_RADIAL_10 | $70,529 (0) | 7.5 (0) | Out = Nil, avoid O/L of Yallourn to Rowville No. 7 or No. 8 220 kV line for trip of the Yallourn to Rowville No. 8 or No. 7 220 kV line. Yallourn W1 on 220 kV side. Feedback | NIL | Vic
F_T++NIL_MG_R6 | $69,349 ($34,055) | 337.8 (569.9) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
Q>NIL_MRTA_B | $68,514 ($10,888) | 2.6 (0.8) | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line. | NIL | Qld
F_T+NIL_MG_R6 | $67,115 ($85,664) | 391.8 (310.6) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
Q:N_NIL_AR_2L-G | $66,726 (0) | 800.0 (0) | Out = Nil, avoid transient instability for a 2 line to Ground fault at Armidale | NIL | Qld
S_PLN_ISL2 | $65,308 ($42,585) | 0.6 (0.5) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
V>>S_NIL_SETB_SGKH | $63,809 ($533,537) | 287.4 (652.1) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line This will bind for high import into SA with high levels of generation from the wind farms and gas turbines in the south east. | NIL | SA
N^^Q_AR_VC_B1 | $63,434 ($341) | 8.7 (0.6) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
S_LB3_0 | $60,541 ($104,857) | 45.6 (155.8) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
V_T_NIL_FCSPS | $59,536 ($331) | 334.5 (1.0) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
V>S_460 | $59,053 ($191,827) | 159.3 (300.8) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
VTBL_ROC | $58,504 ($748,573) | 9.7 (14.3) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
NRM_NSW1_VIC1 | $56,053 ($249,334) | 1.5 (2.5) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V>>S_NIL_KHTB2_KHTB1 | $55,126 ($642) | 36.3 (3.3) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV one trip of Keith - Tailem Bend #2 132kV line, Feedback | NIL | SA
Q:N_AR_2L-G_-200 | $54,064 (0) | 430.1 (0) | Out = Bulli Creek CBs (8L2 and 99012) or (8M2 and 99022) | Outage | Qld
T>TU_LE_WA1_TUO_2 | $53,563 (0) | 12.8 (0) | Out = Tungatinah to Lake Echo to Waddamana No. 1 110kV line open at Tungatinah only (i.e. TU CB G152 OPEN), avoid O/L Tungatinah to Waddamana No.2 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
F_I+NIL_MG_R60 | $53,244 ($34,381) | 6,666.2 (6,255.8) | NEM raise 60 second requirement for a NEM generation event | NIL | FCAS
F_T+NIL_WF_TG_R6 | $50,940 ($877) | 269.0 (21.0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
V_HYML1_2 | $49,853 (0) | 1.1 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
V>>SML_NIL_7A | $48,808 ($34,306) | 42.6 (72.0) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line This constraint equation only binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for high flows on Murraylink into SA. | NIL | Vic
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | $48,248 ($9,407) | 844.3 (202.1) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. | NIL | Vic
F_T+FASH_N-2_TG_R6 | $46,937 (0) | 3.3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
V>V_NIL_GGMS_1 | $45,900 ($71,167) | 59.4 (35.4) | Out = Nil, avoid overloading Guthega to Murray (97G/3) 132 kV line | NIL | Vic
T>T_NIL_LIPM_N-2_2A | $42,618 ($7,495) | 14.4 (13.9) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to North) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
F_S++HYSE_L6 | $39,301 ($105,639) | 1.6 (25.2) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 6 second requirement | Outage | FCAS
N^^V_NIL_2 | $38,516 ($45,018) | 4.8 (23.7) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL | NSW
F_T++RREG_0050 | $38,470 ($5,963) | 1,034.0 (319.1) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
F_T+RREG_0050 | $36,255 ($35,604) | 611.9 (343.7) | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_APD_TL_L5 | $35,889 (0) | 5,722.8 (0) | NEM Lower 5 min Service Requirement for the loss of APD potlines | NIL | FCAS
T_MRWF_UPLIM | $35,035 ($71,858) | 2.8 (5.8) | Limit Musselroe generation to current MW + 10 | Outage | Tas
F_MAIN++NIL_MG_R6 | $33,834 ($16,476) | 1,582.8 (1,547.3) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
F_Q++ARDM_L6 | $31,494 ($326) | 271.1 (13.2) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
V>V_HW_TX12_35_OPT1 | $30,769 (0) | 2.9 (0) | Out = Hazelwood A1 or A2 500/220 kV txfmr, HWTS A3 txfmr switched to HWPS No. 2 bus, avoid O/L Yallourn to Rowville No. 7 or 8 220 kV line on trip of Hazelwood A4 txfmr, 3/5 parallel mode, JLGA connected to HWPS B3/4 side, feedback | Outage | Vic
CA_MQS_42D83B89_01 | $30,046 (0) | 3.3 (0) | Constraint Automation, O/L 275KV_8859 @H58_LARC for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[MANFR] Host MANEEMP2(MQ) | Outage | Constraint Automation
F_T+FARE_N-2_TG_R6 | $29,891 (0) | 0.7 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
S>NIL_NIL_MYSG-T | $29,844 ($42,258) | 54.8 (55.4) | Out = Nil, avoid overloading Mayura to Snuggery 132 kV line on no line trips | NIL | SA
N>LSDU9U6_LSDU9U7 | $29,817 ($11,683) | 5.8 (0.8) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
V>>S_HYML_1 | $29,748 ($22,360) | 19.6 (89.4) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 1 | Outage | SA
T>>T_NIL_BL_EXP_6E | $29,369 ($25,118) | 13.1 (73.3) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
V_T_NIL_BL1 | $29,369 ($4,264) | 164.3 (9.3) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
F_MAIN+NIL_MG_R6 | $29,116 ($9,508) | 759.8 (729.4) | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
F_T++NIL_BL_R6_2 | $28,999 (0) | 116.3 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 400ms | NIL | FCAS
VSML_ZERO | $28,835 ($641,565) | 47.3 (424.2) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
N_BLTU_97B | $27,173 (0) | 0.6 (0) | Blowering PS upper limit set to zero due to outage of Blowering to Tumut 97B 132kV line. | Outage | NSW
V>>S_NIL_PWKN_SGKH | $27,122 ($161,160) | 68.5 (40.9) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL | SA
F_S++HYSE_L5 | $27,068 ($43,215) | 1.7 (24.3) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage | FCAS
S_DVNP_NP1 | $27,000 (0) | 0.2 (0) | Out=Davenport Northern U1 275kV line | Outage | SA
F_T++NIL_WF_TG_R6 | $26,612 ($91) | 244.5 (5.2) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL | FCAS
T_LE_ZERO | $26,200 (0) | 0.2 (0) | Discretionary 0 MW upper limit on Lake Echo generation | Outage | Tas
Q>NIL_MRTA_A | $25,396 ($3,944) | 1.2 (0.3) | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line. | NIL | Qld
N^N_KKLS_1 | $25,333 ($5,717) | 109.8 (81.8) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
N>Q_LSLS_9U8 | $24,855 ($1,379) | 5.5 (4.4) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage | NSW
F_T+CSGO_TG_R6 | $23,683 ($1) | 1.5 (0.2) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
V::N_NIL_xxx | $23,304 ($302) | 317.1 (10.6) | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
T>T_TUBUS_SPLIT_1 | $22,777 (0) | 1.8 (0) | Out = Tungatinah 110 kV bus section, Derwent 110 kV system split at Tungatinah, avoid O/L Tungatinah to New Norfolk No. 1 110 kV line on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
F_Q++ARDM_L5 | $22,655 ($156) | 243.8 (5.3) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
F_MAIN+NIL_MG_R5 | $21,990 ($11,752) | 759.8 (729.4) | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
T>T_X_TUWA_TWO_TUTA | $21,675 (0) | 2.0 (0) | Out = Both Tungatinah to Waddamana 110kV lines (direct and via Lake Echo tee), avoid O/L remaining Tungatinah to Tarraleah line (flow to South) for loss of the parallel line | Outage | Tas
F_I+NIL_DYN_RREG | $21,424 ($11,796) | 2,273.8 (1,879.9) | NEM raise regulation requirement | NIL | FCAS
F_MAIN++NIL_MG_R5 | $20,838 ($13,770) | 1,043.5 (1,465.7) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
T>T_HAGT_N-2 | $20,683 ($69,112) | 15.3 (13.3) | Out=NIL, Loss of both Hadspen to George Town 220kV lines or Palmerston to Hadspen 220kV lines declared credible, Restrict the power flow on HA-GT corridor based on AETV CCGT service status | Outage | Tas
F_MAIN++NIL_MG_R60 | $20,480 ($15,184) | 1,839.7 (2,423.9) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
F_MAIN++APD_TL_L5 | $20,120 (0) | 1,979.3 (0) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL | FCAS
T>>T_NIL_BL_EXP_5F | $19,618 ($141,737) | 7.4 (43.0) | Out = Nil, avoid overloading a Hadspen to George Town 220 kV line for trip of the other Hadspen to George Town 220 kV line considering NCSPS action | NIL | Tas
CA_MQS_42084A52_01 | $18,824 (0) | 2.7 (0) | Constraint Automation, O/L ROBNWB_1 @R_TOWN for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1 2&3MWPS. Generated by STNET[MANFR] Host MANEEMP1(MQ) | Outage | Constraint Automation
F_S++HYSE_L60 | $18,772 ($237,136) | 12.2 (105.0) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage | FCAS
F_MAIN+NIL_MG_R60 | $18,624 ($7,845) | 759.8 (729.4) | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
F_T+NIL_MG_R5 | $18,239 ($18,540) | 183.8 (304.9) | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_T+NIL_MG_R60 | $18,187 ($15,437) | 391.1 (309.7) | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_DYN_LREG | $17,614 ($27,464) | 4,221.3 (5,353.6) | NEM lower regulation requirement | NIL | FCAS
S^NIL_PL_MAX | $17,507 ($56,109) | 1.4 (3.5) | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | $17,162 ($5) | 132.5 (0.6) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
V>>V_NIL_5 | $17,039 ($1,289) | 14.2 (5.6) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
V^^S_NIL_MAXG_xxx | $16,984 ($34,225) | 178.6 (209.0) | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off There are two constraint equations that make up the voltage stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
TVBL_ROC | $16,666 ($2,637) | 12.1 (13.3) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
V>SMLBAHO1 | $16,558 ($5,717) | 23.2 (6.2) | Out = Ballarat to Horsham, or Bendigo to Kerang line, avoid overloading or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang or Ballarat to Horsham line | Outage | Vic
N>>V-NIL_O | $14,935 ($63,883) | 2.2 (1.3) | Out = Nil, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line and subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | NIL | NSW
VT_300 | $14,682 (0) | 2.1 (0) | Vic to Tas on Basslink upper limit of 300 MW | Outage | Vic
S>NIL_WERB_WEWT | $14,664 (0) | 17.2 (0) | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
V>>SML_NIL_7B | $14,455 ($5,780) | 31.1 (20.5) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
S_PLN_ISL31 | $13,858 ($14,282) | 1.6 (0.3) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
VSML_000 | $13,832 (0) | 0.9 (0) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
T_MB_ZERO | $13,500 (0) | 0.1 (0) | Limit Meadowbank to zero MW | Outage | Tas
CA_SPS_428FB629_01 | $13,100 (0) | 0.1 (0) | Constraint Automation, O/L 94E @MT_PIPER for CTG LNWT on trip of MT_PIPER-WWANG 70 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
F_Q+LREG_0110 | $13,100 (0) | 0.1 (0) | Qld Lower Regulation Requirement greater than 110 MW | Outage | FCAS
F_Q+MG_R5 | $13,100 (0) | 0.1 (0) | Raise 5 min Service Requirement for Qld Generation Event | Outage | FCAS
F_Q+MG_R60 | $13,100 (0) | 0.1 (0) | Raise 60 sec Service Requirement for Qld Generation Event | Outage | FCAS
F_Q+ML_L60_0400 | $13,100 (0) | 0.1 (0) | Lower 60 sec Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS
F_Q+ML_L6_0400 | $13,100 (0) | 0.1 (0) | Lower 6 sec Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS
F_Q+RREG_0110 | $13,097 (0) | 0.1 (0) | Qld Raise Regulation Requirement greater than 110 MW | Outage | FCAS
T>T_NIL_BL_IMP_1B | $13,040 ($52,006) | 0.1 (299.3) | Out = Nil, avoid overloading either Gordon to Chapel St 220 kV line for trip of the other Gordon to Chapel St 220 kV line with no SPS action This constraint equation binds at times of high Gordon generation when the NCSPS control scheme is unavailable. | NIL | Tas
V>SMLHORC1 | $12,971 ($26) | 2.2 (0.3) | Out = Horsham to Red Cliffs 220kV line, avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line | Outage | Vic
F_Q++ARDM_L60 | $12,457 ($45) | 271.4 (12.2) | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 60 sec Requirement | Outage | FCAS
N^Q_NIL_A | $12,007 ($58,192) | 4.6 (32.8) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
T^V_NIL_8 | $11,988 ($1,492) | 53.9 (16.2) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
SVML_ZERO | $11,857 ($8,869) | 170.0 (174.7) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
S>RBTU2_DVBG_WEWT | $11,509 (0) | 3.8 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines; avoid O/L Waterloo East-Waterloo 132kV line on trip of Davenport - Bungama 275KV line. | Outage | SA
S>>V_NIL_RBTX_MW4RB | $11,477 (0) | 135.3 (0) | Out= Nil, avoid O/L Morgan Whyalla 4 to Robertstown line on trip of one Robertstown 275/132kV transformer, Feedback | NIL | SA
V>S_NIL_NIL_HYTX2 | $10,741 ($135) | 0.4 (0.3) | Out = NIL, avoid O/L Heywood M2 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL | Vic
T>T_X_TU_LE_WA_TWO_1 | $10,163 (0) | 1.7 (0) | Out = Both Tungatinah to Waddamana 110kV lines (direct and via Lake Echo tee), avoid O/L Meadowbank Tee 2 to New Norfolk on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
V>>V_NIL_4A | $9,858 ($14,004) | 0.3 (0.6) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. Similar to DBUSS - Line, the DBUSS – Transformer scheme splits the Dederang 330 kV bus on trip of a Dederang transformer. | NIL | Vic
T^V_NIL_BL_6 | $8,967 ($12,858) | 86.8 (132.8) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
F_MAIN+APD_TL_L5 | $8,768 (0) | 695.7 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS
V>V_NIL_ROYP56_R2_1 | $8,693 (0) | 15.6 (0) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 220 kV, feedback | NIL | Vic
S>>V_NIL_NOTI_x & S>NIL_NOTI_x | $8,345 ($192,236) | 2.8 (68.8) | Out = Nil, avoid overloading the Torrens Island to New Osborne No.4 66 kV line for trip of the Torrens Island to New Osborne No.3 66 kV line, Torrens Island 66 kV bus split These constraint equations manage the flows on the Torrens Island to New Osborne No.3 and No.4 66 kV lines for different configurations of the Torrens Island 66 kV bus. The different constraint equations were created in early 2013 following the splitting of the Torrens Island 66 kV bus. Their binding results have been combined. These constraint equations generally bind for high output from the Quarantine gas turbines. | NIL | SA
CA_SPS_4317B056_01 | $7,564 (0) | 0.8 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
F_T+NIL_BL_R60_1 | $7,187 ($1,049) | 781.4 (205.3) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL | FCAS
V_MTMERCER_ZERO | $7,185 (0) | 0.6 (0) | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
F_T++NIL_TL_L60 | $6,821 ($15,828) | 2,333.4 (5,129.3) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
V>>S_NIL_NIL_SGKHC | $6,670 ($2,143) | 2.9 (7.3) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on Nil trip, Feedback | NIL | SA
F_Q+ML_L5_0400 | $6,548 (0) | 0.1 (0) | Lower 5 min Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS
F_T++BL_650_R6_2 | $6,421 (0) | 12.0 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage | FCAS
N>N-LSTN_TE_C1 | $6,323 ($60) | 11.3 (0.8) | Out = Lismore to Tenterfield (96L) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
T>T_LIPM_110_2A | $6,087 (0) | 15.8 (0) | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
F_MAIN++TL_L5_0500 | $6,033 ($2) | 428.5 (1.5) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage | FCAS
F_I+NIL_APD_TL_L60 | $5,986 (0) | 3,889.8 (0) | NEM Lower 60 sec Service Requirement for the loss of APD potlines | NIL | FCAS
S_LB2WF_CONF | $5,913 ($4,644) | 9.3 (4.6) | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
T>T_FASH_1_2_C1 | $5,788 ($3,334) | 17.5 (11.4) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hampshire link closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
F_T++BL_650_R6_3 | $5,492 (0) | 16.9 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage | FCAS
N_GUNNING1_ZERO | $5,484 ($6,736) | 5.3 (6.3) | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
T>T_NIL_LIPM_N-2_2B | $5,480 ($22) | 9.1 (0.5) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
F_T+NIL_WF_TG_R5 | $5,378 ($743) | 236.8 (20.7) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
T_PMPO_110 | $5,128 (0) | 28.9 (0) | Out=A single Palmerston-Poatina 110KV line. One line out of service only | Outage | Tas
V>>V-MSUT_1 | $5,040 ($1,906) | 89.5 (42.9) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | Outage | Vic
F_T++NIL_TL_L5 | $4,698 ($2,815) | 732.7 (1,439.3) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
F_MAIN++APD_TL_L60 | $4,675 (0) | 1,854.8 (0) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL | FCAS
F_I+TL_L5_0500 | $4,569 ($33) | 1,274.7 (13.3) | NEM lower 5 min Service Requirement for a NEM network event | Outage | FCAS
F_S++HYML_L60 | $4,487 ($117,500) | 9.8 (14.7) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 60 second requirement | Outage | FCAS
F_T+NIL_TL_L5 | $4,407 ($1,767) | 750.8 (690.8) | Out=Nil, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
Q:N_ARSVC_AR_2L-G | $4,363 (0) | 52.4 (0) | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
VS_250 | $4,322 ($8,669) | 55.4 (27.3) | Victoria to South Australia on Heywood upper transfer limit of 250 MW This constraint equation is included in a number of constraint sets which are used for outages of the 500 kV lines in from Sydenham to Heywood and the 275 kV lines from Heywood to South East. | Outage | Vic
F_Q++ARTW_L6 | $4,285 ($167) | 59.4 (10.4) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
F_T+NIL_BL_R5 | $4,159 ($1,421) | 407.4 (160.6) | Tasmania raise 5 minute requirement for loss of Basslink, FCSPS available | NIL | FCAS
F_Q++ARTW_L60 | $3,962 ($41) | 59.1 (9.7) | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS
S>>NIL_NIL_TINO3 | $3,958 (0) | 0.3 (0) | Out= Nil with Torrens Island 66kV CB6W2, CB6E4 & CB6C6 open, avoid O/L Torrens Island - New Osborne No.3 66kV line on Nil trip, Feedback | NIL | SA
T_V_NIL_BL1 | $3,847 ($13,024) | 46.2 (5.3) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
Q:N_BI_POT_-050 | $3,810 (0) | 3.3 (0) | Nominated Offset -50MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage | Qld
S>>NIL_SETB_KHTB2 | $3,504 ($7,892) | 50.9 (18.8) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
S-SNWWF_0 | $3,450 (0) | 5.1 (0) | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | SA
V>>V_BAELML_1 | $3,389 (0) | 2.9 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage | Vic
T>T_TANN2_110_2 | $3,192 (0) | 0.5 (0) | Out = Tarraleah to New Norfolk No. 2 110 kV line, avoid O/L the Tungatinah to New Norfolk No. 1 110 kV line (flow to South) on trip of Meadowbank to New Norfolk 110 kV line, feedback | Outage | Tas
VT_ZERO | $3,138 ($4,034) | 4.5 (8.1) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
T_FAJB | $3,103 (0) | 0.3 (0) | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Tas
V::N_HWSM_xxx | $3,092 ($337) | 31.1 (8.1) | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
S>>BRBG_BGTX_HUWT | $3,073 (0) | 3.3 (0) | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | SA
S>NIL_BWPA_HUWT | $2,905 ($1,512) | 3.9 (1.5) | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West - Para 275kV line, Feedback | NIL | SA
F_I+TL_L60_0500 | $2,788 ($3) | 976.7 (6.3) | Lower 60 sec Service Requirement for a NEM Network Event, TL = 500 | Outage | FCAS
F_T+NIL_WF_TG_R60 | $2,785 ($189) | 267.8 (21.0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
F_Q++ARTW_L5 | $2,622 ($573) | 51.3 (6.6) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
T_T_FASH_7_N-2 | $2,537 (0) | 9.6 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, Hampshire link open, limit all West Coast generation <= 110% of West Coast load | Outage | Tas
F_T++NIL_MG_R60 | $2,537 ($7,469) | 308.0 (327.4) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
F_I+ML_L6_0400 | $2,527 ($3,925) | 3,125.0 (3,416.4) | NEM lower 6 second requirement for a NEM load event | NIL | FCAS
F_MAIN+NIL_DYN_RREG | $2,458 ($2,253) | 182.3 (109.0) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL | FCAS
T::T_HA_GT_PM_5 | $2,405 (0) | 0.3 (0) | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT in service. | Outage | Tas
F_MAIN+APD_TL_L60 | $2,396 (0) | 692.8 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS
T>T_GT_HA_3A_N-2 | $2,383 ($9,658) | 5.6 (11.3) | Out = NIL, Loss of both Hadspen to Georgetown 220kV lines declared credible, avoid O/L the Sheffield to Palmerston 220 kV line (flow to North) for loss of both Hadspen to Georgetown 220 kV lines | Outage | Tas
T>T_TUBUS_TATU1_1 | $2,381 (0) | 5.6 (0) | Out = Tungatinah 110 kV bus section and Tarraleah to Tungatinah No. 1 110 kV line, avoid O/L Tungatinah to New Norfolk No. 1 110 kV line on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
N>N-NIL_LSDU | $2,318 ($325,000) | 0.4 (159.6) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
V>V_HWJL3-4_RAD | $2,245 (0) | 0.9 (0) | Outage = Hazelwood to Jeeralang No.3 or No.4 220kV line, limit HWPS units3,4,5 and Jeeralang A to avoid O/L HWTS A1 Tx for trip of HWPS-JLTS No.4 or No.3 220kV line, Radial Mode with 1&2 busses split and 3&4 busses split or tied | Outage | Vic
T_T_FASH_5_N-2 | $2,202 ($249) | 2.0 (0.5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Mackintosh P/S unavailable, Hampshire link open, limit Mackintosh + Tribute + Reece 1 <= 110% of West Coast load | Outage | Tas
T>T_X_TU_LE_WA_TWO | $2,077 (0) | 3.7 (0) | Out = Both Tungatinah to Waddamana 110kV lines open (direct and via Lake Echo tee), avoid O/L New Norfolk to Creek Rd line for loss of New Norfolk to Chapel St line , feedback | Outage | Tas
S>>BWPA_DVBR_RHBG-T | $2,060 (0) | 1.4 (0) | Out= Blyth West- Para 275kV line with Bungama CB6539 OPEN, avoid O/L Redhill- Brinkworth 132kV T line on trip of Davenport-Brinkworth 275kV line, Feedback | Outage | SA
V:T_SHGT_BL_1 | $2,047 (0) | 9.8 (0) | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Vic
V^^S_RBTU2_MAXG | $2,031 (0) | 11.3 (0) | Out= Robertstown - Para and Robertstown - Tungkillo 275 kV lines; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
T::T_NIL_4 | $1,853 (0) | 16.2 (0) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
F_T_REECE2_DS_R6 | $1,759 ($69) | 8.2 (5.8) | Determine upper limit for R6 FCAS enablement for Reece 2 based on FCAS Boost Mode status point for unit | NIL | FCAS
F_T+NIL_TL_L60 | $1,755 ($1,435) | 756.9 (760.1) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
T>T_NIL_BL_3C | $1,749 ($16,525) | 11.8 (136.3) | Out = Nil, avoid overloading a Hadspen to Palmerston 220 kV line for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action | NIL | Tas
CA_SPS_42008454_01 | $1,719 (0) | 0.3 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
V>>V_NIL1A_R | $1,706 ($1,104) | 23.1 (30.4) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line This constraint equation only binds for high flows from Victoria to NSW | NIL | Vic
N>N-X_9U6_9G2_2 | $1,617 (0) | 7.9 (0) | Out = one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5), avoid O/L remaining 132kV line, Qld to NSW limit | Outage | NSW
F_T++NIL_MG_R5 | $1,563 ($1,322) | 320.4 (230.6) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
F_T++NIL_BL_R60_2 | $1,533 (0) | 322.4 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 400ms | NIL | FCAS
F_Q++MUTW_L6 | $1,502 (0) | 19.8 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS
F_Q++MUTW_L60 | $1,422 (0) | 20.4 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS
N^^Q_ARDM_B1 | $1,413 ($241) | 0.2 (3.3) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage | NSW
Q>N-MUTE_758 | $1,356 (0) | 20.8 (0) | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
V_MACARTHUR_ZERO | $1,352 ($16,117) | 1.1 (15.2) | Macarthur upper limit of 0 MW | Outage | Vic
N^^Q_ARTW_B1 | $1,319 (0) | 0.1 (0) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
T>T_MBTU_110_1 | $1,269 (0) | 3.7 (0) | Out = Tungatinah to Meadowbank 110 kV line, avoid O/L Tungatinah to New Norfolk No. 2 110 kV line (flow to South) on trip of Tungatinah to New Norfolk No. 1 110 kV line, feedback | Outage | Tas
V>V_NIL_RADIAL_6 | $1,268 (0) | 0.1 (0) | Out = Nil, avoid O/L of Hazelwood A3 500/220kV transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, radial mode, Hazelwood 1,2,3,4 busses split, feedback | NIL | Vic
T_V_NIL_FCSPS | $1,263 ($616) | 2.3 (3.5) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
T_X_GTHA_1 | $1,260 (0) | 1.5 (0) | Outage = Both Hadspen to Georgetown 220kV lines, limit Southern + Poatina + Trevallyn generation <= South + North load + 10MW, limiting PM-SH line flow to 10 MW | Outage | Tas
V>>V_MLTS_TX_2A_R | $1,218 (0) | 22.7 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage | Vic
Q:N_AR_2L-G_-150 | $1,209 (0) | 21.3 (0) | Nominated Offset -150MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | Outage | Qld
T^T_NIL_BL_6_DS | $1,183 (0) | 1.8 (0) | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah-Waddamana-Palmerston 220 kV line, dispatch equation only | NIL | Tas
T_X_TUWA2_CRNN_1 | $1,178 (0) | 2.1 (0) | Out = Tungatinah to Waddamana No. 2 and New Norfolk to Creek Rd 110 kV lines, avoid O/L Lake Echo Tee to Waddamana No. 1 110 kV line section on trip of New Norfolk to Chapel St 110 kV line, feedback | Outage | Tas
T>T_NIL_BL_IMP_7CC | $1,153 ($29) | 5.8 (0.3) | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V>>V_KTS_TX_A2_2A_R | $1,138 (0) | 12.6 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
V>>SML_BESH_1 | $1,133 (0) | 5.3 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Waubra to Horsham 220 kV line section for trip of the Ballarat to Bendigo 220 kV line, feedback | Outage | Vic
V::N_SMCSVxxx | $1,112 (0) | 5.8 (0) | Out = South Morang 330kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
CA_SPS_42009181_01 | $1,057 (0) | 0.3 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
V^S_HYCP | $1,048 (0) | 21.2 (0) | Out = Nil, limit Vic to SA to avoid voltage collapse in Heywood area for loss of a 500 kV circuit between Moorabool and Heywood with automatic allowance for Heywood 275 kV capacitor bank status | NIL | Vic
F_MAIN+TL_L5_0500 | $1,040 (0) | 45.0 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS | Outage | FCAS
T>T_NIL_BL_IMP_5F | $1,025 ($26,971) | 11.7 (327.1) | Out = Nil, avoid overloading Hadspen to Georgetown No.1 220 kV line (flow to North) for trip of the Hadspen to Georgetown No.2 220 kV line with no SPS action This constraint only binds when the NCSPS control scheme is unavailable. | NIL | Tas
I_CTRL_ISSUE_TE | $1,015 ($153) | 23.0 (3.8) | DC Link Control Issue Constraint for Terranora | Outage | Other
T_T_FASH_1_N-2 | $1,010 (0) | 4.3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
T_T_FASH_HM_OPEN_1 | $993 (0) | 1.9 (0) | Out = one Farrell to Sheffield 220kV line, Hampshire link open, Farrell 220 kV bus not split, limit West Coast gen <= 110% of West Coast load | Outage | Tas
F_MAIN++ML_L6_0400 | $985 ($861) | 1,080.8 (534.5) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
V>>V_NIL_8 | $980 (0) | 0.3 (0) | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines; Feedback | NIL | Vic
V:T_NIL_BL_1 | $951 (0) | 3.2 (0) | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
V::N_MSUT_xxx | $943 ($898) | 20.9 (17.4) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
N^Q_TW_330_BUS3_1 | $919 (0) | 6.8 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage | NSW
V>SML_NSWRB_10 | $913 (0) | 0.5 (0) | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
F_T++NIL_WF_TG_R5 | $903 ($16) | 118.5 (6.0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL | FCAS
F_MAIN++ML_L6_APD | $891 ($7) | 459.3 (4.6) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
V>>V_LTMS_1 | $879 (0) | 10.8 (0) | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage | Vic
V::N_MLTX_xxx | $857 (0) | 13.8 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V::N_JNWO_xxx | $855 (0) | 8.2 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V::N_ROSM_xxx | $808 (0) | 3.5 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
Q>N-MUTE_757 | $806 (0) | 16.3 (0) | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
V::N_DDSM_xxx | $801 (0) | 9.0 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
F_MAIN++NIL_DYN_LREG | $778 ($33) | 143.2 (4.0) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL | FCAS
V>>SML_BESH_3 | $667 (0) | 3.1 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line (flow from MLTS to BATS) for trip of the Moorabool to Elaine to Ballarat 220 kV line and Mt Mercer Wind Farm, feedback | Outage | Vic
F_MAIN+ML_L6_0400 | $646 ($632) | 565.3 (366.6) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
T>>T_NIL_BL_EXP_7C | $634 ($172) | 1.7 (0.5) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
S>NIL_HUWT_STBG | $626 ($154) | 0.7 (0.2) | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line. | NIL | SA
T_CESH | $616 (0) | 0.5 (0) | Out=Sheffield-Cethana 220KV line. Energy <= 0MW | Outage | Tas
V::S_HYSE | $593 ($114) | 10.3 (3.2) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of one NPS unit or the remaining South East - Heywood 275 kV line. | Outage | SA
F_Q++LDMU_L6 | $588 (0) | 7.8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage | FCAS
V>V_NIL_RADIAL_3 | $582 (0) | 1.2 (0) | Out = Nil, avoid O/L of Hazelwood A1 500/220kV transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, radial mode, Hazelwood 1,2,3,4 busses split, feedback | NIL | Vic
F_MAIN++NIL_DYN_RREG | $574 ($928) | 46.8 (46.3) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL | FCAS
V>SML_BUDP_2 | $552 ($32,746) | 5.9 (13.3) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
T>T_NIL_BL_IMP_6EE | $552 ($126) | 2.5 (1.8) | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V>>V_MLTS_TX_2B_R | $541 (0) | 15.8 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood | Outage | Vic
F_I+ML_L5_0400 | $528 ($16,102) | 171.0 (5,981.2) | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL | FCAS
T>T_PM_TX_1A | $515 ($15) | 8.8 (0.3) | Out= Palmerston 220/110kV transformer, prevent overload of either Palmerston to Hadspen 110kV line (flow to North) for trip of the parallel Palmerston to Hadspen 110 kV line, feedback | Outage | Tas
V>>V_KTS_TX_A2_2_P | $493 ($12) | 4.6 (0.8) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage | Vic
VSML_220 | $488 ($65,147) | 1.6 (67.9) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
S>>BWPA_BRTW_WTTP | $484 (0) | 0.6 (0) | Out= Blyth West- Para 275kV line with Bungama CB6539 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | SA
VT_000 | $479 (0) | 0.9 (0) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
N>N-LS_TX_TE_B | $470 ($6) | 0.2 (0.3) | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. DS only | Outage | NSW
T^V_NIL_9 | $453 (0) | 1.1 (0) | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
V::N_JNWG_xxx | $452 ($18) | 3.0 (0.6) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V::N_LTWG_xxx | $447 ($127) | 5.5 (2.1) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
F_Q++LDMU_L60 | $444 (0) | 7.8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage | FCAS
T>T_NIL_TOV_5F | $444 (0) | 9.3 (0) | Out = Nil, avoid TOV following NCSPS slow action for O/L of Hadspen to Georgetown No. 1 220 kV lines (flow to North) for trip of the Hadspen to Georgetown No. 2 220 kV line, considering status of Tamar CCGT, feedback equation | NIL | Tas
V>SMLBAHO4 | $420 ($21,603) | 7.2 (41.0) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage | Vic
T>T_TUNN2_2 | $416 (0) | 0.8 (0) | Out = Tungatinah to New Norfolk No. 2 110 kV line, avoid O/L the Tungatinah to New Norfolk No.3 110 kV line (flow to South) on trip of Tungatinah to New Norfolk No. 1 110 kV line, feedback | Outage | Tas
N^^V_MSUT_1 | $409 ($176) | 6.9 (1.8) | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
N>>N-NIL__2_OPENED | $408 (0) | 0.5 (0) | Out= NIL, avoid O/L Liddell to Tamworth (84) on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
F_MAIN+NIL_DYN_LREG | $401 ($855) | 102.3 (67.3) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL | FCAS
F_Q++MUTW_L5 | $395 (0) | 13.8 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS
V>>S_RBTU2_BRPA_WTTP | $393 (0) | 1.9 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | SA
T_FASH_MAXGEN_1 | $388 ($2,761) | 1.5 (7.9) | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link closed. Constraint swamped if only one machine on line | Outage | Tas
V>>N-NIL_HA | $379 ($416) | 4.7 (3.1) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL | Vic
V::N_BUDP_xxx | $374 (0) | 3.2 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
T>T_TUNN2_1 | $362 (0) | 0.9 (0) | Out = Tungatinah to New Norfolk No. 2 110 kV line, avoid O/L the Tungatinah to New Norfolk No. 1 110 kV line (flow to South) on trip of Tungatinah to New Norfolk No.3 110 kV line, feedback | Outage | Tas
T_T_FASH2_A_2 | $354 (0) | 0.4 (0) | Out = Farrell to Sheffield No.1 or 2 line with Tribute and Reece 1 supplying Sheffield, Hampshire link closed, limit Bastyan + Reece 2 + John Butters + Mackintosh >= 90% of West Coast load | Outage | Tas
F_MAIN+ML_L6_APD | $346 ($5) | 171.5 (2.0) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
T>T_GTSH_IMP_4K | $341 ($1,514) | 1.5 (10.0) | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
T>T-X_TUTA | $325 (0) | 0.1 (0) | Out = both Tarraleah to Tungatinah 110 kV line, avoid pre-contingent O/L of the Tarraleah to New Norfolk No. 2 110 kV, feedback | Outage | Tas
F_T++FARE_N-2_TG_R6 | $325 ($611) | 2.6 (3.8) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
N^^V_EPMB_1 | $323 (0) | 2.6 (0) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
VN_0700 | $318 (0) | 4.3 (0) | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage | Vic
F_QNV++MLMO_L60 | $315 (0) | 15.9 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
V>>V_KTS_TX_A3_2B_R | $314 (0) | 9.6 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Vic
I_CTRL_ISSUE_ML | $312 (0) | 12.6 (0) | DC Link Control Issue Constraint for Murraylink | Outage | Other
T_TA_60 | $307 (0) | 0.7 (0) | Discretionary 60 MW upper limit on total Tarraleah generation | Outage | Tas
S_PLN_ISL32 | $306 ($30,722) | 0.4 (0.7) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T>T_NIL_BL_5C | $298 ($7,158) | 2.8 (89.2) | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
N^^V_MSDD1 | $297 (0) | 3.3 (0) | Out = Murray to Dederang No.1 or No.2 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
TV_ZERO | $296 ($233) | 0.1 (0.8) | Tas to Vic on Basslink upper limit of 0 MW | Outage | Tas
T>T_TULEWA1_TUNN2_1 | $295 (0) | 0.6 (0) | Out = Tungatinah to New Norfolk No. 2 and Tungatinah to Lake Echo to Waddamana No. 1 110 kV lines, avoid O/L Tungatinah to Waddamana No. 2 110 kV line (flow to North) on trip of Tungatinah to New Norfolk No.3 110 kV line, feedback | Outage | Tas
T_T_BA_JB_RC2_250 | $290 ($489) | 3.0 (8.3) | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
T_ROCOF_3 | $290 (0) | 1.8 (0) | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | Tas
S_LB2_63 | $286 (0) | 0.5 (0) | Discretionary upper limit for Lake Bonney 2 generation of 63 MW | Outage | SA
V>V_X_ROYP_78_8 | $268 (0) | 2.6 (0) | Out = Rowville to Yallourn No. 7 and No. 8 220 kV lines, avoid O/L Yallourn to Hazelwood No. 1 220 kV line on trip of Yallourn to Rowville No. 6 220 kV line, YWG1 on 220 kV side, feedback | Outage | Vic
VS_400 | $265 (0) | 1.3 (0) | Victoria to SA on VicSA upper transfer limit of 400 MW | Outage | Vic
F_T+BL_650_R6_1 | $263 ($12) | 6.1 (1.3) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage | FCAS
V>>V_EPTT_3 | $262 (0) | 5.0 (0) | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to North) for loss of the parallel line, feedback | Outage | Vic
V^^S_PAVC_MAXG | $260 ($6,881) | 3.4 (36.2) | Out = Para one SVC, VIC to SA Voltage Stability limit for loss of the largest generation unit in SA | Outage | SA
T>T_FASH_1_N-2 | $259 ($14,961) | 1.1 (12.2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
F_Q++LDMU_L5 | $255 (0) | 7.8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage | FCAS
V>>S_HYML_2 | $252 ($21,941) | 7.6 (58.0) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 2 | Outage | SA
F_Q++LDTW_R6 | $249 ($226) | 5.3 (11.0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
V>V_NIL_ROYP56_R2_3 | $237 (0) | 0.4 (0) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - ROTS No. 7 or No. 8 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 220 kV, feedback | NIL | Vic
F_I+LREG_0400 | $235 (0) | 4.2 (0) | NEM Lower Regulation Requirement greater than 400 MW | Outage | FCAS
F_MAIN++ML_L5_APD | $231 ($1,128) | 29.4 (72.8) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
VN_0750 | $224 (0) | 1.9 (0) | Discretionary Vic to NSW transfer upper limit of 750 MW | Outage | Vic
F_T++NIL_WF_TG_R60 | $220 ($18) | 25.8 (5.2) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL | FCAS
F_T+FARE_N-2_RREG | $217 (0) | 0.6 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | FCAS
T>T_NIL_BL_IMP_3F | $213 ($131) | 3.3 (5.2) | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Tas
V>V_HWRO12_1AR | $212 (0) | 0.9 (0) | Out = Hazelwood to Rowville No. 1 or No. 2 220 kV line, radial mode, prevent O/L of the Rowville to Yallourn No. 7 or No. 8 220 kV line for trip of the parallel No. 8 or No. 7 220 kV line, Yallourn W1 on 220 kV, feedback | Outage | Vic
V>>N_SMHTX_2 | $207 (0) | 4.3 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V>SMLKGRC1 | $205 (0) | 0.3 (0) | Out = Kerang to Redcliffs 220kV line, avoid overloading Darlington Pt to Balranald (X5/1) 220kV line for trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
V>>S_TB6125+28_KHTB1 | $204 ($411) | 0.7 (1.6) | Out = Tailem Bend CBs 6125 and/or 6128 (both or either CB); Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend 132kV #1 line for loss of Tailem Bend transformer #4. | Outage | SA
F_V+NIL_PTH01_R5 | $201 ($199) | 13.7 (16.3) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
Q:N_30+38+KCTX_AR | $199 (0) | 5.8 (0) | Out= Liverpool-SydneyWest & Regentville-SydneyWest & one KempsCreek Tie Tx (30+38+KCTX), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
N^Q_AR_330_BS1_1 | $193 (0) | 6.3 (0) | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage | NSW
F_T++NIL_BLSPS_L6_2 | $193 ($1,778) | 0.1 (1.0) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
F_I+RREG_0350 | $189 (0) | 2.3 (0) | NEM Raise Regulation Requirement greater than 350 MW | Outage | FCAS
S:V_580 | $181 (0) | 0.9 (0) | Maintain maximum transfer limit of 580 MW on SA-VIC and Murraylink combined to avoid oscillatory instability | NIL | SA
S>>V_NIL_KHTB2_KHTB1 | $181 (0) | 0.1 (0) | Out= Nil, avoid O/L Tailem Bend - Keith #1 132kV on trip of Tailem Bend - Keith #2 132kV line, Feedback | NIL | SA
F_T++CSGO_TG_R6 | $176 ($5,289) | 0.8 (40.3) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage | FCAS
T>T_FASH_2_N-2 | $173 ($236) | 1.0 (1.3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.2 transformer | Outage | Tas
F_I+TG_R5_1000 | $170 (0) | 2.8 (0) | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS
F_MAIN+TL_L60_0500 | $162 (0) | 44.9 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS | Outage | FCAS
F_V+NIL_PTH01_R6 | $160 ($118) | 13.8 (16.4) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
Q:N_AR_2L-G_-100 | $158 (0) | 2.9 (0) | Nominated Offset -100MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | Outage | Qld
F_Q_GSTONE2_RREG | $154 (0) | 2.1 (0) | Out= NIL, Gladstone 2 RREG Requirement <= 0MW | Outage | FCAS
N^Q_AR_330_BS5_1 | $154 (0) | 0.8 (0) | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage | NSW
CA_SPS_42375E8A_01 | $154 (0) | 3.6 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LHPA on trip of LTSS-MSS (66) 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
Q_CS_1100 | $151 ($39,273) | 0.3 (8.8) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer | Outage | Qld
N>>N-NIL_DPTX | $150 (0) | 0.3 (0) | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other | NIL | NSW
F_MAIN++TL_L60_0500 | $149 (0) | 104.3 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage | FCAS
F_V+NIL_PTH01_R60 | $147 ($92) | 13.8 (16.3) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
V>>V_EPTT_2A_R | $145 (0) | 1.5 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode, feedback | Outage | Vic
S>MYTX1_MYTX2 | $141 (0) | 0.3 (0) | Out = Mayura 132/33 kV transformer #1 with the 33kV bus tie isolator 44248 open or closed, avoid O/L Mayura 132/33 kV transformer #2, Feedback | Outage | SA
V>>N-X_MSUT_LTUT_B | $140 (0) | 3.8 (0) | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid O/L DDTS to WOTS 330kV line on trip of Lower Tumut to Murray (66) line, Feedback | Outage | Vic
F_I+ML_L60_0400 | $140 ($1,379) | 68.3 (1,609.5) | NEM lower 60 second requirement for a NEM load event | NIL | FCAS
T>T_X-TUWA_TUTA2_2 | $139 (0) | 0.3 (0) | Out = Multiple 110 kV lines ex Tungatinah - Tungatinah - Tarraleah No. 2, Tungatinah - Lake Echo - Waddamana No. 1 and No. 110 kV lines OOS, avoid O/L Tarraleah to New Norfolk No. 2 110 kV line on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
F_T+FASH1_2C_RREG | $136 (0) | 15.6 (0) | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage | FCAS
F_T++FASH_N-2_TG_R6 | $134 ($3,276) | 5.1 (5.0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
T^T_NIL_LIPM_N-2_DS | $134 (0) | 0.3 (0) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid voltage instability or violations for loss of both Liapootah to Palmerston 220 kV lines, dispatch only | NIL | Tas
F_Q_GSTONE1_RREG | $134 (0) | 1.9 (0) | Out= NIL, Gladstone 1 RREG Requirement <= 0MW | Outage | FCAS
F_T+FASH_N-2_RREG | $130 ($304) | 3.9 (18.5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | FCAS
F_I+ML_L5_APD | $126 ($1,390) | 25.3 (326.2) | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_T++BL_650_R60_3 | $123 (0) | 23.5 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage | FCAS
T>T_NIL_BL_IMP_6E | $123 ($433) | 1.6 (5.8) | Out = Nil, avoid overloading Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) on trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action | NIL | Tas
CA_SPS_43667C70_01 | $111 (0) | 0.8 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
NRM_VIC1_SA1 | $109 ($52,366) | 0.2 (2.1) | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
VT_200 | $104 (0) | 0.3 (0) | Vic to Tas on Basslink upper limit of 200 MW | Outage | Vic
F_MAIN++ML_L5_0400 | $104 ($4,672) | 6.2 (837.0) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
T>T_NIL_BL_IMP_5FF | $104 ($11,406) | 1.7 (107.3) | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
V>>N-JNWG_RADIAL_1 | $103 ($34) | 0.5 (0.6) | Out = Jindera to Wagga(62), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
F_Q_GSTONE3_RREG | $103 (0) | 2.1 (0) | Out= NIL, Gladstone 3 RREG Requirement <= 0MW | Outage | FCAS
F_Q_GSTONE4_RREG | $103 (0) | 2.1 (0) | Out= NIL, Gladstone 4 RREG Requirement <= 0MW | Outage | FCAS
V::N_EPMB_xxx | $102 (0) | 2.3 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V>>V_CBTS_TX_2B_R | $99 (0) | 3.9 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage | Vic
S:V_420 | $99 (0) | 0.5 (0) | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability This constraint equation was added, in January 2011, to a number of outage constraint sets across the NEM (except for Tasmania). The 420 MW value is the previous system normal limit. Throughout 2011 AEMO conducted studies as to whether the 420 MW limit was appropriate for various outages. In some cases the limit was increased. This work will continue in 2012. | Outage | SA
T>T_X-TUWA_TUTA2_1 | $98 (0) | 0.2 (0) | Out = Multiple 110 kV lines ex Tungatinah - Tungatinah - Tarraleah No. 2, Tungatinah - Lake Echo - Waddamana No. 1 and No. 110 kV lines OOS, avoid O/L Tungatinah to Tarraleah No. 1 on trip of New Norfolk to Meadowbank 110 kV line, feedback | Outage | Tas
QNTE_ROC | $96 ($488) | 3.8 (11.6) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
V>V_NIL_ROYP56_R5_1 | $94 ($241) | 0.5 (1.2) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 500 kV, feedback | NIL | Vic
N>>Q-LDTW_2 | $94 (0) | 1.5 (0) | Out= Liddell-Tamworth(84), avoid Liddell->Muswellbrook(83) OL on trip of QLD largest unit; Fb | Outage | NSW
F_Q++LDTW_R60 | $94 ($123) | 5.8 (8.6) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS
Q:N_NIL_OSC | $92 ($981) | 1.1 (2.1) | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
VT_350 | $91 (0) | 0.2 (0) | Vic to Tas on Basslink upper limit of 350 MW | Outage | Vic
F_N_ER02_RREG | $89 (0) | 9.3 (0) | Out= NIL, Eraring 2 RREG Requirement <= 0MW | Outage | FCAS
T_V_FCSPS_RAMP | $88 ($87) | 0.5 (0.3) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
F_T+FASH_N-2_TG_R5 | $87 ($7) | 4.2 (0.3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_I+ML_L6_APD | $86 ($227) | 181.9 (153.3) | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_QNV++MLMO_L5 | $85 (0) | 7.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_T+BL_650_R60_1 | $85 ($1) | 6.3 (0.4) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage | FCAS
T>T_GTSH_IMP_4A | $84 ($1,709) | 1.4 (9.2) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>V_KTSY_2_R | $83 (0) | 2.8 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of Keilor to South Morang 500kV line, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
F_ESTN++MLTR_L5 | $81 ($1) | 14.2 (0.3) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS
F_ESTN++MLSY_L5 | $78 ($31) | 18.7 (9.3) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 5 min Requirement | Outage | FCAS
F_T+BL_650_R5 | $77 ($17) | 3.7 (1.6) | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 650 ms | Outage | FCAS
F_MAIN++ML_L60_APD | $75 ($100) | 27.4 (48.3) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
V>>V_KTS_TX_A2_2B_R | $72 (0) | 3.3 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Vic
F_T++FASH_N-2_TG_R60 | $69 ($25) | 6.3 (5.6) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
F_MAIN+ML_L5_APD | $69 ($31) | 9.6 (1.9) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
Q:N_NIL_BI_POT | $67 (0) | 3.4 (0) | Out = Nil, avoid transient instability for a trip of a Boyne Island potline (400 MW) For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_OSC or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
F_N_ER02_R5 | $65 (0) | 8.3 (0) | Out= NIL, Eraring 2 R5 Requirement <= 0MW | Outage | FCAS
F_V+NIL_PTH01_L5 | $62 ($63) | 13.8 (14.7) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
T>>T_NIL_BL_EXP_3F | $61 ($321) | 0.3 (0.4) | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
F_Q_MEWV_823_R5 | $58 (0) | 2.8 (0) | Out= Mt England to Wivenhoe (823) line, Raise 5 min requirement of zero for Wivenhoe #1 | Outage | FCAS
CA_SPS_43667C70_02 | $57 (0) | 0.1 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
F_Q++MUTW_R6 | $55 ($7) | 0.3 (1.1) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage | FCAS
S>V_NIL_HYTX_HYTX | $55 (0) | 0.7 (0) | Out = Nil, avoid overloading a Heywood 275/500 kV transformer on trip of the other Heywood 275/500 kV transformer | NIL | SA
V>>SML_NIL_5 | $54 (0) | 0.1 (0) | Out = NIL, prevent pre-contingent overload of the Ballarat to Bendigo 220 kV line, feedback | NIL | Vic
F_V+NIL_APD01_R5 | $53 ($178) | 2.8 (12.4) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
F_ESTN++MLSY_L60 | $52 ($45) | 23.0 (12.1) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 60 sec Requirement | Outage | FCAS
T>T_NIL_BL_110_18_1 | $51 ($56,544) | 0.1 (40.5) | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
T>T_FASH_1_2_C2 | $51 (0) | 0.1 (0) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hampshire link closed, Bastyan + Mackintosh supplying txfmrs, other generators supplying 220kV line to Sheffield, limit Bastyan and Mackintosh >= 90% of Rosebery + Queenstown MW | Outage | Tas
F_Q_GSTONE2_R6 | $51 (0) | 2.1 (0) | Out= NIL, Gladstone 2 R6 Requirement <= 0MW | Outage | FCAS
F_T+NIL_ML_L6 | $50 (0) | 2.6 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
F_Q++LDTW_L6 | $50 ($331) | 4.3 (9.7) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
NQTE_ROC | $49 ($57,465) | 4.8 (16.7) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
F_Q_GSTONE1_R6 | $47 (0) | 1.9 (0) | Out= NIL, Gladstone 1 R6 Requirement <= 0MW | Outage | FCAS
F_N_ER02_R6 | $45 (0) | 8.5 (0) | Out= NIL, Eraring 2 R6 Requirement <= 0MW | Outage | FCAS
V>>V_EPTT_2_P | $45 (0) | 1.7 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, parallel mode, feedback | Outage | Vic
F_QNV++MLSY_L60 | $44 ($1) | 4.0 (0.6) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_N_ER02_R60 | $43 (0) | 7.8 (0) | Out= NIL, Eraring 2 R60 Requirement <= 0MW | Outage | FCAS
T>TU_LE_WA1_TUO_1 | $43 (0) | 0.1 (0) | Out = Tungatinah to Lake Echo to Waddamana No. 1 110kV line open at Tungatinah only (i.e. TU CB G152 OPEN), avoid O/L Tungatinah to Waddamana NO.2 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Tas
F_T+FARE_N-2_TG_R5 | $42 (0) | 3.3 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T++FARE_N-2_TG_R60 | $42 ($41) | 2.7 (8.1) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
F_MAIN++NIL_BL_R60 | $41 ($9) | 5.0 (4.0) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL | FCAS
F_N_ER02_LREG | $40 (0) | 8.4 (0) | Out= NIL, Eraring 2 LREG Requirement <= 0MW | Outage | FCAS
V::N_DDWO_xxx | $40 (0) | 0.5 (0) | Out = Dederang to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
F_Q++ARTW_R6 | $38 ($22,570) | 0.2 (26.0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
S:V_SA_PSS | $38 (0) | 0.3 (0) | Out= Nil; SA to Vic Oscillatory stability limit based on PSS availability in South Australia. | NIL | SA
N:Q_AR_BUS5_N-2 | $38 (0) | 3.2 (0) | Out = Nil, loss of Armidale No.5 330kV reclassified as credible, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | NSW
F_Q_MACKAYGT_R5 | $38 (0) | 2.3 (0) | Out= NIL, Mackay GT R5 Requirement <= 0MW | Outage | FCAS
F_Q_STAN2_L6_ZERO | $38 (0) | 0.9 (0) | Out= NIL, Stanwell 2 L6 Requirement <= 0MW | Outage | FCAS
V>>S_NIL_SGBL_SGKH | $36 (0) | 0.8 (0) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on trip of Snuggery - Blanche 132kV line, Feedback. | NIL | SA
F_Q++LDTW_L60 | $36 ($228) | 4.1 (9.0) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_MAIN++RREG_0350 | $36 (0) | 0.8 (0) | Mainland Raise Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage | FCAS
F_ESTN++MLTR_L60 | $35 ($1) | 16.8 (0.6) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_Q_GSTONE2_R60 | $35 (0) | 2.1 (0) | Out= NIL, Gladstone 2 R60 Requirement <= 0MW | Outage | FCAS
F_V+NIL_APD01_R6 | $34 ($103) | 2.8 (12.3) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
N^^V_DDSM1 | $34 (0) | 0.4 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage | NSW
F_T+CSGO_TG_R5 | $34 ($6) | 1.6 (0.8) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
F_Q_GSTONE3_R6 | $34 (0) | 1.3 (0) | Out= NIL, Gladstone 3 R6 Requirement <= 0MW | Outage | FCAS
F_Q_GSTONE4_R6 | $34 (0) | 1.3 (0) | Out= NIL, Gladstone 4 R6 Requirement <= 0MW | Outage | FCAS
F_Q_MEWV_824_R5 | $33 (0) | 2.8 (0) | Out= Mt England to Wivenhoe (824) line, Raise 5 min requirement of zero for Wivenhoe #2 | Outage | FCAS
V>>S_RBTU2_BUPA_BRPA | $33 (0) | 0.3 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines , avoid O/L Brinkworth - Templers West line on trip of Bungama - Blyth West 275kV line, Feedback | Outage | SA
V>>V_CBTS_TX_2A_R | $32 (0) | 1.8 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
V>>V_ROTS_TX_2B_R | $32 (0) | 9.1 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
V>>V_NIL_6_P | $32 (0) | 0.4 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood 3/5 parallel mode, feedback | NIL | Vic
F_Q_GSTONE1_R60 | $32 (0) | 1.9 (0) | Out= NIL, Gladstone 1 R60 Requirement <= 0MW | Outage | FCAS
F_I+TG_R60_1000 | $31 (0) | 2.8 (0) | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS
V>V_NIL_RADIAL_3-4_3 | $31 (0) | 0.1 (0) | Outage = Nil, limit Yallourn unit 1 +HWPS+JLGS+Bairnsdale+Morwell, avoid O/L Hazelwood 500/220kV A1 txfmr for trip of A2 txfmr, Yallourn unit 1 in 500kV mode, HWPS Radial Mode with 3&4 busses tied, 1&2 busses split. Swamped if HWPS-JLTS 2 line open. | NIL | Vic
Q:N_AR_CP2_AR_2L-G | $31 (0) | 1.5 (0) | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
T>T_HAPM_110_IMP_4B | $30 ($183) | 0.9 (4.9) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L a Palmerston to Hadspen No. 1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
F_T+FASH_N-2_TG_R60 | $30 (0) | 3.1 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_V+NIL_APD01_R60 | $29 ($82) | 2.8 (12.1) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
Q_KMBG_7143 | $29 (0) | 0.1 (0) | Out= 7143 Kamerunga Barron Gorge PS 132kV line | Outage | Qld
F_T++FASH1_2C_TG_R6 | $27 ($952) | 0.3 (0.8) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
T>T_PMWA_IMP_4D | $27 ($2,191) | 0.8 (21.7) | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
F_Q_GSTONE3_R60 | $27 (0) | 1.3 (0) | Out= NIL, Gladstone 3 R60 Requirement <= 0MW | Outage | FCAS
F_Q_GSTONE4_R60 | $27 (0) | 1.3 (0) | Out= NIL, Gladstone 4 R60 Requirement <= 0MW | Outage | FCAS
F_I+LREG_0250 | $27 (0) | 1.3 (0) | NEM Lower Regulation Requirement greater than 250 MW | Outage | FCAS
T>T_NIL_BL_220_6B | $26 ($480) | 0.3 (2.9) | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
V>>V_EPTT_2B_R | $25 (0) | 0.8 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage | Vic
F_MAIN+ML_L60_APD | $24 ($5) | 9.6 (2.0) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_MAIN++TG_R5_1000 | $24 (0) | 0.7 (0) | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage | FCAS
T>T_NIL_TOV_5FF | $23 (0) | 0.4 (0) | Out = Nil, avoid TOV following NCSPS slow action for O/L of Hadspen to Georgetown No. 2 220 kV lines (flow to North) for trip of the Hadspen to Georgetown No. 1 220 kV line, considering status of Tamar CCGT, feedback equation | NIL | Tas
F_N_ER02_L5 | $23 (0) | 7.0 (0) | Out= NIL, Eraring 2 L5 Requirement <= 0MW | Outage | FCAS
F_I+ML_L60_APD | $23 ($55) | 18.2 (82.9) | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_V+NIL_PTH01_L60 | $22 ($4) | 12.8 (3.7) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
T>T_SHGT_HAGT_N-2 | $22 (0) | 0.8 (0) | Out= NIL, Loss of both Hadspen to Georgetown 220kV lines declared credible, avoid O/L the Sheffield to Georgetown 220kV line for loss of both Hadspen to Georgetown 220kV lines , Feedback | Outage | Tas
F_QNV++MLSY_L5 | $20 ($0) | 2.9 (0.1) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
N>N_LSDU_9U6_1 | $19 (0) | 0.2 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | NSW
F_I+TG_R6_1000 | $19 (0) | 1.6 (0) | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1000 | Outage | FCAS
N^Q_ARTW_1 | $19 ($2,589) | 0.2 (12.8) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage | NSW
F_T++BL_650_R60_2 | $19 (0) | 3.7 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage | FCAS
N>N_LSDU_9U6_2 | $18 (0) | 0.1 (0) | Out = one of Lismore to Dunoon (9U6 or 9U7) 132 kV line, avoid overloading on the Mullumbimby 132/66 kV transformer on trip of the remaining Lismore to Dunoon (9U6 or 9U7) 132 kV line | Outage | NSW
Q:N_DM_CB_AR_2L-G | $17 (0) | 0.3 (0) | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
F_MAIN++NIL_BL_L60 | $16 ($259) | 7.7 (53.9) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL | FCAS
V::N_BYPASS_HW_SY_xxx | $16 (0) | 0.3 (0) | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
V>>N-MSUT_4 | $16 (0) | 0.1 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
T>T_GTSH_IMP_4E | $15 ($1,961) | 0.2 (13.2) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_110_IMP_4P | $15 ($0) | 0.6 (0.1) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L of Palmerston to Hadspen No. 3 110 kV line (flow to North) for trip of the Palmerston 220/110 kV transformer with no NCSPS action, feedback | Outage | Tas
F_MAIN++TG_R60_1000 | $15 (0) | 0.8 (0) | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage | FCAS
F_T++FASH_N-2_TG_R5 | $14 ($222) | 3.5 (10.5) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
V>>V_KTS_TX_A3_2A_R | $14 (0) | 0.6 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
F_T+CSGO_TG_R60 | $12 ($1,220) | 0.9 (0.6) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
F_ESTN++HYTR_L60 | $11 ($57) | 5.3 (23.8) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_Q_STAN2_L60_ZERO | $10 (0) | 0.8 (0) | Out= NIL, Stanwell 2 L60 Requirement <= 0MW | Outage | FCAS
F_MAIN+ML_L5_0400 | $10 ($2,731) | 1.9 (289.3) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_N_ER02_L6 | $10 (0) | 8.8 (0) | Out= NIL, Eraring 2 L6 Requirement <= 0MW | Outage | FCAS
V>>V_ROTT_R_2A | $10 (0) | 0.4 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV side, feedback | Outage | Vic
F_Q_GSTONE1_LREG | $10 (0) | 1.8 (0) | Out= NIL, Gladstone 1 LREG Requirement <= 0MW | Outage | FCAS
V>>V_CBTS_TX_3A_R | $9 (0) | 0.3 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
F_Q_GSTONE2_LREG | $9 (0) | 1.7 (0) | Out= NIL, Gladstone 2 LREG Requirement <= 0MW | Outage | FCAS
F_V+NIL_APD01_L5 | $9 ($32) | 2.6 (10.8) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
F_QNV++MLMO_L6 | $9 (0) | 4.2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_ESTN++HYMO_L60 | $9 ($1) | 5.1 (3.0) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage | FCAS
F_Q++LDTW_L5 | $9 ($5,472) | 1.2 (5.7) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
T_T_TU_105 | $9 (0) | 0.1 (0) | Discretionary 105 MW upper limit on Tungatinah | Outage | Tas
N^N-89_LSTX_SVC | $8 ($386) | 0.1 (2.8) | Out = Coffs Harbour to Lismore (89) 330 kV line and Lismore 330/132 kV transformer with Lismore SVC in reactive power control mode, avoid voltage collapse on trip of Koolkhan to Lismore (967) 132 kV line | Outage | NSW
V>>V_CBTS_TX_3B_R | $8 (0) | 0.3 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage | Vic
F_QNV+MLMO_L60 | $8 (0) | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_Q++ARTW_R60 | $8 ($17,593) | 0.3 (19.3) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS
F_Q++MUTW_R60 | $8 ($3) | 0.3 (0.5) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage | FCAS
F_QNV++HYMO_L60 | $7 ($9) | 4.5 (2.8) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_T+NIL_ML_L5 | $7 (0) | 1.7 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
F_ESTN++HYTR_L5 | $7 ($37) | 1.3 (15.3) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage | FCAS
F_Q_GSTONE3_LREG | $7 (0) | 1.3 (0) | Out= NIL, Gladstone 3 LREG Requirement <= 0MW | Outage | FCAS
F_Q_GSTONE4_LREG | $7 (0) | 1.3 (0) | Out= NIL, Gladstone 4 LREG Requirement <= 0MW | Outage | FCAS
F_QNV++MLSY_L6 | $7 (0) | 2.3 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
V>V_HWJL2_RADIAL_7 | $6 (0) | 0.1 (0) | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split | Outage | Vic
F_S++HYML_L5 | $6 ($18,667) | 0.2 (2.3) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 5 minute requirement | Outage | FCAS
F_T+FARE_N-2_TG_R60 | $6 (0) | 0.6 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
N>>V-LTMS_5 | $5 (0) | 0.2 (0) | Out = Lower Tumut to Murray (66) 330 kV line, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | Outage | NSW
V>>V_ROTT_R_2B | $5 (0) | 0.3 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV side, feedback | Outage | Vic
F_Q_TARONG#4_RREG | $5 (0) | 0.9 (0) | Out= NIL, Tarong 4 RREG Requirement <= 0MW | Outage | FCAS
N^^V_SMTXH2_2 | $4 (0) | 0.2 (0) | Out = South Morang H1 330/220 kV transformer, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage | NSW
F_Q_STAN2_RREG_ZERO | $4 (0) | 0.9 (0) | Out= NIL, Stanwell 2 RREG Requirement <= 0MW | Outage | FCAS
F_T+NIL_ML_L60 | $4 (0) | 2.6 (0) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
V>>V_SMTT2_2 | $4 (0) | 0.1 (0) | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the South Morang to Thomastown No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
F_Q_STAN2_LREG_ZERO | $4 (0) | 0.1 (0) | Out= NIL, Stanwell 2 LREG Requirement <= 0MW | Outage | FCAS
T>T_HAPM_110_IMP_4A | $4 ($44) | 0.3 (0.8) | Out = Hadspen to Palmerston No. 3 110 kV line, avoid O/L the Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_110_IMP_4Q | $4 (0) | 1.0 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L of Palmerston to Hadspen No. 4 110 kV line (flow to North) for trip of the Palmerston 220/110 kV transformer with no NCSPS action, feedback | Outage | Tas
V>>N-JNWO_RADIAL_2 | $4 (0) | 0.2 (0) | Out = Jindera to Wodonga(060), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
F_N_ER02_L60 | $4 (0) | 2.3 (0) | Out= NIL, Eraring 2 L60 Requirement <= 0MW | Outage | FCAS
F_Q_CALL_B_2_LREG | $4 (0) | 1.1 (0) | Out= NIL, Callide B2 LREG Requirement <= 0MW | Outage | FCAS
F_Q+MG_R6 | $3 (0) | 0.1 (0) | Raise 6 sec Service Requirement for Qld Generation Event | Outage | FCAS
V>>S_MSTU_TBTU_TBMO | $3 (0) | 0.8 (0) | Out= Mt Barker South - Tungkillo 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
V>>N_SMHTX_1 | $3 (0) | 0.2 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
F_V+NIL_PTH01_L6 | $3 ($3) | 7.8 (3.8) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_MAIN++LREG_0400 | $3 (0) | 0.2 (0) | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage | FCAS
F_ESTN++MLMO_L60 | $3 (0) | 1.7 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
S>>V_NIL_NIL_HUWT | $2 ($1,390) | 0.1 (1.8) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL | SA
F_T+NIL_BB_TG_R6 | $2 (0) | 0.3 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
F_QNV++HYMO_L5 | $2 ($0) | 0.4 (0.1) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
V>>N-DDWO_RADIAL_1 | $2 (0) | 0.2 (0) | Out = Dederang to Wodonga, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
F_MAIN+ML_L60_0400 | $2 ($482) | 1.8 (271.1) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_STHN+MG_R5 | $2 (0) | 0.1 (0) | Raise 5 min Service Requirement for a Southern Generation Event | Outage | FCAS
F_NVS++MG_R6 | $2 (0) | 0.1 (0) | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS
V>>N-X_MSUT_LTUT | $2 (0) | 0.2 (0) | Out= Murray-UpperTumut(65) and Lower Tumut-Upper Tumut (64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Vic
F_ESTN++HYMO_L5 | $2 ($0) | 0.3 (0.1) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage | FCAS
F_V+NIL_APD01_L60 | $2 ($6) | 1.5 (2.8) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_T++NIL_ML_L6 | $2 (0) | 1.0 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS
F_T+NIL_BB_TG_R60 | $2 (0) | 0.2 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
F_NVS++MG_R60 | $2 (0) | 0.1 (0) | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS
F_Q++NIL_R5 | $1 (0) | 0.2 (0) | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS
QNI_ISLE_B | $1 (0) | 0.1 (0) | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage | Qld
F_QNV+MLMO_L5 | $1 (0) | 0.2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
N>N-NIL_8C_8E | $1 (0) | 0.1 (0) | Out = Nil, avoid O/L Dumaresq to Armidale (8C) on trip of Dumaresq to Armidale (8E) line, Feedback | NIL | NSW
N>N-CHKK_TE_1 | $1 ($486) | 0.2 (0.2) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
S:V_430 | $1 (0) | 0.3 (0) | Maintain maximum transfer limit of 430 MW on SA-VIC and Murraylink combined to avoid oscillatory instability during the outage of one or more of the major transmission lines connecting NEM regions. | Outage | SA
F_T++NIL_ML_L60 | $1 ($0) | 1.0 (0.1) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS
F_ESTN++MLMO_L5 | $1 (0) | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage | FCAS
F_ESTN++MLSY_L6 | $1 ($2) | 0.8 (3.4) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 6 sec Requirement | Outage | FCAS
F_T++NIL_ML_L5 | $1 (0) | 0.4 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS
V::N_HYSE_xxx | $1 ($884) | 0.1 (21.8) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
F_V+NIL_APD01_L6 | $1 ($7) | 1.3 (3.6) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
V>>S_NIL_KHTB1_KHTB2 | $1 (0) | 0.1 (0) | Out = Nil, avoid O/L Keith - Tailem Bend #2 132kV on trip of Keith - Tailem Bend #1 132kV line, Feedback | NIL | SA
F_T++BLSPS_EXP_L60_1 | $1 ($19) | 0.7 (0.7) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
F_T++BLSPS_EXP_L6_1 | $1 ($20) | 0.7 (0.7) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
F_T++NIL_BLSPS_L60_2 | $1 ($2) | 0.1 (0.7) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
F_T++NIL_BLSPS_L5 | $0 ($3) | 0.2 (0.9) | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL | FCAS
F_STHN+APD_TL_L5 | $0 (0) | 0.1 (0) | Lower 5 min requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
F_S++HYML_L6 | $0 ($39,302) | 1.3 (4.1) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 6 second requirement | Outage | FCAS
F_T++NIL_BLSPS_L60_1 | $0 ($0) | 0.3 (0.4) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
F_T++NIL_BLSPS_L6_1 | $0 ($12,900) | 0.3 (0.1) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
F_STHN+LREG_0120 | $0 (0) | 0.1 (0) | Southern Lower Regulation Requirement greater than 120 MW | Outage | FCAS
F_MAIN++ML_L60_0400 | $0 ($831) | 0.6 (590.5) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
F_T++FARE_N-2_TG_R5 | $0 ($16) | 0.1 (3.8) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS | Outage | FCAS
V>SML_BUDP_3 | $0 (0) | 0.1 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Kerang to Wemen 220 kV line section on trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
T>T_X-HAPM_2_1N | $0 (0) | 0.1 (0) | Out= Hadspen to Palmerston No. 1 and No. 2 220 kV lines, avoid O/L either of the Hadspen to Palmerston No. 3 or No 4 110 kV lines (flow to North) on trip of Sheffield to Palmerston 220 kV line, Feedback | Outage | Tas
T>T_NIL_NCSPS5_1B | $0 ($56,422) | 0.1 (26.7) | Out = Nil, avoid overloading the line terminal equipment of either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line | NIL | Tas
N_MBTE1_A | $0 ($121) | 0.1 (0.3) | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
F_T++BLSPS_EXP_L5 | $0 ($1) | 0.4 (0.7) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage | FCAS
F_STHN+APD_TL_L60 | $0 (0) | 0.1 (0) | Lower 60 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
F_QNV++HYMO_L6 | $0 (0) | 0.1 (0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS

## Interconnector Binding 2014
Interconnector Direction | Constraint Equation ID | 2014 Hours (2013 Hours) | Description | Type
N-Q-MNSP1 Export | N_X_MBTE_3A | 342.5 (1429.3) | Out = all three Directlink cables, NSW to Queensland limit All three Directlink cables was out for 70.3 days in 2014 compared to 158.1 days in 2013 | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 107.1 (74.3) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. The Koolkhan to Lismore (967) 132 kV line was out for 9.3 days in 2014 compared to 3.8 days in 2013 | Outage
N-Q-MNSP1 Export | N_X_MBTE2_A | 51.4 (121.5) | Out = two Directlink cables, NSW to Queensland limit Two Directlink cables was out for 169.8 days in 2014 compared to 214.9 days in 2013 | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 23.0 (3.8) | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 14.6 (194.4) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
N-Q-MNSP1 Export | N>N-LSTN_TE_C1 | 11.2 (0.8) | Out = Lismore to Tenterfield (96L) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line The Lismore to Tenterfield (96L) 132 kV line was out for 2.8 days in 2014 compared to 0 days in 2013 | Outage
N-Q-MNSP1 Export | N^Q_TW_330_BUS3_1 | 6.8 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage
N-Q-MNSP1 Export | N>Q_LSLS_9U8 | 6.2 (2.7) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line One Lismore 330 to Lismore 132 (9U8 or 9U9 or 9W1) 132 kV line was out for 109.4 days in 2014 compared to 0 days in 2013 | Outage
N-Q-MNSP1 Export | N^Q_AR_330_BS1_1 | 5.2 (0) | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage
N-Q-MNSP1 Export | NQTE_ROC | 4.8 (16.4) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL
N-Q-MNSP1 Export | N>LSDU9U6_LSDU9U7 | 4.0 (0.6) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R6 | 3.8 (10.8) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
N-Q-MNSP1 Export | N^Q_NIL_A | 3.6 (21.5) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
N-Q-MNSP1 Export | N:Q_AR_BUS5_N-2 | 3.2 (0) | Out = Nil, loss of Armidale No.5 330kV reclassified as credible, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | N^^Q_AR_VC_B1 | 2.3 (0) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N>>Q-LDTW_2 | 1.4 (0) | Out= Liddell-Tamworth(84), avoid Liddell->Muswellbrook(83) OL on trip of QLD largest unit; Fb | Outage
N-Q-MNSP1 Export | N>>N-NIL__3_OPENED | 1.3 (0) | Out = Nil, avoid overloading Liddell to Muswellbrook 330kV line (83) on trip of Liddell to Tamworth 330kV line (84) | NIL
N-Q-MNSP1 Export | N>Q-MUTW_2 | 1.1 (2.2) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage
N-Q-MNSP1 Export | N^Q_AR_330_BS5_1 | 0.8 (0) | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage
N-Q-MNSP1 Export | #R010344_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010358_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010402_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010509_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010521_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010022_003_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N^Q_AR_330_BS5_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010531_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010344_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010358_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010392_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010402_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010509_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010521_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010531_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010559_002_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010559_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010566_002_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010566_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010857_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint N^N-89_LSTX_SVC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010857_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N-89_LSTX_SVC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R009878_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010245_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010462_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010476_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010552_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N-967_LS_SVC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010557_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N-967_LS_SVC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010607_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | N>N-NIL_LSDU | 0.3 (122.7) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line | NIL
N-Q-MNSP1 Export | #R009878_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010005_003_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_AR_330_BS5_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010245_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010288_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010326_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_TW_330_BUS3_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010326_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^Q_TW_330_BUS3_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010500_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_AR_330_BS1_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010711_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N>>N-ERNC90_B, Effective Date: 25/06/2014, Version: 1 | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R60 | 0.3 (0) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | #R010392_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010500_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^Q_AR_330_BS1_1, Effective Date: 10/03/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010942_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | N>N-CHKK_TE_1 | 0.2 (0.3) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | #R009902_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010359_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010462_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010476_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010552_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^N-967_LS_SVC, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R010757_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>>N-ERVP_A, Effective Date: 25/06/2014, Version: 1 | Outage
N-Q-MNSP1 Export | #R010876_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R011143_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R011210_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R011441_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R011476_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R011479_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Export | N>N-LS_TX_TE_B | 0.1 (0.2) | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. DS only | Outage
N-Q-MNSP1 Export | N>N_LSDU_9U6_1 | 0.1 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N^Q_ARTW_1 | 0.1 (3.2) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 0.1 (0) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 0.1 (0.3) | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 1318.9 (2343.7) | Out = all three Directlink cables, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 833.8 (0.6) | Out = one Directlink cable, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 528.7 (74.7) | Out = two Directlink cables, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 24.3 (0) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies | NIL
N-Q-MNSP1 Import | Q>N-MUTE_758 | 20.8 (0) | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 17.8 (6.4) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_757 | 16.2 (0) | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 14.6 (3.0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 13.3 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 9.6 (28.4) | Negative Residue Management constraint equation for QLD to NSW flow | NIL
N-Q-MNSP1 Import | N>N-X_9U6_9G2_2 | 7.9 (0) | Out = one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 132kV line between Mullumbimby and Ballina (9G2, 9G3, 9G4 or 9G5), avoid O/L remaining 132kV line, Qld to NSW limit | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 6.6 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | F_Q++LDMU_L5 | 4.0 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | F_Q++LDMU_L6 | 3.8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | QNTE_ROC | 3.8 (11.9) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_I_F | 1.9 (0.8) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 1.8 (7.2) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | #R010522_010_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N>>N-MPWW_ONE_9, Effective Date: 04/10/2013, Version: 1 | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 0.6 (2.5) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | #R009907_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R009902_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R009907_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R009952_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010288_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010522_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N>>N-MPWW_ONE_9, Effective Date: 04/10/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010876_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010888_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint Q>N-MUTE_758, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011102_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011143_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011210_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010607_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010799_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010799_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010811_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010942_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011476_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011702_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011102_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011425_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011479_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R009952_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010876_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010892_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010892_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010894_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010894_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint Q>N-MUTE_757, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011210_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011316_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N>N-X_9U6_9G2_2, Effective Date: 04/03/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011425_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011441_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010607_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010811_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010889_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint Q>N-MUTE_758, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010889_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint Q>N-MUTE_758, Effective Date: 21/08/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R010942_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011143_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R011476_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Outage
N-Q-MNSP1 Import | CA_SPS_428FB629_01 | 0.1 (0) | Constraint Automation, O/L 94E @MT_PIPER for CTG LNWT on trip of MT_PIPER-WWANG 70 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
N-Q-MNSP1 Import | N>N_LSDU_9U6_2 | 0.1 (0) | Out = one of Lismore to Dunoon (9U6 or 9U7) 132 kV line, avoid overloading on the Mullumbimby 132/66 kV transformer on trip of the remaining Lismore to Dunoon (9U6 or 9U7) 132 kV line | Outage
N-Q-MNSP1 Import | Q_CS_1100 | 0.1 (8.8) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 72.1 (516.8) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
NSW1-QLD1 Export | N^^Q_AR_VC_B1 | 8.7 (0.6) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^Q_TW_330_BUS3_1 | 6.8 (0) | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage
NSW1-QLD1 Export | N^Q_AR_330_BS1_1 | 6.3 (0) | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage
NSW1-QLD1 Export | F_Q++LDTW_R6 | 5.2 (10.8) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 4.6 (0) | Out = Nil, avoid overloading Liddell to Muswellbrook 330kV line (83) on trip of Liddell to Tamworth 330kV line (84) | NIL
NSW1-QLD1 Export | N>Q-MUTW_2 | 4.6 (2.1) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage
NSW1-QLD1 Export | N^Q_NIL_A | 4.6 (32.7) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
NSW1-QLD1 Export | N:Q_AR_BUS5_N-2 | 3.2 (0) | Out = Nil, loss of Armidale No.5 330kV reclassified as credible, NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | N>>Q-LDTW_2 | 1.5 (0) | Out= Liddell-Tamworth(84), avoid Liddell->Muswellbrook(83) OL on trip of QLD largest unit; Fb | Outage
NSW1-QLD1 Export | N^Q_AR_330_BS5_1 | 0.8 (0) | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of the largest of Tarong, Stanwell, Callide B or Swanbank E generators | Outage
NSW1-QLD1 Export | #R010022_003_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N^Q_AR_330_BS5_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | N>>N-NIL__2_OPENED | 0.5 (0) | Out= NIL, avoid O/L Liddell to Tamworth (84) on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | F_Q++LDTW_R60 | 0.4 (0) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | #R010711_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N>>N-ERNC90_B, Effective Date: 25/06/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R010005_003_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_AR_330_BS5_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R010326_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_TW_330_BUS3_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R010326_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^Q_TW_330_BUS3_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R010500_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_AR_330_BS1_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R010500_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^Q_AR_330_BS1_1, Effective Date: 10/03/2014, Version: 1 | Outage
NSW1-QLD1 Export | #R010722_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N>>N-ERNC90_B, Effective Date: 25/06/2014, Version: 1 | Outage
NSW1-QLD1 Export | F_Q++ARTW_R6 | 0.2 (22.5) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage
NSW1-QLD1 Export | F_Q++MUTW_R6 | 0.2 (0.6) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^Q_ARTW_1 | 0.2 (12.8) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage
NSW1-QLD1 Export | N^^Q_ARDM_B1 | 0.2 (3.3) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | #R009874_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R010757_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>>N-ERVP_A, Effective Date: 25/06/2014, Version: 1 | Outage
NSW1-QLD1 Export | N>>N-NIL__3_15M | 0.1 (0.3) | Out= NIL, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 0.1 (0) | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Export | QNI_ISLE_B | 0.1 (0) | Qld / Southern separation, allow QNI to supply Northern NSW Load | Outage
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G | 784.4 (0) | Out = Nil, avoid transient instability for a 2 line to Ground fault at Armidale | NIL
NSW1-QLD1 Import | Q:N_AR_2L-G_-200 | 427.3 (0) | Out = Bulli Creek CBs (8L2 and 99012) or (8M2 and 99022) | Outage
NSW1-QLD1 Import | F_Q++ARDM_L6 | 156.7 (10.7) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | F_Q++ARDM_L5 | 114.3 (2.5) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | Q:N_ARSVC_AR_2L-G | 52.3 (0) | Outage= Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++ARTW_L6 | 33.3 (6.9) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L5 | 26.1 (3.0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | V::N_NILxxx | 23.0 (0) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
NSW1-QLD1 Import | Q:N_AR_2L-G_-150 | 21.3 (0) | Nominated Offset -150MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++MUTW_L6 | 13.3 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 10.3 (30.3) | Negative Residue Management constraint equation for QLD to NSW flow | NIL
NSW1-QLD1 Import | V::N_MLTX_xxx | 8.4 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
NSW1-QLD1 Import | V::N_JNWO_xxx | 7.1 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 6.8 (0.8) | NSW1-QLD1 >= MIN(-424, InitialFlow + 200) (Wt=35) | Outage
NSW1-QLD1 Import | F_Q++MUTW_L5 | 6.6 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | V::N_SMCS_xxx | 5.0 (0) | Out = South Morang 330 kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. One or both South Morang 330 kV series capacitors was out for 1.7 days in 2014 compared to 0 days in 2013 | Outage
NSW1-QLD1 Import | V::N_HWSM_Q4 | 4.9 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
NSW1-QLD1 Import | Q:N_30+38+KCTX_AR | 3.7 (0) | Out= Liverpool-SydneyWest & Regentville-SydneyWest & one KempsCreek Tie Tx (30+38+KCTX), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++LDTW_L6 | 3.5 (7.1) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement The Liddell to Tamworth (84) 330 kV line was out for 5.0 days in 2014 compared to 0 days in 2013 | Outage
NSW1-QLD1 Import | Q:N_NIL_BI_POT | 3.4 (0) | Out = Nil, avoid transient instability for a trip of a Boyne Island potline (400 MW) For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_OSC or Q:N_NIL_BCK2L-G will bind. | NIL
NSW1-QLD1 Import | F_Q++LDMU_L5 | 3.3 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q:N_BI_POT_-050 | 3.3 (0) | Nominated Offset -50MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline | Outage
NSW1-QLD1 Import | V::N_BUDP_xxx | 3.2 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
NSW1-QLD1 Import | V::N_LTWG_xxx | 3.2 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
NSW1-QLD1 Import | Q:N_AR_2L-G_-100 | 2.9 (0) | Nominated Offset -100MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++LDMU_L6 | 2.8 (0) | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | V::N_ROSM_xxx | 2.5 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
NSW1-QLD1 Import | Q:N_AR_CP2_AR_2L-G | 1.5 (0) | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | Q:N_NIL_OSC | 1.1 (2.1) | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL
NSW1-QLD1 Import | V::N_JNWG_xxx | 1.1 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 0.8 (2.5) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement The Liddell to Tamworth (84) 330 kV line was out for 5.0 days in 2014 compared to 0 days in 2013 | Outage
NSW1-QLD1 Import | #R010522_010_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N>>N-MPWW_ONE_9, Effective Date: 04/10/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R010522_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N>>N-MPWW_ONE_9, Effective Date: 04/10/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R010694_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint Q:N_DM_CB_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011347_019_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011347_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011379_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R010755_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R010761_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R010814_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R010970_018_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011431_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q3, Effective Date: 21/02/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011480_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint Q:N_AR_CP2_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | Q:N_DM_CB_AR_2L-G | 0.3 (0) | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | Q_CS_1100 | 0.3 (8.7) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer | Outage
NSW1-QLD1 Import | #R010761_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint Q:N_ARSVC_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R010896_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORCQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011213_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLTXQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011328_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BUDPQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011328_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011375_021_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q:N_30+38+KCTX_AR, Effective Date: 10/10/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011480_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint Q:N_AR_CP2_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R010694_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint Q:N_DM_CB_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011027_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011034_004_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q4, Effective Date: 21/02/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011056_006_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011065_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011117_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTXQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | V::N_MSUT_xxx | 0.2 (0) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
NSW1-QLD1 Import | #R010752_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011056_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011065_005_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011190_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011196_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011267_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011328_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Import | #R011378_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q4, Effective Date: 21/02/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011440_013_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint Q:N_ARTW_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | #R011443_011_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint Q:N_MUTW_AR_2L-G, Effective Date: 08/01/2014, Version: 1 | Outage
NSW1-QLD1 Import | CA_SPS_428FB629_01 | 0.1 (0) | Constraint Automation, O/L 94E @MT_PIPER for CTG LNWT on trip of MT_PIPER-WWANG 70 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
NSW1-QLD1 Import | N>N-NIL_8C_8E | 0.1 (0) | Out = Nil, avoid O/L Dumaresq to Armidale (8C) on trip of Dumaresq to Armidale (8E) line, Feedback | NIL
NSW1-QLD1 Import | V::N_BYPASS_HW_SY_QB | 0.1 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 2 | Outage
NSW1-QLD1 Import | V::N_EPMB_xxx | 0.1 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Export | F_T++NIL_TL_L60 | 664.8 (1927.7) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 644.8 (171.5) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
T-V-MNSP1 Export | F_T++NIL_TL_L6 | 629.9 (1441.2) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 385.5 (342.5) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 269.8 (454.8) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 269.0 (368.1) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_TL_L5 | 133.9 (260.8) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 67.5 (57.0) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T^V_NIL_BL_6 | 50.8 (86.8) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL
T-V-MNSP1 Export | T^V_NIL_8 | 35.8 (13.9) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 31.6 (4.3) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL
T-V-MNSP1 Export | V>>V_MLTS_TX_2A_R | 22.7 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 12.2 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | TVBL_ROC | 10.9 (12.8) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Export | V>>V_ROTS_TX_2B_R | 9.1 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2B_R | 8.9 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
T-V-MNSP1 Export | V>>V_MLTS_TX_2B_R | 8.7 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2_P | 4.5 (0.5) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2B_R | 3.1 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
T-V-MNSP1 Export | V>>V_KTSY_2_R | 2.8 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of Keilor to South Morang 500kV line, radial mode, YWG1 on 220 kV, feedback | Outage
T-V-MNSP1 Export | NC_T_BLNKTAS | 2.3 (2.0) | Non Conformance Constraint for Basslink from Tas to Vic | Outage
T-V-MNSP1 Export | F_MAIN++NIL_BL_R60 | 1.7 (1.3) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
T-V-MNSP1 Export | V>>V_EPTT_2_P | 1.7 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, parallel mode, feedback | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 1.6 (3.1) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | V>>V_EPTT_2A_R | 1.3 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode, feedback | Outage
T-V-MNSP1 Export | T^V_NIL_9 | 1.1 (0) | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | F_MAIN++NIL_DYN_RREG | 0.9 (2.1) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_CBTS_TX_2A_R | 0.9 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | CA_SPS_43667C70_01 | 0.8 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
T-V-MNSP1 Export | V>>V_EPTT_2B_R | 0.8 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2A_R | 0.6 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | T_V_FCSPS_RAMP | 0.5 (0.3) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage
T-V-MNSP1 Export | #R011741_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Export | F_MAIN++TG_R60_1000 | 0.4 (0) | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_NIL_6_P | 0.4 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood 3/5 parallel mode, feedback | NIL
T-V-MNSP1 Export | F_MAIN++TG_R5_1000 | 0.3 (0) | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L60_1 | 0.3 (0.1) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | T::T_HA_GT_PM_5 | 0.3 (0) | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT in service. | Outage
T-V-MNSP1 Export | V>>V_ROTT_R_2A | 0.3 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV side, feedback | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_1 | 0.3 (0.3) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | #R010069_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Export | #R010069_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L60_1 | 0.2 (0.2) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 0.2 (0) | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | #R010162_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Export | #R011741_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Export | CA_SPS_43667C70_02 | 0.1 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
T-V-MNSP1 Export | F_MAIN++RREG_0350 | 0.1 (0) | Mainland Raise Regulation Requirement greater than 350 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Export | F_NVS++MG_R6 | 0.1 (0) | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L5 | 0.1 (0.3) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L5 | 0.1 (0.1) | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_T++NIL_BLSPS_L6_2 | 0.1 (0.5) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 0.1 (0) | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 0.1 (0) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_CBTS_TX_3A_R | 0.1 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 546.9 (0) | Mainland lower 5 min Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 311.8 (0) | Mainland lower 60 sec Service Requirement for the loss of APD potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++TL_L5_0500 | 270.2 (1.3) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V_T_NIL_FCSPS | 267.0 (0.8) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) | NIL
T-V-MNSP1 Import | F_T+NIL_BL_R60_1 & F_T++NIL_BL_R60_x | 118.2 (0) | Tasmania raise 60 second requirement for loss of Basslink, FCSPS available | NIL
T-V-MNSP1 Import | V::N_NILxxx | 112.0 (8.9) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 107.0 (58.9) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_BL1 | 100.8 (6.8) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 97.9 (46.8) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 87.8 (101.2) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 79.9 (67.9) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 79.6 (154.8) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | 40.3 (0) | Tasmania raise 6 second requirement for loss of Basslink, FCSPS available | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 32.0 (0.8) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++TL_L60_0500 | 27.8 (0) | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_MSUT_xxx | 16.5 (17.3) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
T-V-MNSP1 Import | T::T_NIL_4 | 15.0 (0) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 13.7 (2.3) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_6E | 12.8 (73.0) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL
T-V-MNSP1 Import | V::N_MLTX_xxx | 10.4 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 9.8 (0.5) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | VTBL_ROC | 9.8 (14.8) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Import | V:T_SHGT_BL_1 | 8.3 (0) | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_5F | 7.0 (42.4) | Out = Nil, avoid overloading a Hadspen to George Town 220 kV line for trip of the other Hadspen to George Town 220 kV line considering NCSPS action | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 5.6 (1.6) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_SMCS_xxx | 5.4 (0) | Out = South Morang 330 kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
T-V-MNSP1 Import | F_T++BL_650_R60_3 | 5.0 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | V::N_LTWG_xxx | 5.0 (2.0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_T++BL_650_R6_2 | 4.9 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | VT_ZERO | 4.5 (7.8) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 4.4 (372.1) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_HWSM_S4 | 4.2 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
T-V-MNSP1 Import | V::N_DDSM_V4 | 4.1 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++BL_650_R6_3 | 3.2 (0) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 3, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | V::N_HWSM_S3 | 3.1 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
T-V-MNSP1 Import | V::N_JNWG_xxx | 2.9 (0.6) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | V::N_ROSM_xxx | 2.9 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_APD | 2.8 (39.6) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_JNWO_xxx | 2.8 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_QNV++HYMO_L60 | 2.2 (0.6) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_EPMB_xxx | 2.2 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 2.1 (2.3) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | VT_300 | 1.9 (0) | Vic to Tas on Basslink upper limit of 300 MW | Outage
T-V-MNSP1 Import | F_T++BL_650_R60_2 | 1.8 (0) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 2, FCSPS available, LoL = 650 ms | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 1.8 (1.6) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 1.7 (0.5) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_HWSM_V3 | 1.7 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_V4 | 1.5 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L60_APD | 1.3 (23.0) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_V3 | 1.3 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLSY_L60 | 1.3 (0.1) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | NC_T_BLNKTAS | 1.1 (0) | Non Conformance Constraint for Basslink from Tas to Vic | Outage
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 1.0 (4.3) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 1.0 (5.0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T_ROCOF_3 | 1.0 (0) | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL
T-V-MNSP1 Import | V::N_BUDP_xxx | 1.0 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
T-V-MNSP1 Import | V::N_HWSM_Q4 | 1.0 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | V:T_NIL_BL_1 | 1.0 (0) | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL
T-V-MNSP1 Import | F_QNV++MLSY_L5 | 0.9 (0.1) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | VT_000 | 0.9 (0) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage
T-V-MNSP1 Import | F_MAIN++NIL_DYN_LREG | 0.8 (0.2) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 0.8 (4.6) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | CA_SPS_4317B056_01 | 0.8 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.8 (0.8) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | #R011063_012_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | V::N_DDWO_xxx | 0.5 (0) | Out = Dederang to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | #R010395_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011047_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011057_011_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011065_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011183_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011379_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011431_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011718_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint VT_000, Effective Date: 05/08/2008, Version: 1 | Outage
T-V-MNSP1 Import | F_QNV++MLSY_L6 | 0.4 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_V2 | 0.4 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | #R009844_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010384_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010528_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010528_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010814_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010970_018_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011047_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011347_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011378_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011417_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011651_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | VT_200 | 0.3 (0) | Vic to Tas on Basslink upper limit of 200 MW | Outage
T-V-MNSP1 Import | #R010189_026_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010236_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_SMDDMS_V21_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010242_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010896_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORCQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011034_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011213_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLTXQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011328_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011336_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011437_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011474_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L5 | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L60 | 0.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_3F | 0.3 (0.2) | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_QB | 0.3 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 2 | Outage
T-V-MNSP1 Import | #R010189_026_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010236_013_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_X_SMDDMS_V21_R, Effective Date: 04/03/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010242_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010628_007_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010730_026_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_LTWGVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010752_007_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011008_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011056_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011056_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011056_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011056_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011057_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011063_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011117_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTXQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011336_008_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011347_019_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011417_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011681_008_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 0.2 (275.6) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++CSGO_TG_R6 | 0.2 (20.4) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_V1 | 0.2 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | VT_350 | 0.2 (0) | Vic to Tas on Basslink upper limit of 350 MW | Outage
T-V-MNSP1 Import | #R009844_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009846_018_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009846_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009944_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009985_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VT_300, Effective Date: 08/01/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010373_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLTXVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010395_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R010407_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010628_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010752_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010752_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010814_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R010896_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORCVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011034_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011056_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011065_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011135_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011190_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011196_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011267_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011378_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011378_012_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011379_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R011651_013_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_DDSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
T-V-MNSP1 Import | #R011718_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VT_000, Effective Date: 05/08/2008, Version: 1 | Outage
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R6 | 0.1 (0.5) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_QA | 0.1 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
T-V-MNSP1 Import | V::N_HYSE_xxx | 0.1 (19.8) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line One Heywood to South East 275 kV line was out for 9.7 days in 2014 compared to 45.1 days in 2013 | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 662.4 (184.0) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-S-MNSP1 Export | V::N_NILxxx | 310.9 (8.4) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
V-S-MNSP1 Export | N^^V_NIL_1 | 105.0 (0) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
V-S-MNSP1 Export | V>>V-MSUT_1 | 87.6 (39.5) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line The Murray to Upper Tumut (65) 330 kV line was out for 33.3 days in 2014 compared to 18.0 days in 2013 | Outage
V-S-MNSP1 Export | V^SML_NSWRB_2 | 65.3 (53.8) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL
V-S-MNSP1 Export | VSML_ZERO | 46.7 (423.9) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V>>SML_NIL_7A | 41.0 (64.9) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line | NIL
V-S-MNSP1 Export | V>>SML_NIL_8 | 39.8 (27.9) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
V-S-MNSP1 Export | V>>SML_NIL_1 | 26.2 (11.9) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line | NIL
V-S-MNSP1 Export | V>>SML_NIL_7B | 24.5 (17.9) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
V-S-MNSP1 Export | V>SMLBAHO1 | 23.3 (5.9) | Out = Ballarat to Horsham, or Bendigo to Kerang line, avoid overloading or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang or Ballarat to Horsham line | Outage
V-S-MNSP1 Export | V>>V_NIL1A_R | 22.6 (30.2) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line | NIL
V-S-MNSP1 Export | V>>V_MLTS_TX_2A_R | 22.3 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
V-S-MNSP1 Export | V::N_MSUT_xxx | 19.0 (13.9) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 12.2 (0) | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | V::N_MLTX_xxx | 11.5 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 11.0 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_5 | 9.4 (5.3) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
V-S-MNSP1 Export | V>>V_MLTS_TX_2B_R | 9.1 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood | Outage
V-S-MNSP1 Export | V::N_HWSM_S4 | 8.1 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-S-MNSP1 Export | V>>V_LTMS_1 | 8.1 (0) | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage
V-S-MNSP1 Export | V::N_JNWO_xxx | 7.3 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>SMLBAHO4 | 7.0 (41.6) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage
V-S-MNSP1 Export | V::N_HWSM_Q4 | 6.1 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SML_BUDP_2 | 5.9 (13.1) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage
V-S-MNSP1 Export | V>>SML_BESH_1 | 5.3 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Waubra to Horsham 220 kV line section for trip of the Ballarat to Bendigo 220 kV line, feedback | Outage
V-S-MNSP1 Export | V>>V_EPTT_3 | 5.0 (0) | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to North) for loss of the parallel line, feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_V4 | 4.8 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 4.6 (2.9) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2_P | 4.6 (0.8) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
V-S-MNSP1 Export | V>>N_SMHTX_2 | 4.3 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | V::N_DDSM_V4 | 4.2 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-X_MSUT_LTUT_B | 3.8 (0) | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid O/L DDTS to WOTS 330kV line on trip of Lower Tumut to Murray (66) line, Feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_V3 | 3.8 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | CA_SPS_42375E8A_01 | 3.6 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LHPA on trip of LTSS-MSS (66) 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-S-MNSP1 Export | V::N_DDSM_V3 | 3.4 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | S>RBTU2_DVBG_WEWT | 3.3 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines; avoid O/L Waterloo East-Waterloo 132kV line on trip of Davenport - Bungama 275KV line. | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2B_R | 3.3 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-S-MNSP1 Export | V::N_LTWG_xxx | 3.2 (1.8) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V::N_BUDP_xxx | 3.1 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-S-MNSP1 Export | V::N_ROSM_xxx | 3.1 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>>SML_BESH_3 | 3.1 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line (flow from MLTS to BATS) for trip of the Moorabool to Elaine to Ballarat 220 kV line and Mt Mercer Wind Farm, feedback | Outage
V-S-MNSP1 Export | V::N_JNWG_xxx | 3.0 (0.5) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>>V_BAELML_1 | 2.9 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage
V-S-MNSP1 Export | N^^V_NIL_2 | 2.7 (20.8) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL
V-S-MNSP1 Export | V::N_SMCS_xxx | 2.6 (0) | Out = South Morang 330 kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-S-MNSP1 Export | V::N_HWSM_S3 | 2.4 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-S-MNSP1 Export | V::N_EPMB_xxx | 2.3 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>SMLHORC1 | 2.3 (0.3) | Out = Horsham to Red Cliffs 220kV line, avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line | Outage
V-S-MNSP1 Export | V>>SML_NIL_1_5M | 2.0 (0) | Out = Nil, avoid O/L Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Elaine To Moorabool 220 kV line and Mt Mercer Wind Farm, 5 minute line ratings, feedback | NIL
V-S-MNSP1 Export | V>>S_RBTU2_BRPA_WTTP | 1.7 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_EPTT_2_P | 1.7 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, parallel mode, feedback | Outage
V-S-MNSP1 Export | VSML_220 | 1.6 (68.1) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL
V-S-MNSP1 Export | V>>V_EPTT_2A_R | 1.5 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode, feedback | Outage
V-S-MNSP1 Export | VSML_000 | 0.9 (0) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | CA_SPS_43667C70_01 | 0.8 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-S-MNSP1 Export | V>>V_EPTT_2B_R | 0.8 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
V-S-MNSP1 Export | #R011378_012_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011710_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #V-S-MNSP1_I_E | 0.7 (0) | V-S-MNSP1.ENERGY * -1 >= 20 (Wt = 35) | Outage
V-S-MNSP1 Export | #R010162_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011057_011_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011620_005_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_HYMLQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011651_013_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_DDSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011734_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | V::N_DDSM_V2 | 0.5 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_DDWO_xxx | 0.5 (0) | Out = Dederang to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>SML_NSWRB_10 | 0.5 (0) | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL
V-S-MNSP1 Export | #R010395_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011047_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011183_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011336_008_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011347_019_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011347_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011379_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011431_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011444_018_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011444_018_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011651_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R009844_019_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009844_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010172_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010242_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010242_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010384_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010528_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010528_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010628_007_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010730_026_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_LTWGVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010814_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010970_018_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011034_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011065_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011183_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011244_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>SMLBAHO4, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011378_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011417_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011431_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011437_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011474_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011474_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | CA_SPS_42008454_01 | 0.3 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-S-MNSP1 Export | CA_SPS_42009181_01 | 0.3 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-S-MNSP1 Export | V>>S_RBTU2_BUPA_BRPA | 0.3 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines , avoid O/L Brinkworth - Templers West line on trip of Bungama - Blyth West 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_8 | 0.3 (0) | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines; Feedback | NIL
V-S-MNSP1 Export | V>SMLKGRC1 | 0.3 (0) | Out = Kerang to Redcliffs 220kV line, avoid overloading Darlington Pt to Balranald (X5/1) 220kV line for trip of Ballarat to Waubra to Horsham 220 kV line | Outage
V-S-MNSP1 Export | #R009795_018_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>SMLBAHO4, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009796_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>SMLBAHO1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010119_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint S>>NIL_NOTI_NOTI_8, Effective Date: 06/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010189_026_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010236_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_SMDDMS_V21_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010236_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_SMDDMS_V21_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010896_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORCQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011034_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011056_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011213_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLTXQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011328_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BUDPQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011328_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011336_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011437_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | N>>N-NIL_DPTX | 0.3 (0) | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other | NIL
V-S-MNSP1 Export | S>>NIL_NIL_TINO3 | 0.3 (0) | Out= Nil with Torrens Island 66kV CB6W2, CB6E4 & CB6C6 open, avoid O/L Torrens Island - New Osborne No.3 66kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_QB | 0.3 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 2 | Outage
V-S-MNSP1 Export | #R009795_015_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>SMLBAHO1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009795_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>SMLBAHO4, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009846_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010069_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010069_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010162_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010172_019_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010189_026_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010604_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010628_007_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010730_023_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011027_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011056_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011056_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011056_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011057_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011063_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011117_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTXQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011190_006_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMBQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011417_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011681_008_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | N^^V_SMTXH2_2 | 0.2 (0) | Out = South Morang H1 330/220 kV transformer, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage
V-S-MNSP1 Export | V::N_DDSM_V1 | 0.2 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N-X_MSUT_LTUT | 0.2 (0) | Out= Murray-UpperTumut(65) and Lower Tumut-Upper Tumut (64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
V-S-MNSP1 Export | V>>N_SMHTX_1 | 0.2 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | #R009794_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>SMLBAHO4, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009846_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009944_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010174_018_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>N-X_MSUT_LTUT_B, Effective Date: 18/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010309_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010373_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLTXVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010395_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R010407_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010482_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010752_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010814_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R010896_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORCVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011008_011_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011034_012_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011049_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011056_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011065_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011135_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011135_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011190_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011196_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011267_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011328_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011336_008_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011378_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q4, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011379_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011439_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-S-MNSP1 Export | #R011672_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R011682_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | CA_SPS_43667C70_02 | 0.1 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_QA | 0.1 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
V-S-MNSP1 Export | V::N_HYSE_xxx | 0.1 (19.2) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line One Heywood to South East 275 kV line was out for 14.6 days in 2014 compared to 67.7 days in 2013 | Outage
V-S-MNSP1 Export | V>>N-MSUT_4 | 0.1 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
V-S-MNSP1 Export | V>>SML_NIL_5 | 0.1 (0) | Out = NIL, prevent pre-contingent overload of the Ballarat to Bendigo 220 kV line, feedback | NIL
V-S-MNSP1 Export | V>>V_NIL_4A | 0.1 (0.2) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. Similar to DBUSS - Line, the DBUSS – Transformer scheme splits the Dederang 330 kV bus on trip of a Dederang transformer. | NIL
V-S-MNSP1 Export | V>>V_SMTT2_2 | 0.1 (0) | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the South Morang to Thomastown No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | V>SML_BUDP_3 | 0.1 (0) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Kerang to Wemen 220 kV line section on trip of Ballarat to Waubra to Horsham 220 kV line | Outage
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 235.3 (51.7) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips | NIL
V-S-MNSP1 Import | SVML_ZERO | 167.8 (173.7) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage
V-S-MNSP1 Import | S>>V_NIL_RBTX_MW4RB | 133.4 (0) | Out= Nil, avoid O/L Morgan Whyalla 4 to Robertstown line on trip of one Robertstown 275/132kV transformer, Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_1B | 8.5 (13.7) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line | NIL
V-S-MNSP1 Import | CA_MQS_42084A52_01 | 3.0 (0) | Constraint Automation, O/L ROBNWB_1 @R_TOWN for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1 2&3MWPS. Generated by STNET[MANFR] Host MANEEMP1(MQ) | Outage
V-S-MNSP1 Import | V>>V_NIL_3 | 2.3 (1.3) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL
V-S-MNSP1 Import | S:V_420 | 0.5 (0) | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability | Outage
V-S-MNSP1 Import | #R010104_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R010771_001_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R010771_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R011049_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R011672_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 0.4 (0) | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | V>>V_ROTT_R_2A | 0.4 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV side, feedback | Outage
V-S-MNSP1 Import | #R011067_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | S:V_580 | 0.3 (0) | Maintain maximum transfer limit of 580 MW on SA-VIC and Murraylink combined to avoid oscillatory instability | NIL
V-S-MNSP1 Import | #R011682_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | S:V_430 | 0.3 (0) | Maintain maximum transfer limit of 430 MW on SA-VIC and Murraylink combined to avoid oscillatory instability during the outage of one or more of the major transmission lines connecting NEM regions. | Outage
V-S-MNSP1 Import | #R010104_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R010916_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R011049_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R011682_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R011710_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | S>>V_NIL_NIL_HUWT | 0.1 (0.2) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL
V-SA Export | V>>S_NIL_SETB_SGKH | 271.3 (648.6) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line | NIL
V-SA Export | V::N_NILxxx | 217.7 (6.2) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
V-SA Export | S>>NIL_SETB_KHTB1 | 192.8 (0.2) | Out = Nil, avoid overloading Keith - Tailem Bend #1 132kV on trip of South East - Tailem Bend 275kV line | NIL
V-SA Export | V^^S_NIL_MAXG_xxx | 172.8 (208.3) | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off | NIL
V-SA Export | V>S_460 | 158.8 (300.3) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL
V-SA Export | V>S_NIL_HYTX_HYTX | 114.6 (249.7) | Out = Nil, avoid overloading the remaining Heywood 275/500 kV transformer on trip of one Heywood 275/500 kV transformer | NIL
V-SA Export | V>>S_NIL_PWKN_SGKH | 64.8 (40.2) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL
V-SA Export | VS_250 | 53.9 (26.3) | Victoria to South Australia on Heywood upper transfer limit of 250 MW | Outage
V-SA Export | S>>NIL_SETB_KHTB2 | 49.4 (16.9) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL
V-SA Export | V>>S_NIL_KHTB2_KHTB1 | 35.3 (3.1) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV one trip of Keith - Tailem Bend #2 132kV line, Feedback | NIL
V-SA Export | V^S_HYCP | 21.2 (0) | Out = Nil, limit Vic to SA to avoid voltage collapse in Heywood area for loss of a 500 kV circuit between Moorabool and Heywood with automatic allowance for Heywood 275 kV capacitor bank status | NIL
V-SA Export | V::N_MSUT_xxx | 16.6 (3.4) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-SA Export | V>>S_HYML_1 | 12.8 (82.7) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 1 | Outage
V-SA Export | V^^S_RBTU2_MAXG | 11.3 (0) | Out= Robertstown - Para and Robertstown - Tungkillo 275 kV lines; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | F_QNV++MLMO_L60 | 10.0 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::S_HYSE | 9.5 (2.9) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of one NPS unit or the remaining South East - Heywood 275 kV line. | Outage
V-SA Export | V::N_MLTX_xxx | 8.9 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | V::N_HWSM_S4 | 8.5 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-SA Export | F_ESTN++MLSY_L60 | 6.8 (1.1) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_SMCS_xxx | 5.4 (0) | Out = South Morang 330 kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-SA Export | V::N_HWSM_Q4 | 5.3 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_JNWO_xxx | 5.0 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | V::N_HWSM_V4 | 4.7 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | F_ESTN++HYTR_L60 | 4.2 (12.6) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_ESTN++MLSY_L5 | 3.8 (0.3) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V::N_HWSM_V3 | 3.7 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_LTWG_xxx | 3.6 (1.9) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | V^^S_PAVC_MAXG | 3.4 (36.1) | Out = Para one SVC, VIC to SA Voltage Stability limit for loss of the largest generation unit in SA | Outage
V-SA Export | V::N_HWSM_S3 | 3.1 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-SA Export | V::N_JNWG_xxx | 3.0 (0.6) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | F_ESTN++HYMO_L60 | 2.9 (1.9) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
V-SA Export | V::N_BUDP_xxx | 2.9 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-SA Export | V::N_ROSM_xxx | 2.9 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | F_QNV++MLMO_L5 | 2.2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V>>S_NIL_NIL_SGKHC | 2.2 (7.3) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on Nil trip, Feedback | NIL
V-SA Export | F_QNV++HYMO_L60 | 2.0 (1.8) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_EPMB_xxx | 1.8 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | F_ESTN++MLTR_L5 | 1.5 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | F_ESTN++MLTR_L60 | 1.5 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_ESTN++MLMO_L60 | 1.3 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | VS_400 | 1.3 (0) | Victoria to SA on VicSA upper transfer limit of 400 MW | Outage
V-SA Export | V_HYML1_2 | 1.1 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage
V-SA Export | F_ESTN++HYTR_L5 | 0.8 (2.8) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V>>S_MSTU_TBTU_TBMO | 0.8 (0) | Out= Mt Barker South - Tungkillo 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | #R011378_012_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | V>>S_TB6125+28_KHTB1 | 0.7 (1.6) | Out = Tailem Bend CBs 6125 and/or 6128 (both or either CB); Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend 132kV #1 line for loss of Tailem Bend transformer #4. | Outage
V-SA Export | #R011057_011_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011063_012_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011620_005_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_HYMLQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #V-SA_RAMP_E_F | 0.5 (0.5) | V-SA <= MAX(250, InitialFlow - 30) (Wt=35) | Outage
V-SA Export | #R009930_008_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint S>>TU_E_BUS_TUMS_8, Effective Date: 17/12/2013, Version: 1 | Outage
V-SA Export | #R010395_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011034_012_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011047_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011336_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011378_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011431_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | F_QNV++MLMO_L6 | 0.4 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V>>S_NIL_SGBL_SGKH | 0.4 (0) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on trip of Snuggery - Blanche 132kV line, Feedback. | NIL
V-SA Export | #R009836_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint S>>TU_E_BUS_TUMS_8, Effective Date: 17/12/2013, Version: 1 | Outage
V-SA Export | #R009844_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010384_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R010415_016_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010528_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010628_007_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010814_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010970_018_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011047_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011056_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011065_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011379_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011417_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
V-SA Export | #R011431_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011437_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011474_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011474_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | V>S_NIL_NIL_HYTX2 | 0.3 (0.3) | Out = NIL, avoid O/L Heywood M2 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL
V-SA Export | #R009836_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint S>>TU_E_BUS_TUMS_8, Effective Date: 17/12/2013, Version: 1 | Outage
V-SA Export | #R010119_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint S>>NIL_NOTI_NOTI_8, Effective Date: 06/03/2014, Version: 1 | Outage
V-SA Export | #R010189_026_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010649_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010896_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORCQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011034_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011056_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011213_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLTXQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011328_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BUDPQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011328_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011347_019_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011347_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011353_004_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011366_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011437_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011681_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | V::N_BYPASS_HW_SY_QB | 0.3 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 2 | Outage
V-SA Export | #R009846_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009854_004_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009944_016_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010189_026_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010283_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint S>>CGMS_TBTU_TBMO, Effective Date: 11/04/2014, Version: 1 | Outage
V-SA Export | #R010628_007_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010730_026_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_LTWGVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010752_007_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010829_006_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V^^S_PAVC_MAXG, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011027_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011056_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011057_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011063_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011117_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTXQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011190_006_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMBQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011328_015_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011336_008_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011336_012_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011353_004_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011366_004_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011417_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
V-SA Export | #R011681_008_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | F_ESTN++MLMO_L5 | 0.2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | F_QNV++MLSY_L6 | 0.2 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++MLSY_L60 | 0.2 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L5 | 0.2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L60 | 0.2 (0) | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | NRM_VIC1_SA1 | 0.2 (1.4) | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | S>>NIL_NIL_TINO3 | 0.2 (0) | Out= Nil with Torrens Island 66kV CB6W2, CB6E4 & CB6C6 open, avoid O/L Torrens Island - New Osborne No.3 66kV line on Nil trip, Feedback | NIL
V-SA Export | #R009844_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009846_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009944_016_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010373_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLTXVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010395_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R010407_016_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010415_016_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010584_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010584_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010752_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010752_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010814_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010829_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V^^S_PAVC_MAXG, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010830_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V^^S_PAVC_MAXG, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R010834_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V^^S_TB6594_35_SETB, Effective Date: 13/12/2013, Version: 1 | Outage
V-SA Export | #R010896_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORCVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011034_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011056_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011065_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011065_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011135_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011135_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | #R011190_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011196_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011267_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011379_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R011439_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
V-SA Export | F_QNV++MLSY_L5 | 0.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_BYPASS_HW_SY_QA | 0.1 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
V-SA Export | V>>S_NIL_KHTB1_KHTB2 | 0.1 (0) | Out = Nil, avoid O/L Keith - Tailem Bend #2 132kV on trip of Keith - Tailem Bend #1 132kV line, Feedback | NIL
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 616.5 (183.0) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-SA Import | S>>V_NIL_SETX_SETX | 406.2 (445.7) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer | NIL
V-SA Import | V>>V_MLTS_TX_2A_R | 19.8 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
V-SA Import | V>>V_ROTS_TX_2B_R | 9.1 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage
V-SA Import | V>>V_KTS_TX_A3_2B_R | 8.4 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-SA Import | F_S++HYML_L60 | 8.3 (10.7) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 60 second requirement | Outage
V-SA Import | V>>V_MLTS_TX_2B_R | 8.2 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood | Outage
V-SA Import | V>>V_KTS_TX_A2_2A_R | 7.8 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | F_S++HYSE_L60 | 7.3 (58.4) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
V-SA Import | V>>V_KTS_TX_A2_2_P | 4.3 (0.8) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
V-SA Import | V>>V_KTSY_2_R | 2.7 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of Keilor to South Morang 500kV line, radial mode, YWG1 on 220 kV, feedback | Outage
V-SA Import | V>>V_KTS_TX_A2_2B_R | 2.1 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-SA Import | V>>V_CBTS_TX_2A_R | 1.8 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-SA Import | V>>V_EPTT_2_P | 1.7 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, parallel mode, feedback | Outage
V-SA Import | V>>V_EPTT_2A_R | 1.5 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode, feedback | Outage
V-SA Import | CA_SPS_43667C70_01 | 0.8 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-SA Import | V>>V_EPTT_2B_R | 0.8 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
V-SA Import | S>V_NIL_HYTX_HYTX | 0.7 (0) | Out = Nil, avoid overloading a Heywood 275/500 kV transformer on trip of the other Heywood 275/500 kV transformer | NIL
V-SA Import | #R010162_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | F_S++HYML_L6 | 0.6 (2.2) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 6 second requirement | Outage
V-SA Import | V>>V_KTS_TX_A3_2A_R | 0.6 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | F_S++HYSE_L5 | 0.5 (6.3) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage
V-SA Import | S:V_420 | 0.5 (0) | South Australia to Victoria on both Heywood and Murraylink maximum transfer limit to avoid oscillatory instability | Outage
V-SA Import | #R011741_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | S:V_580 | 0.4 (0) | Maintain maximum transfer limit of 580 MW on SA-VIC and Murraylink combined to avoid oscillatory instability | NIL
V-SA Import | V>>V_ROTT_R_2A | 0.4 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV side, feedback | Outage
V-SA Import | V>>V_NIL_6_P | 0.3 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood 3/5 parallel mode, feedback | NIL
V-SA Import | S:V_430 | 0.3 (0) | Maintain maximum transfer limit of 430 MW on SA-VIC and Murraylink combined to avoid oscillatory instability during the outage of one or more of the major transmission lines connecting NEM regions. | Outage
V-SA Import | S:V_SA_PSS | 0.3 (0) | Out= Nil; SA to Vic Oscillatory stability limit based on PSS availability in South Australia. | NIL
V-SA Import | #R010069_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | #R010069_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | #R010162_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | F_S++HYML_L5 | 0.2 (0.8) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 5 minute requirement | Outage
V-SA Import | F_S++HYSE_L6 | 0.2 (5.7) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 6 second requirement | Outage
V-SA Import | V>>V_CBTS_TX_3A_R | 0.2 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-SA Import | #R010309_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | #R011741_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 04/03/2014, Version: 1 | Outage
V-SA Import | #V-SA_RAMP_I_F | 0.1 (1.8) | V-SA >= MIN(-60, InitialFlow + 50) (Wt=35) | Outage
V-SA Import | CA_SPS_43667C70_02 | 0.1 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
V-SA Import | S>>V_NIL_KHTB2_KHTB1 | 0.1 (0) | Out= Nil, avoid O/L Tailem Bend - Keith #1 132kV on trip of Tailem Bend - Keith #2 132kV line, Feedback | NIL
V-SA Import | V>>SML_NIL_5 | 0.1 (0) | Out = NIL, prevent pre-contingent overload of the Ballarat to Bendigo 220 kV line, feedback | NIL
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 672.3 (188.0) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
VIC1-NSW1 Export | V::N_NILxxx | 311.6 (9.0) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
VIC1-NSW1 Export | V>>V-MSUT_1 | 87.9 (40.8) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | Outage
VIC1-NSW1 Export | V>>SML_NIL_7A | 41.6 (71.5) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line | NIL
VIC1-NSW1 Export | V>>SML_NIL_8 | 41.0 (28.8) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
VIC1-NSW1 Export | V>>SML_NIL_7B | 27.0 (18.2) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
VIC1-NSW1 Export | V>>SML_NIL_1 | 25.4 (13.1) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line | NIL
VIC1-NSW1 Export | V>>V_NIL1A_R | 22.7 (30.1) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line | NIL
VIC1-NSW1 Export | V>>V_MLTS_TX_2A_R | 22.3 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
VIC1-NSW1 Export | V::N_MSUT_xxx | 18.7 (15.8) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2A_R | 12.6 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_MLTX_xxx | 11.6 (0) | Out = Moorabool 500/220kV transformer, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>V_LTMS_1 | 10.6 (0) | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 10.1 (5.1) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2B_R | 9.4 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
VIC1-NSW1 Export | V>>V_MLTS_TX_2B_R | 9.1 (0) | Out = Moorabool A1 or A2 500/220kV transformer, avoid O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_2B_R | 9.1 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_S4 | 7.9 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 500 kV. Limit only applied during Heywood flow from SA to VIC | Outage
VIC1-NSW1 Export | V::N_JNWO_xxx | 7.6 (0) | Out = Jindera to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_HWSM_Q4 | 6.2 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMCS_xxx | 5.6 (0) | Out = South Morang 330 kV series capacitor, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
VIC1-NSW1 Export | V>>SML_BESH_1 | 5.3 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Waubra to Horsham 220 kV line section for trip of the Ballarat to Bendigo 220 kV line, feedback | Outage
VIC1-NSW1 Export | V>>V_EPTT_3 | 5.0 (0) | Out = Eildon to Thomastown 220kV line, avoid O/L a Dederang to South Morang 330kV line (flow to North) for loss of the parallel line, feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_V4 | 4.8 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HA | 4.6 (2.9) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2_P | 4.6 (0.8) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
VIC1-NSW1 Export | V>>N_SMHTX_2 | 4.3 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L Thomastown to South Morang No. 2 or No. 1 220 kV line (flow TTS to SMTS) on trip of South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Export | VN_0700 | 4.3 (0) | Discretionary Vic to NSW transfer upper limit of 700 MW | Outage
VIC1-NSW1 Export | V::N_DDSM_V4 | 4.1 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-X_MSUT_LTUT_B | 3.8 (0) | Out = Murray-Upper Tumut and Lower Tumut-Upper Tumut(65+64), avoid O/L DDTS to WOTS 330kV line on trip of Lower Tumut to Murray (66) line, Feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_V3 | 3.8 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | CA_SPS_42375E8A_01 | 3.6 (0) | Constraint Automation, O/L DDTS_WOTS_330 @DDTS for CTG LHPA on trip of LTSS-MSS (66) 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | V::N_DDSM_V3 | 3.4 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_LTWG_xxx | 3.3 (2.0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2B_R | 3.3 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
VIC1-NSW1 Export | V::N_BUDP_xxx | 3.1 (0) | Out = Buronga to Darlington Point 220 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
VIC1-NSW1 Export | V::N_ROSM_xxx | 3.1 (0) | Out = Rowville to South Morang 500kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>SML_BESH_3 | 3.1 (0) | Out = Bendigo to Shepparton 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line (flow from MLTS to BATS) for trip of the Moorabool to Elaine to Ballarat 220 kV line and Mt Mercer Wind Farm, feedback | Outage
VIC1-NSW1 Export | V::N_JNWG_xxx | 2.9 (0.4) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>V_BAELML_1 | 2.9 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line, avoid O/L Moorabool to Ballarat No. 1 220 kV line on trip of Moorabool to Terang 220 kV line, feedback | Outage
VIC1-NSW1 Export | V>>V_KTSY_2_R | 2.8 (0) | Out = Keilor to Sydenham 500 kV line, avoid overload of South Morang F2 500/330 txfmr for trip of Keilor to South Morang 500kV line, radial mode, YWG1 on 220 kV, feedback | Outage
VIC1-NSW1 Export | V::N_EPMB_xxx | 2.3 (0) | Out = Eildon to Mt Beauty 220kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>SML_NIL_1_5M | 2.0 (0) | Out = Nil, avoid O/L Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Elaine To Moorabool 220 kV line and Mt Mercer Wind Farm, 5 minute line ratings, feedback | NIL
VIC1-NSW1 Export | VN_0750 | 1.9 (0) | Discretionary Vic to NSW transfer upper limit of 750 MW | Outage
VIC1-NSW1 Export | V::N_HWSM_S3 | 1.8 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink VIC to TAS, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
VIC1-NSW1 Export | V>>V_CBTS_TX_2A_R | 1.8 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid pre-contingent O/L South Morang F2 500/330 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V>>V_EPTT_2_P | 1.7 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, parallel mode, feedback | Outage
VIC1-NSW1 Export | V>>V_EPTT_2A_R | 1.5 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode, feedback | Outage
VIC1-NSW1 Export | CA_SPS_43667C70_01 | 0.8 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPS on trip of TRTS-HYTS-APD1 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | V>>V_EPTT_2B_R | 0.8 (0) | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
VIC1-NSW1 Export | #R011378_012_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010162_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010522_010_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N>>N-MPWW_ONE_9, Effective Date: 04/10/2013, Version: 1 | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2A_R | 0.6 (0) | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | #R011057_011_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011063_012_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011620_005_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_HYMLQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011651_013_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_DDSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 0.5 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_DDWO_xxx | 0.5 (0) | Out = Dederang to Wodonga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | #R010395_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010522_010_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N>>N-MPWW_ONE_9, Effective Date: 04/10/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011034_012_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011047_012_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011183_014_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011347_019_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011347_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011379_019_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011431_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011444_018_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011444_018_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011651_013_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_DDSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011741_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | V>>N-JNWG_RADIAL_1 | 0.4 (0.6) | Out = Jindera to Wagga(62), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | V>>V_NIL_6_P | 0.4 (0) | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood 3/5 parallel mode, feedback | NIL
VIC1-NSW1 Export | #R009844_019_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009844_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010172_019_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010242_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010242_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010384_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010528_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010528_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_ROSMVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010628_007_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010730_026_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_LTWGVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010814_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_QA, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010970_018_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_JNWOQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011047_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011065_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011183_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_DDSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011378_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011417_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011431_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011437_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011474_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011474_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010189_026_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010236_013_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_X_SMDDMS_V21_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010236_013_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_X_SMDDMS_V21_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010896_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HORCQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011034_012_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011056_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011213_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_MLTXQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011280_026_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>N-JNWG_RADIAL_1, Effective Date: 08/10/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011328_014_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_BUDPQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011328_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011336_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011336_012_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011437_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011681_008_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_QB | 0.3 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 2 | Outage
VIC1-NSW1 Export | #R009846_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010069_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010069_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010162_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010172_019_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010189_026_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_DDWOVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010628_007_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010752_007_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011008_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011027_018_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011056_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011056_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011056_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_SMCSVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011057_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_ROSMVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011063_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011117_005_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_MLTXQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011190_006_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMBQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011336_012_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_HWSM_V4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011417_011_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWCB_V3, Effective Date: 24/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011681_008_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | V::N_DDSM_V1 | 0.2 (0) | Out = Dederang to South Morang 330 kV line, prevent transient instability for fault and trip of remaining Dederang to South Morang 330 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-DDWO_RADIAL_1 | 0.2 (0) | Out = Dederang to Wodonga, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-X_MSUT_LTUT | 0.2 (0) | Out= Murray-UpperTumut(65) and Lower Tumut-Upper Tumut (64), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N_SMHTX_1 | 0.2 (0) | Out = South Morang H1 or H2 330/220 kV txfmr, avoid O/L of South Morang H2 or H1 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Export | V>>V_CBTS_TX_3A_R | 0.2 (0) | Out = Cranbourne A1 500/220kV txfmr, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 or A2 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | #R009846_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_BURCVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009944_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010174_018_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>N-X_MSUT_LTUT_B, Effective Date: 18/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010309_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010373_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MLTXVC_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010395_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R010407_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010482_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010730_023_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010752_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010814_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_VA, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R010896_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HORCVE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011034_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011056_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011065_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSQD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011065_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_SMCSVD_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011135_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011135_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_S3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011190_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011196_007_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_EPMBQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011267_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_JNWGQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011328_015_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_BUDPQE_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011336_008_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_S4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011378_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_Q4, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011379_019_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_JNWOQF_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R011439_011_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V3, Effective Date: 21/02/2014, Version: 1 | Outage
VIC1-NSW1 Export | #R011741_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A3_2A_R, Effective Date: 04/03/2014, Version: 1 | Outage
VIC1-NSW1 Export | CA_SPS_428FB629_01 | 0.1 (0) | Constraint Automation, O/L 94E @MT_PIPER for CTG LNWT on trip of MT_PIPER-WWANG 70 330KV LINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | CA_SPS_43667C70_02 | 0.1 (0) | Constraint Automation, O/L SMTS TRANSF F2TR_330 for CTG MVPQ on trip of MOPS-HYTS-APD2 500KV & APD POTLINE. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_QA | 0.1 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink TAS to VIC, QLD accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_HYSE_xxx | 0.1 (21.0) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
VIC1-NSW1 Export | V>>N-MSUT_4 | 0.1 (0) | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | V>>SML_NIL_5 | 0.1 (0) | Out = NIL, prevent pre-contingent overload of the Ballarat to Bendigo 220 kV line, feedback | NIL
VIC1-NSW1 Export | V>>V_SMTT2_2 | 0.1 (0) | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the South Morang to Thomastown No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 207.8 (102.1) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
VIC1-NSW1 Import | V>>V_NIL_1B | 9.3 (13.5) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line | NIL
VIC1-NSW1 Import | N^^V_MSUT_1 | 6.9 (1.8) | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_NIL_2 | 4.4 (21.0) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL
VIC1-NSW1 Import | V>>V_NIL_3 | 3.6 (1.3) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL
VIC1-NSW1 Import | N^^V_MSDD1 | 3.3 (0) | Out = Murray to Dederang No.1 or No.2 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_EPMB_1 | 2.6 (0) | Out = Eildon to Mount Beauty 220 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | N>>V-NIL_O | 2.1 (1.1) | Out = Nil, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line and subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines | NIL
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 1.6 (3.6) | Negative Residue Management constraint equation for NSW to VIC flow | NIL
VIC1-NSW1 Import | V>>V_NIL_4A | 1.1 (0.5) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. | NIL
VIC1-NSW1 Import | #R010612_004_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N^^V_JNWO, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Import | N^^V_DDSM1 | 0.4 (0) | Out = Dederang to South Morang 330 kV line, avoid voltage collapse in Southern NSW for loss of the largest VIC generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V_ROTT_R_2A | 0.4 (0) | Out = Rowville to Thomastown 220 kV line, avoid overloading the Richmond to Brunswick 220 kV cable for trip of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV side, feedback | Outage
VIC1-NSW1 Import | #R010457_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Import | N>>N-NIL_DPTX | 0.3 (0) | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other | NIL
VIC1-NSW1 Import | #R009821_005_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^^V_SMTXH1_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Import | N>>V-LTMS_5 | 0.2 (0) | Out = Lower Tumut to Murray (66) 330 kV line, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines | Outage
VIC1-NSW1 Import | N^^V_SMTXH2_2 | 0.2 (0) | Out = South Morang H1 330/220 kV transformer, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage
VIC1-NSW1 Import | #R010596_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^V_EPMB_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Import | V>>V_NIL_4C | 0.1 (0.1) | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL

## Outages 2014
Constraint Set ID | 2014 DAYS (2013 DAYS) | Description
N-MBTE_1 | 365.0 (0) | One Directlink cable
N-X_MBTE_2 | 169.8 (214.9) | Two Directlink cables
Q-X_BC_CB8L2_CB99012 | 130.9 (0) | Bulli Creek CBs (8L2 and 99012) or (8M2 and 99022)
N-LSLS_9U8 | 109.4 (0) | One Lismore 330 to Lismore 132 (9U8 or 9U9 or 9W1) 132 kV line
N-X_MBTE_3 | 70.3 (158.1) | All three Directlink cables
F-I_TL_0500 | 55.3 (0) | FCAS Lower Requirements for a NEM Network Event, TL = 500
V-HWMW | 44.0 (0) | Outage of Hazelwood PS to Morwell PS 220 kV line
Q-BCKBR_9901_9902 | 40.9 (0) | One Bulli Creek to Braemar (9901 or 9902) 330 kV line
F-I_ML_APD | 38.2 (0) | Out=Nil, Dymanic FCAS for APD Load Event
I-MSUT | 16.7 (9.0) | Murray to Upper Tumut (65) 330 kV line
V-MLTX_R | 15.4 (0) | Outage = Moorabool (A1 or A2) 500/220kV transformer, Radial Mode
V-KTTX_A2_OR_A4_R | 13.9 (0) | Outage = Keilor 500/220kV A2 or A4 transformer, Radial
I-ML_ZERO | 10.0 (27.2) | Limit Murraylink to zero in either direction
N-AR_VC1 | 9.9 (0) | Armidale SVC
F-I-BCDM_ONE | 9.8 (1.1) | One Bulli Creek to Dumaresq 330 kV line - FCAS Requirements
I-BCDM_ONE | 9.8 (1.1) | One Bulli Creek to Dumaresq 330 kV line
N-KKLS_967 | 9.3 (3.8) | Koolkhan to Lismore (967) 132 kV line
V-KTTX_A3_R | 7.4 (0) | Outage = Keilor 500/220kV A3 transformer, Radial
V-HWSM | 7.2 (2.5) | Hazelwood to South Morang 500 kV line
I-HYSE | 4.9 (22.6) | One Heywood to South East 275 kV line
Q-GB_VC | 4.7 (0) | Greenbank SVC
V-HYTX | 4.6 (21.6) | One Heywood 500/275 kV (M1 or M2) transformer
V-SMSY | 4.0 (0) | One South Morang to Sydenham 500 kV line
V-MLSY | 3.8 (0) | Moorabool to Sydenham 500 kV line
N-ARTW_85 | 3.4 (0.3) | Armidale to Tamworth (85) 330 kV line
V-EPMB | 3.3 (0) | Outage = Eildon to Mt Beauty 220kV line
S-DVCN | 3.3 (0) | Davenport to Canowie 275 kV line
Q-BK_VC | 3.1 (0) | Blackwall SVC
N-LTYS_03 | 2.9 (0) | Lower Tumut to Yass (3) 330 kV line
N-LSTN_96L | 2.8 (0) | Lismore to Tenterfield (96L) 132 kV line
S-RBPA | 2.8 (0) | Out= Robertstown - Para 275 kV line
I-LTMS | 2.8 (0) | Lower Tumut to Murray (66) 330 kV line
Q-SP_VC | 2.5 (0) | South Pine SVC
N-LDTW_84 | 2.5 (0) | Liddell to Tamworth (84) 330 kV line
S-BNMT | 2.3 (4.5) | Blanche to Mt Gambier 132 kV line
NSA-Q_BARCALDN | 2.2 (1.2) | Clermont to Lilyvale (7153) 132 kV line, Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine This NSA constraint set is included as it is only invoked under outage conditions
N-ARDM_ONE | 2.2 (0) | One Armidale to Dumaresq (8C or 8E) line
F-N-ARDM_ONE | 2.2 (1.1) | One Armidale to Dumaresq (8C or 8E) 330 kV line
V-DDSM | 2.1 (0) | One Dederang to South Morang 330 kV line
V-EPTT_R | 2.1 (1.2) | Eildon to Thomastown 220 kV line
I-MUTE_757 | 2.0 (0) | Mudgeeraba to Terranora (757) 110 kV line
N-MUTW_88 | 2.0 (0) | Out = Muswellbrook to Tamworth (88) line
F-N-MUTW_88 | 2.0 (0) | Muswellbrook to Tamworth (88) 330 kV line
N-UTYS_2 | 1.9 (0) | Upper Tumut to Yass (2) 330 kV line
I-MUTE_758 | 1.8 (0) | Mudgeeraba to Terranora (758) 110 kV line
V-ROTX_R | 1.7 (0) | Outage = Rowville 500/220kV (A) transformer, Radial
N-AR_BUS5_N-2 | 1.7 (0) | Out = Nil, loss of Armidale No.5 330kV reclassified as credible
V-DDMS | 1.6 (1.5) | One Dederang to Murray (67 or 68) 330 kV line
N-ARTW_86 | 1.6 (4.7) | Armidale to Tamworth (86) 330 kV line
T-PMPO_110 | 1.6 (0) | Out=A single Palmerston-Poatina 110KV line. One line out of service only
N-CNLT_07 | 1.5 (0) | Canberra to Lower Tumut line
S-DVBL | 1.4 (0) | Out = Davenport - Belalie 275kV line
S-RBPA+RBTU | 1.4 (0) | Out = Robertstown - Para and Robertstown - Tungkillo 275kV lines.
V-MLTR | 1.2 (0.3) | Moorabool to Tarrone No.1 500 kV line
V-MLMO | 1.0 (0) | Moorabool to Mortlake 500 kV line
I-CTRL_ISSUE_TE | 0.9 (0) | DC Link Control Issue Constraint for Terranora
V-SMSC | 0.9 (0) | One or both South Morang 330 kV series capacitors
S-PA_VC_1 | 0.8 (6.4) | One Para SVC
V-HWCB4 | 0.8 (1.2) | Hazelwood to Cranbourne No.4 500 kV line
N-CNUT_01 | 0.8 (0) | Canberra to Upper Tumut (01) 330 kV line
V-HYTR | 0.8 (2.1) | Heywood to Tarrone 500 kV line
N-CNYS_9 | 0.7 (0) | Out = Canberra - Yass (9)
N-AR_330_BS1 | 0.7 (0) | Out= Armidale No.1 330kV bus
N-LTUT_64_15M | 0.6 (22.2) | Lower Tumut to Upper Tumut (64) 330 kV line
N-WOODLWN1_ZERO | 0.5 (0) | Woodlawn unit upper limit of 0 MW
S-BRBG | 0.5 (0) | Out = Brinkworth to Redhill to Bungama 132kV lines (Note: outage also takes out Clements Gap Windfarm).
V-KTSM_R | 0.4 (0) | Keilor to South Morang 500 kV line
I-X_MSUT_LTUT | 0.4 (0) | Out= Murray - Upper Tumut (65) & Lower Tumut-Upper Tumut (64) line
S-MYTX1_44248OPEN | 0.4 (0.1) | Out = Mayura No.1 132/33kV transformer O/S (with 33kV bus tie isolator 44248 open)
V-HYMO | 0.3 (0.9) | Heywood to Mortlake No.2 500 kV line
N-TW_330_BUS3 | 0.3 (0) | Out= Tamworth No.3 330kV bus
T-FASH_N-2_HM_O_3 | 0.2 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, West Coast 110/220 kV parallel open
CA_MQS_42084A52 | 0.2 (0) | Constraint Automation Set. Generated by STNET[MANFR] Host MANEEMP1(MQ)
V-KTSY_R | 0.2 (0) | Keilor to Sydenham 500 kV line
S-PA_EAST_BUS | 0.1 (0) | Out= Para 275kV East bus (i.e. SVC2,Cap bank 2,Tx2,CB6509, CB6512,CB6520,CB6517 O/S)
I-HYSE_N-2 | 0.1 (0) | Loss of both Heywood to South East 275kV lines reclassified as credible contingency.
S-X_PLN_01 | 0.1 (0) | Whyalla to Yadnarie line, Port Lincoln PS islanded
S-MTSE | 0.1 (0) | Mt Gambier to South East 132 kV line
S-PATU | 0.0 (0) | Out = Para to Tungkillo 275 kV line
S-X_PLN_02 | 0.0 (0) | Yadnarie to Port Lincoln line
I-OSC_STAB_MON | 0.0 (0) | Out = Oscillatory Stability Monitoring

## Outage stats 2014
TNSP | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2009 | 14 | 33 | 5 | 4
2010 | 25 | 40 | 6 | 2
2011 | 15 | 31 | 5 | 4
2012 | 15 | 23 | 2 | 1
2013 | 10 | 7 | 0 | 1
ElectraNet 2009 | 51 | 145 | 186 | 154
2010 | 104 | 226 | 186 | 226
2011 | 59 | 201 | 364 | 186
2012 | 240 | 457 | 582 | 424
2013 | 200 | 435 | 874 | 136
Essential E 2009 | 2 | 35 | 72 | 5
2010 | 5 | 34 | 62 | 11
2011 | 3 | 58 | 127 | 1
2012 | 15 | 83 | 177 | 0
2013 | 19 | 41 | 81 | 0
Powerlink 2009 | 136 | 455 | 767 | 4
2010 | 88 | 451 | 832 | 32
2011 | 114 | 445 | 722 | 12
2012 | 317 | 885 | 1219 | 26
2013 | 301 | 812 | 1183 | 96
SPAusNet 2009 | 152 | 970 | 893 | 66
2010 | 158 | 817 | 757 | 38
2011 | 147 | 794 | 650 | 11
2012 | 234 | 972 | 738 | 36
2013 | 146 | 895 | 502 | 56
Transend 2009 | 40 | 138 | 122 | 47
2010 | 41 | 143 | 112 | 62
2011 | 17 | 115 | 97 | 92
2012 | 57 | 279 | 250 | 83
2013 | 111 | 550 | 496 | 281
TransGrid 2009 | 138 | 668 | 792 | 279
2010 | 123 | 816 | 782 | 384
2011 | 129 | 602 | 873 | 534
2012 | 198 | 533 | 900 | 629
2013 | 251 | 452 | 849 | 590

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.