## in
Facility | FCESS Service | Maximum Service Quantity | Units | Facility Speed Factor (? in sec) | Operating Condition Description | Last updated
ALINTA_PNJ_U1 | Contingency Reserve Lower | 58 | MW | N/A | All operating modes | 2023-11-29
ALINTA_PNJ_U1 | Regulation Lower | 30 | MW | N/A | All operating modes
ALINTA_PNJ_U1 | Regulation Raise | 30 | MW | N/A | All operating modes
ALINTA_PNJ_U1 | RoCoF Control Service | 1085 | MWs | N/A | All operating modes
ALINTA_PNJ_U2 | Contingency Reserve Lower | 30 | MW | N/A | All operating modes
ALINTA_PNJ_U2 | Contingency Reserve Raise | 6 | MW | 6 | All operating modes
ALINTA_PNJ_U2 | Regulation Lower | 30 | MW | N/A | All operating modes
ALINTA_PNJ_U2 | Regulation Raise | 30 | MW | N/A | All operating modes
ALINTA_PNJ_U2 | RoCoF Control Service | 1085 | MWs | N/A | All operating modes
ALINTA_WGP_GT | Contingency Reserve Lower | 60 | MW | N/A | Gas fuel operation
ALINTA_WGP_GT | Contingency Reserve Raise | 55 | MW | 15 | Gas fuel operation
ALINTA_WGP_GT | Regulation Lower | 30 | MW | N/A | Gas fuel operation
ALINTA_WGP_GT | Regulation Raise | 30 | MW | N/A | Gas fuel operation
ALINTA_WGP_GT | RoCoF Control Service | 1494 | MWs | N/A | Gas fuel operation
ALINTA_WGP_U2 | Contingency Reserve Lower | 60 | MW | N/A | Gas fuel operation
ALINTA_WGP_U2 | Contingency Reserve Raise | 60 | MW | 15 | Gas fuel operation
ALINTA_WGP_U2 | Regulation Lower | 30 | MW | N/A | All operating modes
ALINTA_WGP_U2 | Regulation Raise | 30 | MW | N/A | All operating modes
ALINTA_WGP_U2 | RoCoF Control Service | 1494 | MWs | N/A | All operating modes
BW1_BLUEWATERS_G2 | RoCoF Control Service | 1077 | MWs | N/A | All operating modes
BW2_BLUEWATERS_G1 | RoCoF Control Service | 1077 | MWs | N/A | All operating modes
COCKBURN_CCG1 | Regulation Lower | 60 | MW | N/A | All operating modes
COCKBURN_CCG1 | Regulation Raise | 60 | MW | N/A | All operating modes
COCKBURN_CCG1 | RoCoF Control Service | 2176 | MWs | N/A | With both gas turbine and steam turbine in service
COCKBURN_CCG1 | RoCoF Control Service | 1497 | MWs | N/A | With just gas turbine in service
COLLIE_G1 | Contingency Reserve Lower | 16.5 | MW | N/A | All operating modes
COLLIE_G1 | Contingency Reserve Raise | 24.7 | MW | 10 | All operating modes
COLLIE_G1 | RoCoF Control Service | 1196 | MWs | N/A | All operating modes
KEMERTON_GT11 | Contingency Reserve Lower | 76 | MW | N/A | Gas fuel operation
KEMERTON_GT11 | Contingency Reserve Lower | 71 | MW | N/A | Distillate fuel operation
KEMERTON_GT11 | Contingency Reserve Raise | 76 | MW | 15 | Gas fuel operation
KEMERTON_GT11 | Contingency Reserve Raise | 71 | MW | 15 | Distillate fuel operation
KEMERTON_GT11 | Regulation Lower | 75 | MW | N/A | Gas fuel operation
KEMERTON_GT11 | Regulation Lower | 71 | MW | N/A | Distillate fuel operation
KEMERTON_GT11 | Regulation Raise | 75 | MW | N/A | Gas fuel operation
KEMERTON_GT11 | Regulation Raise | 71 | MW | N/A | Distillate fuel operation
KEMERTON_GT11 | RoCoF Control Service | 1092 | MWs | N/A | All operating modes
KEMERTON_GT12 | Contingency Reserve Lower | 76 | MW | N/A | Gas fuel operation
KEMERTON_GT12 | Contingency Reserve Lower | 71 | MW | N/A | Distillate fuel operation
KEMERTON_GT12 | Contingency Reserve Raise | 76 | MW | 15 | Gas fuel operation
KEMERTON_GT12 | Contingency Reserve Raise | 71 | MW | 15 | Distillate fuel operation
KEMERTON_GT12 | Regulation Lower | 75 | MW | N/A | Gas fuel operation
KEMERTON_GT12 | Regulation Lower | 71 | MW | N/A | Distillate fuel operation
KEMERTON_GT12 | Regulation Raise | 75 | MW | N/A | Gas fuel operation
KEMERTON_GT12 | Regulation Raise | 71 | MW | N/A | Distillate fuel operation
KEMERTON_GT12 | RoCoF Control Service | 1092 | MWs | N/A | All operating modes
KWINANA_GT2 | Contingency Reserve Lower | 52.5 | MW | N/A | All operating modes
KWINANA_GT2 | Contingency Reserve Raise | 52.5 | MW | 10 | All operating modes
KWINANA_GT2 | Regulation Lower | 80 | MW | N/A | All operating modes
KWINANA_GT2 | Regulation Raise | 80 | MW | N/A | All operating modes
KWINANA_GT2 | RoCoF Control Service | 223 | MWs | N/A | All operating modes
KWINANA_GT3 | Contingency Reserve Lower | 52.5 | MW | N/A | All operating modes
KWINANA_GT3 | Contingency Reserve Raise | 52.5 | MW | 10 | All operating modes
KWINANA_GT3 | Regulation Lower | 80 | MW | N/A | All operating modes
KWINANA_GT3 | Regulation Raise | 80 | MW | N/A | All operating modes
KWINANA_GT3 | RoCoF Control Service | 223 | MWs | N/A | All operating modes
MUJA_G6 | Contingency Reserve Lower | 21.2 | MW | N/A | All operating modes
MUJA_G6 | Contingency Reserve Raise | 21.2 | MW | 6 | All operating modes
MUJA_G6 | RoCoF Control Service | 880 | MWs | N/A | All operating modes
MUJA_G7 | Contingency Reserve Lower | 22.7 | MW | N/A | All operating modes
MUJA_G7 | Contingency Reserve Raise | 22.7 | MW | 3 | All operating modes
MUJA_G7 | RoCoF Control Service | 880 | MWs | N/A | All operating modes
MUJA_G8 | Contingency Reserve Lower | 22.7 | MW | N/A | All operating modes
MUJA_G8 | Contingency Reserve Raise | 22.7 | MW | 6 | All operating modes
MUJA_G8 | RoCoF Control Service | 880 | MWs | N/A | All operating modes
NEWGEN_KWINANA_CCG1 | Regulation Lower | 30 | MW | N/A | All operating modes
NEWGEN_KWINANA_CCG1 | Regulation Raise | 30 | MW | N/A | All operating modes
NEWGEN_KWINANA_CCG1 | RoCoF Control Service | 2686 | MWs | N/A | With both gas turbine and steam turbine in service
NEWGEN_KWINANA_CCG1 | RoCoF Control Service | 1645 | MWs | N/A | With just gas turbine in service
NEWGEN_NEERABUP_GT1 | Regulation Lower | 40 | MW | N/A | All operating modes
NEWGEN_NEERABUP_GT1 | Regulation Raise | 40 | MW | N/A | All operating modes
PINJAR_GT1 | Contingency Reserve Lower | 12.9 | MW | N/A | Gas fuel operation
PINJAR_GT1 | Contingency Reserve Raise | 12.9 | MW | 3 | Gas fuel operation
PINJAR_GT1 | Regulation Lower | 28.5 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT1 | Regulation Lower | 25 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT1 | Regulation Raise | 28.5 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT1 | Regulation Raise | 25 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT1 | RoCoF Control Service | 248 | MWs | N/A | Gas fuel operation
PINJAR_GT2 | Contingency Reserve Lower | 12.9 | MW | N/A | Gas fuel operation
PINJAR_GT2 | Contingency Reserve Raise | 12.9 | MW | 3 | Gas fuel operation
PINJAR_GT2 | Regulation Lower | 28.5 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT2 | Regulation Lower | 25 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT2 | Regulation Raise | 28.5 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT2 | Regulation Raise | 25 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT2 | RoCoF Control Service | 248 | MWs | N/A | Gas fuel operation
PINJAR_GT3 | Contingency Reserve Lower | 15.7 | MW | N/A | Gas fuel operation
PINJAR_GT3 | Contingency Reserve Raise | 15.7 | MW | 3 | Gas fuel operation
PINJAR_GT3 | Regulation Lower | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT3 | Regulation Lower | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT3 | Regulation Raise | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT3 | Regulation Raise | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT3 | RoCoF Control Service | 276 | MWs | N/A | Gas fuel operation
PINJAR_GT4 | Contingency Reserve Lower | 15.7 | MW | N/A | Gas fuel operation
PINJAR_GT4 | Contingency Reserve Raise | 15.7 | MW | 3 | Gas fuel operation
PINJAR_GT4 | Regulation Lower | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT4 | Regulation Lower | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT4 | Regulation Raise | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT4 | Regulation Raise | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT4 | RoCoF Control Service | 276 | MWs | N/A | Gas fuel operation
PINJAR_GT5 | Contingency Reserve Lower | 11.4 | MW | N/A | Gas fuel operation
PINJAR_GT5 | Contingency Reserve Raise | 11.4 | MW | 3 | Gas fuel operation
PINJAR_GT5 | Regulation Lower | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT5 | Regulation Lower | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT5 | Regulation Raise | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT5 | Regulation Raise | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT5 | RoCoF Control Service | 276 | MWs | N/A | Gas fuel operation
PINJAR_GT7 | Contingency Reserve Lower | 11.4 | MW | N/A | Gas fuel operation
PINJAR_GT7 | Contingency Reserve Raise | 11.4 | MW | 3 | Gas fuel operation
PINJAR_GT7 | Regulation Lower | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT7 | Regulation Lower | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT7 | Regulation Raise | 29.3 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT7 | Regulation Raise | 27 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT7 | RoCoF Control Service | 276 | MWs | N/A | Gas fuel operation
PINJAR_GT9 | Contingency Reserve Lower | 45.6 | MW | N/A | Gas fuel operation
PINJAR_GT9 | Contingency Reserve Raise | 45.6 | MW | 3 | Gas fuel operation
PINJAR_GT9 | Regulation Lower | 50 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT9 | Regulation Lower | 50 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT9 | Regulation Raise | 50 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT9 | Regulation Raise | 50 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT9 | RoCoF Control Service | 988 | MWs | N/A | Gas fuel operation
PINJAR_GT10 | Contingency Reserve Lower | 37.7 | MW | N/A | Gas fuel operation
PINJAR_GT10 | Contingency Reserve Raise | 37.7 | MW | 3 | Gas fuel operation
PINJAR_GT10 | Regulation Lower | 50 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT10 | Regulation Lower | 50 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT10 | Regulation Raise | 50 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT10 | Regulation Raise | 50 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT10 | RoCoF Control Service | 988 | MWs | N/A | Gas fuel operation
PINJAR_GT11 | Contingency Reserve Lower | 55.9 | MW | N/A | Gas fuel operation
PINJAR_GT11 | Contingency Reserve Raise | 55.9 | MW | 3 | Gas fuel operation
PINJAR_GT11 | Regulation Lower | 50 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT11 | Regulation Lower | 50 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT11 | Regulation Raise | 50 | MW | N/A | Peak loading mode - gas fuel operation
PINJAR_GT11 | Regulation Raise | 50 | MW | N/A | Base loading mode - gas fuel operation
PINJAR_GT11 | RoCoF Control Service | 1194 | MWs | N/A | Gas fuel operation
TIWEST_COG1 | Regulation Lower | 15 | MW | N/A | Peak loading mode
TIWEST_COG1 | Regulation Lower | 15 | MW | N/A | Base loading mode
TIWEST_COG1 | Regulation Raise | 15 | MW | N/A | Peak loading mode
TIWEST_COG1 | Regulation Raise | 15 | MW | N/A | Base loading mode
SIMCOA_IPT_LD_01 | Contingency Reserve Raise | 63 | MW | 0.2 | Including 3x21 MW furnaces